Below is a detailed explanation of how the new scoring will be done

The scoring is done by the progression of a few simple steps

First Step: Normalizing

The vertical ceiling for all classes and/or sub classes in the V9R03 is 110%-

The below table shows the breakdown distribution of such scoring

| Vertical Ceiling Group | Class | Sub-Class | Old Vertical Ceiling |
| --- | --- | --- | --- |
| 1 | Power System | Power Meter & Main Breaker | 5.00% |
| 2 | Power System | GEDP | 12.00% |
| 3 | Power System | Surge Arrestor | 10.00% |
| 4 | Power System | DC Boxes | 5.00% |
| 5 | Power System | Rectifiers | 10.00% |
| 6 | Power System | Batteries / UPS / Stabilizer / Transformer / Solar Cells (PV) System | 5.00% |
| 7 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | 12.00% |
| 8 | Fire System | Fire Alarm and Fighting System | 10.00% |
| 9 | Equipment and DDF | Radio Equipment and DDF | 7.00% |
| 10 | Civil | Shelter Body / Main Enclosure | 10.00% |
| 11 | Civil | Pylon / Palm Tree / Monopole / Masts / Side Arms | 7.00% |
| 12 | Civil | Fence / Roof | 7.00% |
| 13 | Generator | ATS / Engine | 10.00% |

n=113Old Vertical Ceilingn=110%

So, we will multiply each ceiling by (100/110) in order to let the sum of all vertical groups = 100%

New Vertical Ceiling=Old Vertical Ceiling× 100110

This will lead to the following table

| Vertical Ceiling Group | Class | Sub-Class | New Vertical Ceiling |
| --- | --- | --- | --- |
| 1 | Power System | Power Meter & Main Breaker | 4.55% |
| 2 | Power System | GEDP | 10.91% |
| 3 | Power System | Surge Arrestor | 9.09% |
| 4 | Power System | DC Boxes | 4.55% |
| 5 | Power System | Rectifiers | 9.09% |
| 6 | Power System | Batteries / UPS / Stabilizer / Transformer / Solar Cells (PV) System | 4.55% |
| 7 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | 10.91% |
| 8 | Fire System | Fire Alarm and Fighting System | 9.09% |
| 9 | Equipment and DDF | Radio Equipment and DDF | 6.36% |
| 10 | Civil | Shelter Body / Main Enclosure | 9.09% |
| 11 | Civil | Pylon / Palm Tree / Monopole / Masts / Side Arms | 6.36% |
| 12 | Civil | Fence / Roof | 6.36% |
| 13 | Generator | ATS / Engine | 9.09% |

n=113New Vertical Ceilingn=100%

Second Step: Distributing the score of each item in the Vertical Group

The rule was that:

- Critical Reserve is 10% score effective

- Major Reserve is 5% score effective

- Minor Reserve is 2% score effective

Here is another way to look at it

Critical Reserve=2 ×Major Reserve

Critical Reserve=5 ×Minor Reserve

Major Reserve=52 ×Minor Reserve

We will distribute the ceiling for the below reserves as show in the below example for (Equipment and DDF) reserves:

| Class | Sub-Class | Criteria | Recommendation | Minor | Major | Critical | Used | Weighted Representation |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Equipment and DDF | Radio Equipment and DDF | Clean (not normal dust) | TRUE | TRUE | FALSE | FALSE | TRUE | 0.09% |
| Equipment and DDF | Radio Equipment and DDF | Label unit/components | TRUE | TRUE | FALSE | FALSE | TRUE | 0.09% |
| Equipment and DDF | Radio Equipment and DDF | Unit unfixed/not installed well | TRUE | FALSE | FALSE | TRUE | TRUE | 0.45% |
| Equipment and DDF | Radio Equipment and DDF | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…) | TRUE | FALSE | FALSE | TRUE | TRUE | 0.45% |
| Equipment and DDF | Radio Equipment and DDF | Unit sharp edges | TRUE | FALSE | TRUE | FALSE | TRUE | 0.22% |
| Equipment and DDF | Radio Equipment and DDF | Unit earth | TRUE | FALSE | TRUE | FALSE | TRUE | 0.22% |
| Equipment and DDF | Radio Equipment and DDF | Components faulty | TRUE | FALSE | FALSE | TRUE | TRUE | 0.45% |
| Equipment and DDF | Radio Equipment and DDF | Wrong connection | TRUE | FALSE | FALSE | TRUE | TRUE | 0.45% |
| Equipment and DDF | Radio Equipment and DDF | Alarms on equipment (excluding ADM) | TRUE | FALSE | TRUE | FALSE | TRUE | 0.22% |
| Equipment and DDF | Radio Equipment and DDF | Alarms reporting to the OMC | TRUE | FALSE | FALSE | TRUE | TRUE | 0.45% |
| Equipment and DDF | Radio Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits]) | TRUE | FALSE | TRUE | FALSE | TRUE | 0.22% |
| Equipment and DDF | Radio Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM organization | TRUE | FALSE | TRUE | FALSE | TRUE | 0.22% |
| Equipment and DDF | Radio Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM wrong penetration | TRUE | FALSE | TRUE | FALSE | TRUE | 0.22% |
| Equipment and DDF | Radio Equipment and DDF | Cables/Feeders/Jumpers/Coaxial/FO/PCM connection tightness | TRUE | FALSE | TRUE | FALSE | TRUE | 0.22% |
| Equipment and DDF | Radio Equipment and DDF | Cables termination/lugs (AC side), lugs (DC side) | TRUE | FALSE | FALSE | TRUE | TRUE | 0.45% |
| Equipment and DDF | Radio Equipment and DDF | Messy DDF (more than or equal to 10 Krone Blocks or equivalent) | TRUE | FALSE | FALSE | TRUE | TRUE | 0.45% |
| Equipment and DDF | Radio Equipment and DDF | Messy DDF (less than 10 Krone Blocks or equivalent) | TRUE | FALSE | TRUE | FALSE | TRUE | 0.22% |
| Equipment and DDF | Radio Equipment and DDF | Trays/ducts/conduits unfixed | TRUE | FALSE | TRUE | FALSE | TRUE | 0.22% |
| Equipment and DDF | Radio Equipment and DDF | Trays/ducts/conduits has lean supports | TRUE | FALSE | FALSE | TRUE | TRUE | 0.45% |
| Equipment and DDF | Radio Equipment and DDF | Ducts/conduits covers missing/unfixed | TRUE | TRUE | FALSE | FALSE | TRUE | 0.09% |
| Equipment and DDF | Radio Equipment and DDF | Trays covers missing/unfixed (if laid on the ground only) | TRUE | FALSE | FALSE | FALSE | TRUE | 0.00% |
| Equipment and DDF | Radio Equipment and DDF | Trays/Roxtec/Plate not earthed | TRUE | TRUE | FALSE | FALSE | TRUE | 0.09% |
| Equipment and DDF | Radio Equipment and DDF | Trays rust | TRUE | TRUE | FALSE | FALSE | TRUE | 0.09% |
| Equipment and DDF | Radio Equipment and DDF | Trays corrosion | TRUE | FALSE | TRUE | FALSE | FALSE | 0.00% |
| Equipment and DDF | Radio Equipment and DDF | Unit rust (else trays) | TRUE | TRUE | FALSE | FALSE | TRUE | 0.09% |
| Equipment and DDF | Radio Equipment and DDF | Unit corrosion (else trays) | TRUE | FALSE | FALSE | TRUE | FALSE | 0.00% |
| Equipment and DDF | Radio Equipment and DDF | Some parts are missing | TRUE | FALSE | TRUE | FALSE | TRUE | 0.22% |
| Equipment and DDF | Radio Equipment and DDF | Panorama pictures for each system | TRUE | FALSE | FALSE | FALSE | TRUE | 0.00% |

Let’s explain this in a simple way

Radio Equipment and DDF(Items)=6.36%

Let’s also assume the following:

Critical Reserve=10x
Major Reserve=5x
Minor Reserve=2x

From the previous equations, it is safe to conclude the following:

Critical Reserves+ Major Reserves+ Minor Reserves=6.36%

Note: we’ve taken a sample of 1222 different reports and found that there were some items that were not used.
We will exclude them in order to distribute the weight we have upon the effective found items

Substitute for each reserve type by its (nx) factor

810x+105x+62x=6.36%

x=0.0466%

Critical Reserve=10x=0.466%
Major Reserve=5x=0.233%
Minor Reserve=2x=0.0933%

Third Step: Summation of all reserves to determine the Linear Score

After breaking down the score into one value per each item, it is possible at the moment to sum up all the items and subtract it from the total (which is 100%)

Linear Score=100%- All reserves found in siteScore effect of each item

Fourth Step: Multiplying the Linear Score with the first factor (KVertical)

KVertical is a programmable factor and its explanation is simple

For each Vertical Group

If the critical reserves count is greater than 1 critical reserve per this group then,       

multiply the Linear Score by a its corresponding KVertical

Next Vertical Group

This will all result in multiplying the linear score by a factor depending on the number of critical reserves found per vertical group

The below table explains this factor

| Vertical Ceiling Group | Class | Sub-Class | K |
| --- | --- | --- | --- |
| 1 | Power System | Power Meter & Main Breaker | 0.9 |
| 2 | Power System | GEDP | 0.9 |
| 3 | Power System | Surge Arrestor | 0.9 |
| 4 | Power System | DC Boxes | 0.9 |
| 5 | Power System | Rectifiers | 0.9 |
| 6 | Power System | Batteries / UPS / Stabilizer / Transformer / Solar Cells (PV) System | 0.9 |
| 7 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | 0.9 |
| 8 | Fire System | Fire Alarm and Fighting System | 0.9 |
| 9 | Equipment and DDF | Radio Equipment and DDF | 0.9 |
| 10 | Civil | Shelter Body / Main Enclosure | 0.9 |
| 11 | Civil | Pylon / Palm Tree / Monopole / Masts / Side Arms | 0.9 |
| 12 | Civil | Fence / Roof | 0.9 |
| 13 | Generator | ATS / Engine | 0.9 |

Example:

Let’s assume that a site has

- 3 critical reserves in the (GEDP)

- 4 Critical reserves in the (Surge Arrestor)

- 1 Critical Reserve in the (Power Meter & Main Breaker)

KVertical Score=Linear score × KGEDP × KSurge Arrestor=Linear Score ×0.9 ×0.9=Linear Score ×0.81

Critical Reserve in the (Power Meter & Main Breaker) was neglected because it is not greater than 1

Fifth Step: Multiplying the KVertical Score with the Second factor

The second multiplying factor is the a factor that depends upon the number of critical reserves found

Let’s assume it goes by the below table

| Number of Critical Reserves |  | Scoring Factor |
| --- | --- | --- |
| From | To |  |
| 0 | 5 | 100% |
| 6 | 11 | 80% |
| 12 | 17 | 70% |
| 18 | 20 | 60% |
| 21 | 25 | 50% |
| 26 | 30 | 40% |
| 31 | ∞ | 30% |

Example:

Let’s assume the same site in the KVertical Example which has

- 3 critical reserves in the (GEDP)

- 4 Critical reserves in the (Surge Arrestor)

- 1 Critical Reserve in the (Power Meter & Main Breaker)

Total Number of Critical reserves = 7

KCritical Resrves=80%

KCritical Reserves Score=Linear Score × KVertical × KCritical Reserves

Sixth Step: Multiplying the KCritical Reserves Score with the Third factor

The third multiplying factor is the a factor that depends upon the number of all reserves found.
that way, other non-critical reserves have been taken into consideration

Let’s assume it goes by the below table

| Number of All Reserves |  | Scoring Factor |
| --- | --- | --- |
| From | To |  |
| 0 | 6 | 100% |
| 7 | 8 | 90% |
| 9 | 17 | 85% |
| 18 | 20 | 75% |
| 21 | 25 | 65% |
| 26 | 30 | 55% |
| 31 | 35 | 45% |
| 36 | 40 | 35% |
| 41 | ∞ | 25% |

Let’s assume that the previously mentioned site has

- 8 Critical Reserves

- 14 Major Reserves

- 11 Minor Reserves

Total = 33 reserves

KAll Reserves=45%

Site Score

The final score can be easily explained in the below equation

Site Score=Linear Score × KVertical × KCritical Reserves × KAll Reserves

Assuming that the linear score in the previous example was 95% then the score will be

Site Score=95% × 81% × 80% × 45%=27.7%