## Connection
ID | Problem source site code | Problem source site name | Solution | Problem Nature | Key Word | System | ReportID | Site Name | Site Code | Sub-Class | Criteria/Comment
IM758089 | 0427DE | 0061_D_SK-EZBA-SARYA_0427DE | GN problem/ stolen batteries /clear after check GN | Faulty System | batt | Batteries | 345382 | SK-EZBA-SARYA | C2_0427DE_PH4 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM758089 | 0427DE | 0061_D_SK-EZBA-SARYA_0427DE | GN problem/ stolen batteries /clear after check GN | Faulty System | GN | Generator | 345382 | SK-EZBA-SARYA | C2_0427DE_PH4 | ATS / Engine | Components faulty/Exhaust fan not working and another not exist
IM758124 | 3335DE | 0741_D_SK-BERMAKIM_3335DE | GN. Problem / stolen batteries / Clear after check GN | Faulty System | batt | Batteries | 303888 | SK-BERMAKIM | C2_3335DE_PH12 | Batteries | Item(s) stolen/No backup batteries.
IM758124 | 3335DE | 0741_D_SK-BERMAKIM_3335DE | GN. Problem / stolen batteries / Clear after check GN | Faulty System | GN | Generator | 303888 | SK-BERMAKIM | C2_3335DE_PH12 | ATS / Engine | Wrong connection/Sensor has disconnected cable.
IM758124 | 3335DE | 0741_D_SK-BERMAKIM_3335DE | GN. Problem / stolen batteries / Clear after check GN | Faulty System | GN | Generator | 303888 | SK-BERMAKIM | C2_3335DE_PH12 | ATS / Engine | Panorama pictures for each system/Overview.
IM758124 | 3335DE | 0741_D_SK-BERMAKIM_3335DE | GN. Problem / stolen batteries / Clear after check GN | Faulty System | GN | Generator | 303888 | SK-BERMAKIM | C2_3335DE_PH12 | ATS / Engine | Panorama pictures for each system/Generator has key (no logbook found).
IM758129 | 0153RE | 03564_Q_0153RE_RS-HILTON-SAHL | DG Stopped due fuel problem , weak batteries //PLVD activated once DG Fix and power restored site Recovered | Faulty System | DG | Generator | 355600 | 01_H_RS-HILTON-SAHL_0153RE | C1_0153RE_PH8 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/check terminals
IM758140 | 3948DE | 601_D_SK-SMAKEN-SHRQ_3948DE | GN problem/batteries under investigation/clear after check GN | Faulty System | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | Batteries | Some parts are (missing / stolen)/missing battereis
IM758190 | 4011CA | 02353_V_4011CA_MOSTORD-RD2 | down due to main power cut off and stolen batt. (I) | Faulty System | batt | Batteries | 355905 | MOSTORD-RD2 | C1_4011CA_PH17 | Batteries | Some parts are (missing / stolen)/Batteries are stolen
IM758230 | 0329RE | 03838_S_0329RE_RS-SENTIDO-DRM | down after ETS DG stoppage and site has dead batteries // Recovered after ET DG fixxed | Faulty System | DG | Generator | 304289 | 01_S_RS-SENTIDO-DRM_0329RE | C1_0329RE_PH12 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM758243 | 0400UP | 651_S_AT-MOHAMADYAT_0400UP | H.T alarm due to defected A/C capacitor in site AT-MOHAMADYAT_0400UP H.T alarm affected the MW link operation that recovered after HW reset | Faulty System | A/C | A/Cs | 324740 | 01_S_AT-MOHAMADYAT_0400UP | C2_0400UP_PH9 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/Ice exist in A/c IDU
IM758243 | 0400UP | 651_S_AT-MOHAMADYAT_0400UP | H.T alarm due to defected A/C capacitor in site AT-MOHAMADYAT_0400UP H.T alarm affected the MW link operation that recovered after HW reset | Faulty System | H.T | A/Cs | 324740 | 01_S_AT-MOHAMADYAT_0400UP | C2_0400UP_PH9 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/Ice exist in A/c IDU
IM758243 | 0400UP | 651_S_AT-MOHAMADYAT_0400UP | H.T alarm due to defected A/C capacitor in site AT-MOHAMADYAT_0400UP H.T alarm affected the MW link operation that recovered after HW reset | Faulty System | A/C | A/Cs | 324740 | 01_S_AT-MOHAMADYAT_0400UP | C2_0400UP_PH9 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/Ice exist in A/c ODU
IM758243 | 0400UP | 651_S_AT-MOHAMADYAT_0400UP | H.T alarm due to defected A/C capacitor in site AT-MOHAMADYAT_0400UP H.T alarm affected the MW link operation that recovered after HW reset | Faulty System | H.T | A/Cs | 324740 | 01_S_AT-MOHAMADYAT_0400UP | C2_0400UP_PH9 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/Ice exist in A/c ODU
IM758243 | 0400UP | 651_S_AT-MOHAMADYAT_0400UP | H.T alarm due to defected A/C capacitor in site AT-MOHAMADYAT_0400UP H.T alarm affected the MW link operation that recovered after HW reset | Faulty System | A/C | A/Cs | 324740 | 01_S_AT-MOHAMADYAT_0400UP | C2_0400UP_PH9 | A/Cs Cooling / Free Cooling / Ventilation | Wrong connection/A/c 1 working without control board
IM758243 | 0400UP | 651_S_AT-MOHAMADYAT_0400UP | H.T alarm due to defected A/C capacitor in site AT-MOHAMADYAT_0400UP H.T alarm affected the MW link operation that recovered after HW reset | Faulty System | H.T | A/Cs | 324740 | 01_S_AT-MOHAMADYAT_0400UP | C2_0400UP_PH9 | A/Cs Cooling / Free Cooling / Ventilation | Wrong connection/A/c 1 working without control board
IM758250 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem and stolen batteries and VF access problem (M) | Faulty System | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | Batteries | Some parts are (missing / stolen)/missing battereis
IM758283 | 0433CA | 01867_S_0433CA_MENYET-SEIRG | down due to C.B tripped and stolen batteries and access problem (M) | Faulty System | batt | Batteries | 324693 | MENYET-SEIRG | C2_0433CA_PH3 | Batteries | Item(s) stolen/Three batteries are stolen
IM758300 | 0400UP | 651_S_AT-MOHAMADYAT_0400UP | H.T alarm due to defected A/C capacitor in site AT-MOHAMADYAT_0400UP H.T alarm affected the MW link operation that recovered after HW reset | Faulty System | A/C | A/Cs | 324740 | 01_S_AT-MOHAMADYAT_0400UP | C2_0400UP_PH9 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/Ice exist in A/c IDU
IM758300 | 0400UP | 651_S_AT-MOHAMADYAT_0400UP | H.T alarm due to defected A/C capacitor in site AT-MOHAMADYAT_0400UP H.T alarm affected the MW link operation that recovered after HW reset | Faulty System | H.T | A/Cs | 324740 | 01_S_AT-MOHAMADYAT_0400UP | C2_0400UP_PH9 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/Ice exist in A/c IDU
IM758300 | 0400UP | 651_S_AT-MOHAMADYAT_0400UP | H.T alarm due to defected A/C capacitor in site AT-MOHAMADYAT_0400UP H.T alarm affected the MW link operation that recovered after HW reset | Faulty System | A/C | A/Cs | 324740 | 01_S_AT-MOHAMADYAT_0400UP | C2_0400UP_PH9 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/Ice exist in A/c ODU
IM758300 | 0400UP | 651_S_AT-MOHAMADYAT_0400UP | H.T alarm due to defected A/C capacitor in site AT-MOHAMADYAT_0400UP H.T alarm affected the MW link operation that recovered after HW reset | Faulty System | H.T | A/Cs | 324740 | 01_S_AT-MOHAMADYAT_0400UP | C2_0400UP_PH9 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/Ice exist in A/c ODU
IM758300 | 0400UP | 651_S_AT-MOHAMADYAT_0400UP | H.T alarm due to defected A/C capacitor in site AT-MOHAMADYAT_0400UP H.T alarm affected the MW link operation that recovered after HW reset | Faulty System | A/C | A/Cs | 324740 | 01_S_AT-MOHAMADYAT_0400UP | C2_0400UP_PH9 | A/Cs Cooling / Free Cooling / Ventilation | Wrong connection/A/c 1 working without control board
IM758300 | 0400UP | 651_S_AT-MOHAMADYAT_0400UP | H.T alarm due to defected A/C capacitor in site AT-MOHAMADYAT_0400UP H.T alarm affected the MW link operation that recovered after HW reset | Faulty System | H.T | A/Cs | 324740 | 01_S_AT-MOHAMADYAT_0400UP | C2_0400UP_PH9 | A/Cs Cooling / Free Cooling / Ventilation | Wrong connection/A/c 1 working without control board
IM758362 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | main power/Stolen batteries/clear after power back | Faulty System | batt | Batteries | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | Batteries | Item(s) stolen/There is no battery for site
IM758369 | 3489DE | 0461_S_DK-KFR-GHANNAM_3489DE | main power/Stolen batteries/clear after power back | Faulty System | batt | Batteries | 325088 | DK-KFR-GHANNAM | C1-3489DE-PH13 | Batteries | Item(s) stolen/No backup batteries.
IM758386 | 3720DE | 0651_D_MF-SK-KARADIS_3720DE | GN problem/Stolen batteries@-SK-KARADIS_3720DE/clear check GN | Faulty System | batt | Batteries | 355737 | MF-SK-KARADIS | C2-3720DE-PH14 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM758386 | 3720DE | 0651_D_MF-SK-KARADIS_3720DE | GN problem/Stolen batteries@-SK-KARADIS_3720DE/clear check GN | Faulty System | GN | Generator | 355737 | MF-SK-KARADIS | C2-3720DE-PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Cables have bad connections, proper terminals and proper installtion are rerquired.
IM758389 | 3720DE | 0651_D_MF-SK-KARADIS_3720DE | GN problem/Stolen batteries@-SK-KARADIS_3720DE/clear check GN | Faulty System | batt | Batteries | 355737 | MF-SK-KARADIS | C2-3720DE-PH14 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM758389 | 3720DE | 0651_D_MF-SK-KARADIS_3720DE | GN problem/Stolen batteries@-SK-KARADIS_3720DE/clear check GN | Faulty System | GN | Generator | 355737 | MF-SK-KARADIS | C2-3720DE-PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Cables have bad connections, proper terminals and proper installtion are rerquired.
IM758391 | 0615DE | K_GH-KFR-BAB_20860_1 | main power/Stolen batteries@KFR-BAB_0615DE/clear after power back | Faulty System | batt | Batteries | 314420 | GH-KFR-BAB | C15_0615DE_PH14 | Batteries | Item(s) stolen/stolen batteries
IM758412 | 0329RE | 03838_S_0329RE_RS-SENTIDO-DRM | ET DG failure -site on PG --PG stoppage and site restored after refueled the PG | Faulty System | DG | Generator | 304289 | 01_S_RS-SENTIDO-DRM_0329RE | C1_0329RE_PH12 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM758413 | 0786DE | 0201_S_SK-DYARAB-NGM2_0786DE | Hi temp/Clear after check AC's | Faulty System | Hi Temp | A/Cs | 355736 | SK-DYARAB-NGM2 | C8_0786DE_PH09 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/A/C2 isn't working and its CB tripped off.
IM758413 | 0786DE | 0201_S_SK-DYARAB-NGM2_0786DE | Hi temp/Clear after check AC's | Faulty System | Hi Temp | A/Cs | 355736 | SK-DYARAB-NGM2 | C8_0786DE_PH09 | A/Cs Cooling / Free Cooling / Ventilation | Cables termination/lugs (AC side), lugs (DC side)/A/C's cables need proper terminals.
IM758413 | 0786DE | 0201_S_SK-DYARAB-NGM2_0786DE | Hi temp/Clear after check AC's | Faulty System | Hi Temp | A/Cs | 355736 | SK-DYARAB-NGM2 | C8_0786DE_PH09 | A/Cs Cooling / Free Cooling / Ventilation | Some parts are (missing / stolen)/A/C has missing filters.
IM758434 | 3916DE | 1191_S_BH-BAYDA-2_3916DE | Main power / weak batteries / Last BDT 18/10/2018 / connect PG / lock 2G | Faulty System | batt | Batteries | 355465 | BH-BAYDA-2 | C1_3916DE_PH14 | Batteries | Components faulty/faulty
IM758470 | 3565DE | 0531_D_DK-BALAMON_3565DE | GN problem/40Min time discharged batteries@BALAMON_3565DE/clear check GN | Faulty System | GN | Generator | 325113 | DK-BALAMON | C1-3565DE-PH13 | ATS / Engine | Panorama pictures for each system/Overview.
IM758470 | 3565DE | 0531_D_DK-BALAMON_3565DE | GN problem/40Min time discharged batteries@BALAMON_3565DE/clear check GN | Faulty System | GN | Generator | 325113 | DK-BALAMON | C1-3565DE-PH13 | ATS / Engine | Panorama pictures for each system/No ATS diagram.
IM758470 | 3565DE | 0531_D_DK-BALAMON_3565DE | GN problem/40Min time discharged batteries@BALAMON_3565DE/clear check GN | Faulty System | GN | Generator | 325113 | DK-BALAMON | C1-3565DE-PH13 | ATS / Engine | Panorama pictures for each system/Battery poles need cleaning, wax and covers.
IM758471 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | main power/Stolen batteries/clear after power back | Faulty System | batt | Batteries | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | Batteries | Item(s) stolen/There is no battery for site
IM758500 | 3531DE | 1341_D_SK-MIT-EZZ_3531DE | GN. Problem / stolen batteries / clear after checking GN. | Faulty System | batt | Batteries | 303843 | SK-MIT-EZZ | C1-3531DE-PH13 | Batteries | Item(s) stolen/No backup batteries.
IM758500 | 3531DE | 1341_D_SK-MIT-EZZ_3531DE | GN. Problem / stolen batteries / clear after checking GN. | Faulty System | GN | Generator | 303843 | SK-MIT-EZZ | C1-3531DE-PH13 | ATS / Engine | Wrong connection/Generator need proper water feeding and radiator need check.
IM758538 | 0615DE | K_GH-KFR-BAB_20860_1 | main power/Stolen batteries@KFR-BAB_0615DE/clear after power back | Faulty System | batt | Batteries | 314420 | GH-KFR-BAB | C15_0615DE_PH14 | Batteries | Item(s) stolen/stolen batteries
IM758541 | 0222RE | 03824_G_0222RE_RS-FLAMNCO-HTL | DG failure -site on PG --PG stoppage and site restored after refueled the PG | Faulty System | DG | Generator | 355690 | 01_G_RS-FLAMNCO-HTL_0222RE | C1_0222RE_PH09 | ATS / Engine | Components faulty/need battery
IM758557 | 3714UP | 01_D_SHKH-FDL-GAP-2_3714UP | ET shared generator stopped due to technical error and solved after ET FM team intervention Site has weak backup batteries | Faulty System | Gen | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | ATS / Engine | Components faulty/Gen battery is faulty
IM758557 | 3714UP | 01_D_SHKH-FDL-GAP-2_3714UP | ET shared generator stopped due to technical error and solved after ET FM team intervention Site has weak backup batteries | Faulty System | generator | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | ATS / Engine | Components faulty/Gen battery is faulty
IM758557 | 3714UP | 01_D_SHKH-FDL-GAP-2_3714UP | ET shared generator stopped due to technical error and solved after ET FM team intervention Site has weak backup batteries | Faulty System | Gen | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | ATS / Engine | Components faulty/Main c.b inside gen had one faulty slot and one phase welded directly
IM758557 | 3714UP | 01_D_SHKH-FDL-GAP-2_3714UP | ET shared generator stopped due to technical error and solved after ET FM team intervention Site has weak backup batteries | Faulty System | generator | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | ATS / Engine | Components faulty/Main c.b inside gen had one faulty slot and one phase welded directly
IM758557 | 3714UP | 01_D_SHKH-FDL-GAP-2_3714UP | ET shared generator stopped due to technical error and solved after ET FM team intervention Site has weak backup batteries | Faulty System | Gen | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage exist under fuel tank
IM758557 | 3714UP | 01_D_SHKH-FDL-GAP-2_3714UP | ET shared generator stopped due to technical error and solved after ET FM team intervention Site has weak backup batteries | Faulty System | generator | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage exist under fuel tank
IM758557 | 3714UP | 01_D_SHKH-FDL-GAP-2_3714UP | ET shared generator stopped due to technical error and solved after ET FM team intervention Site has weak backup batteries | Faulty System | Gen | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | ATS / Engine | Panorama pictures for each system/Open gland in Gen enclosure need insulation
IM758557 | 3714UP | 01_D_SHKH-FDL-GAP-2_3714UP | ET shared generator stopped due to technical error and solved after ET FM team intervention Site has weak backup batteries | Faulty System | generator | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | ATS / Engine | Panorama pictures for each system/Open gland in Gen enclosure need insulation
IM758557 | 3714UP | 01_D_SHKH-FDL-GAP-2_3714UP | ET shared generator stopped due to technical error and solved after ET FM team intervention Site has weak backup batteries | Faulty System | Gen | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM758557 | 3714UP | 01_D_SHKH-FDL-GAP-2_3714UP | ET shared generator stopped due to technical error and solved after ET FM team intervention Site has weak backup batteries | Faulty System | generator | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM758557 | 3714UP | 01_D_SHKH-FDL-GAP-2_3714UP | ET shared generator stopped due to technical error and solved after ET FM team intervention Site has weak backup batteries | Faulty System | Gen | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | ATS / Engine | Panorama pictures for each system/Last Gen hour meter at Audit G (18510 )
IM758557 | 3714UP | 01_D_SHKH-FDL-GAP-2_3714UP | ET shared generator stopped due to technical error and solved after ET FM team intervention Site has weak backup batteries | Faulty System | generator | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | ATS / Engine | Panorama pictures for each system/Last Gen hour meter at Audit G (18510 )
IM758573 | 3718DE | 0241_S_MF-ABU-HASAN_3718DE | Main Power / batteries under investigation/clear after power back | Faulty System | batt | Batteries | 324625 | MF-ABU HASAN | C1_3718DE_PH14 | Batteries | Item(s) stolen/stolen batteries
IM758581 | 0418DE | 0081_H_DK-OLELA_0418DE | Generator fault due to hot weather crisis | Faulty System | Gen | Generator | 356228 | DK-OLELA | C1_0418DE_PH4 | ATS / Engine | Alarms reporting to the OMC/Generator alarm need adjust.
IM758581 | 0418DE | 0081_H_DK-OLELA_0418DE | Generator fault due to hot weather crisis | Faulty System | generator | Generator | 356228 | DK-OLELA | C1_0418DE_PH4 | ATS / Engine | Alarms reporting to the OMC/Generator alarm need adjust.
IM758591 | 3390UP | 0601_D_AT-MAGRIS_3390UP | Generator stopped due to LOP alarm as engine need overhauling action Site has weak backup batteries | Faulty System | Gen | Generator | 304086 | 01_G_AT-MAGRIS_3390UP | C2_3390UP_PH14 | ATS / Engine | Item(s) stolen/Gen Battery was missing and Battery cables are not isolated
IM758591 | 3390UP | 0601_D_AT-MAGRIS_3390UP | Generator stopped due to LOP alarm as engine need overhauling action Site has weak backup batteries | Faulty System | generator | Generator | 304086 | 01_G_AT-MAGRIS_3390UP | C2_3390UP_PH14 | ATS / Engine | Item(s) stolen/Gen Battery was missing and Battery cables are not isolated
IM758641 | 0876DE | 0641_Q_PS-RSD-02_0876DE | Access GA / GN problem / last BDT @ 19 OCT 2018 is 02:30 | Faulty System | GN | Generator | 335153 | PS-RSD-02 | C4_0876DE_PH09 | ATS / Engine | Components faulty/faulty cover
IM758641 | 0876DE | 0641_Q_PS-RSD-02_0876DE | Access GA / GN problem / last BDT @ 19 OCT 2018 is 02:30 | Faulty System | GN | Generator | 335153 | PS-RSD-02 | C4_0876DE_PH09 | ATS / Engine | Components faulty/faulty battery and no poles' covers
IM758641 | 0876DE | 0641_Q_PS-RSD-02_0876DE | Access GA / GN problem / last BDT @ 19 OCT 2018 is 02:30 | Faulty System | GN | Generator | 335153 | PS-RSD-02 | C4_0876DE_PH09 | ATS / Engine | Components faulty/replace
IM758641 | 0876DE | 0641_Q_PS-RSD-02_0876DE | Access GA / GN problem / last BDT @ 19 OCT 2018 is 02:30 | Faulty System | GN | Generator | 335153 | PS-RSD-02 | C4_0876DE_PH09 | ATS / Engine | Components faulty/faulty radiator
IM758641 | 0876DE | 0641_Q_PS-RSD-02_0876DE | Access GA / GN problem / last BDT @ 19 OCT 2018 is 02:30 | Faulty System | GN | Generator | 335153 | PS-RSD-02 | C4_0876DE_PH09 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/arrange and add duct cover and labels
IM758641 | 0876DE | 0641_Q_PS-RSD-02_0876DE | Access GA / GN problem / last BDT @ 19 OCT 2018 is 02:30 | Faulty System | GN | Generator | 335153 | PS-RSD-02 | C4_0876DE_PH09 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/clean
IM758641 | 0876DE | 0641_Q_PS-RSD-02_0876DE | Access GA / GN problem / last BDT @ 19 OCT 2018 is 02:30 | Faulty System | GN | Generator | 324939 | PS-RSD-02 | C4_0876DE_PH09 | ATS / Engine | Wrong connection/Generator has bad water feeding.
IM758641 | 0876DE | 0641_Q_PS-RSD-02_0876DE | Access GA / GN problem / last BDT @ 19 OCT 2018 is 02:30 | Faulty System | GN | Generator | 324939 | PS-RSD-02 | C4_0876DE_PH09 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/Cables need arrangement and unused need to be removed.
IM758641 | 0876DE | 0641_Q_PS-RSD-02_0876DE | Access GA / GN problem / last BDT @ 19 OCT 2018 is 02:30 | Faulty System | GN | Generator | 324939 | PS-RSD-02 | C4_0876DE_PH09 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/Cable need adjust or replacement.
IM758641 | 0876DE | 0641_Q_PS-RSD-02_0876DE | Access GA / GN problem / last BDT @ 19 OCT 2018 is 02:30 | Faulty System | GN | Generator | 324939 | PS-RSD-02 | C4_0876DE_PH09 | ATS / Engine | Panorama pictures for each system/Overview.
IM758641 | 0876DE | 0641_Q_PS-RSD-02_0876DE | Access GA / GN problem / last BDT @ 19 OCT 2018 is 02:30 | Faulty System | GN | Generator | 324939 | PS-RSD-02 | C4_0876DE_PH09 | ATS / Engine | Panorama pictures for each system/Batteries poles need cleaning, wax and cover.
IM758683 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | Access VF Guard/GN problem/Stolen batteries/clear by check GN | Faulty System | batt | Batteries | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | Batteries | Item(s) stolen/There is no battery for site
IM758683 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | Access VF Guard/GN problem/Stolen batteries/clear by check GN | Faulty System | GN | Generator | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cable has damaged protective isolation
IM758687 | 0222RE | 03824_G_0222RE_RS-FLAMNCO-HTL | DG failure -site on PG --PG stoppage and site restored after refueled the PG | Faulty System | DG | Generator | 355690 | 01_G_RS-FLAMNCO-HTL_0222RE | C1_0222RE_PH09 | ATS / Engine | Components faulty/need battery
IM758702 | 3656DE | 0431_E_SK-BANI-HILAL_3656DE | GN problem/Stolen batteries/clear after check GEN | Faulty System | batt | Batteries | 345380 | SK-BANI-HILAL | C04-3656DE-PH13 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM758702 | 3656DE | 0431_E_SK-BANI-HILAL_3656DE | GN problem/Stolen batteries/clear after check GEN | Faulty System | Gen | Generator | 345380 | SK-BANI-HILAL | C04-3656DE-PH13 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot
IM758702 | 3656DE | 0431_E_SK-BANI-HILAL_3656DE | GN problem/Stolen batteries/clear after check GEN | Faulty System | GN | Generator | 345380 | SK-BANI-HILAL | C04-3656DE-PH13 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot
IM758703 | 3413DE | 0801_D_PS-KHADIGA_3413DE | GN problem @PS-KHADIGA_3413DE / last BDT @ 28 OCT 2017 is 03:00 | Faulty System | GN | Generator | 335150 | PS-KHADIGA | C2_3413DE_PH13 | ATS / Engine | Components faulty/faulty
IM758703 | 3413DE | 0801_D_PS-KHADIGA_3413DE | GN problem @PS-KHADIGA_3413DE / last BDT @ 28 OCT 2017 is 03:00 | Faulty System | GN | Generator | 335150 | PS-KHADIGA | C2_3413DE_PH13 | ATS / Engine | Wrong connection/remove cable
IM758703 | 3413DE | 0801_D_PS-KHADIGA_3413DE | GN problem @PS-KHADIGA_3413DE / last BDT @ 28 OCT 2017 is 03:00 | Faulty System | GN | Generator | 335150 | PS-KHADIGA | C2_3413DE_PH13 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM758703 | 3413DE | 0801_D_PS-KHADIGA_3413DE | GN problem @PS-KHADIGA_3413DE / last BDT @ 28 OCT 2017 is 03:00 | Faulty System | GN | Generator | 324940 | PS-KHADIGA | C2_3413DE_PH13 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/Unused cable need to be removed.
IM758703 | 3413DE | 0801_D_PS-KHADIGA_3413DE | GN problem @PS-KHADIGA_3413DE / last BDT @ 28 OCT 2017 is 03:00 | Faulty System | GN | Generator | 324940 | PS-KHADIGA | C2_3413DE_PH13 | ATS / Engine | Panorama pictures for each system/Overview.
IM758738 | 0418DE | 0081_H_DK-OLELA_0418DE | GN problem/Weak batteries /clear | Faulty System | GN | Generator | 356228 | DK-OLELA | C1_0418DE_PH4 | ATS / Engine | Alarms reporting to the OMC/Generator alarm need adjust.
IM758761 | 0222RE | 03824_G_0222RE_RS-FLAMNCO-HTL | DG failure -site on PG --PG stoppage and site restored after refueled the PG | Faulty System | DG | Generator | 355690 | 01_G_RS-FLAMNCO-HTL_0222RE | C1_0222RE_PH09 | ATS / Engine | Components faulty/need battery
IM758786 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem and stolen battery and PG access | Faulty System | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | Batteries | Some parts are (missing / stolen)/missing battereis
IM758791 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN. Problem / stolen batteries / Handling 1651_D_SK-REFAEEN_3841DE / clear after checking GN. | Faulty System | batt | Batteries | 324500 | SK-AZZAZI | C1_4029DE_PH15 | Batteries | Item(s) stolen/No backup batteries.
IM758791 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN. Problem / stolen batteries / Handling 1651_D_SK-REFAEEN_3841DE / clear after checking GN. | Faulty System | GN | Generator | 324500 | SK-AZZAZI | C1_4029DE_PH15 | ATS / Engine | Wrong connection/Some cables are disconnected and need adjust.
IM758791 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN. Problem / stolen batteries / Handling 1651_D_SK-REFAEEN_3841DE / clear after checking GN. | Faulty System | GN | Generator | 324500 | SK-AZZAZI | C1_4029DE_PH15 | ATS / Engine | Panorama pictures for each system/Generator battery poles need cleaning, wax and covers.
IM758791 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN. Problem / stolen batteries / Handling 1651_D_SK-REFAEEN_3841DE / clear after checking GN. | Faulty System | GN | Generator | 324500 | SK-AZZAZI | C1_4029DE_PH15 | ATS / Engine | Panorama pictures for each system/Overview.
IM758794 | 0300DE | U_G_BH-NEW-NUBARIYA_0300DE | GN problem / weak batteries / recovered after solved GN problem | Faulty System | GN | Generator | 356082 | New_Nobarya | C3_0300DE_PH3 | ATS / Engine | Unit earth/Missing earthling
IM758794 | 0300DE | U_G_BH-NEW-NUBARIYA_0300DE | GN problem / weak batteries / recovered after solved GN problem | Faulty System | GN | Generator | 356082 | New_Nobarya | C3_0300DE_PH3 | ATS / Engine | Wrong connection/Wrong connection
IM758795 | 4005DE | 0751_D_DK-BASHALOSH_4005DE | GEN problem/Weak batteries/clear after check GEN | Faulty System | Gen | Generator | 356229 | DK-BASHALOSH | C4_4005DE_PH15 | ATS / Engine | Unit earth/Disconnected earth cable.
IM758795 | 4005DE | 0751_D_DK-BASHALOSH_4005DE | GEN problem/Weak batteries/clear after check GEN | Faulty System | Gen | Generator | 356229 | DK-BASHALOSH | C4_4005DE_PH15 | ATS / Engine | Components faulty/Battery poles need cleaning, wax and covers.
IM758795 | 4005DE | 0751_D_DK-BASHALOSH_4005DE | GEN problem/Weak batteries/clear after check GEN | Faulty System | Gen | Generator | 356229 | DK-BASHALOSH | C4_4005DE_PH15 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Neutral bar need adjust.
IM758795 | 4005DE | 0751_D_DK-BASHALOSH_4005DE | GEN problem/Weak batteries/clear after check GEN | Faulty System | Gen | Generator | 356229 | DK-BASHALOSH | C4_4005DE_PH15 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Some cables need proper terminals.
IM758807 | 3971DE | 0511_S_GH-ABU-GENDI_3971DE | Access PG / Main power / Batteries D9 | Faulty System | batt | Batteries | 324794 | GH-ABU-GENDI | C1_3971DE_PH15 | Batteries | Item(s) stolen/stolen batteries
IM758826 | 3349CA | 01126_S_3349CA_IMBABA-6 | down due to commercial cut and faulty batteries (MA) | Faulty System | batt | Batteries | 303961 | IMBABA-6 | C2_3349CA_PH12 | Batteries | Components faulty/Batteries are in a very bad condition (DC voltage dropped to 42.7V. after 1 min of power disconnecting)
IM758865 | 3943DE | 0921_S_SK-AKRASH_3943DE | access ET Guard/ET GEN problem/Stolen batteries @ SK-AKRASH_3943DE/clear on PG/PG can't carry all load | Faulty System | batt | Batteries | 303886 | SK-AKRASH | C1_3943DE_PH15 | Batteries | Item(s) stolen/No backup batteries.
IM758872 | 3971DE | 0511_S_GH-ABU-GENDI_3971DE | Access ET / Main power / stolen batteries / connected PG | Faulty System | batt | Batteries | 324794 | GH-ABU-GENDI | C1_3971DE_PH15 | Batteries | Item(s) stolen/stolen batteries
IM758891 | 0370UP | 1961_G_CAIRO-ASWAN-12_0370UP | Main Power Disconnection, stolen batteries, Autoecovered. | Faulty System | batt | Batteries | 304136 | 01_G_CAIRO-ASWAN-12_0370UP | C2_0370UP_PH8 | Batteries | Item(s) stolen/ Batteries were stolen
IM758900 | 0442AL | 2401_S_AWAYED-NTH_0442AL | Down Due To Main Power Cutting / Batteries Stolen / PG Access Problem / On Air After Main Power Auto Recovered | Faulty System | batt | Batteries | 345440 | S_AWAYED-NTH_0442AL | C2_0442AL_PH9 | Batteries | Some parts are (missing / stolen)/Stolen Batteries
IM758940 | 0278CA | 02185_N_0278CA_ABBOUD | down due to main power failure stolen batteries and access PG at site 0278CA_ABBOUD | Faulty System | batt | Batteries | 304055 | ABBOUD | C1_0278CA_PH3 | Batteries | Item(s) stolen/Batteries and cables are stolen
IM758972 | 0646CA | 02128_N_0646CA_OM-BAYOUMI | down due to power problem and battery faulty @ 0646CA_OM-BAYOUMI | Faulty System | batt | Batteries | 345350 | OM-BAYOUMI | C3_0646CA_PH8 | Rectifiers | Alarms reporting to the OMC/Major alarm is active on the site
IM758972 | 0646CA | 02128_N_0646CA_OM-BAYOUMI | down due to power problem and battery faulty @ 0646CA_OM-BAYOUMI | Faulty System | batt | Batteries | 345350 | OM-BAYOUMI | C3_0646CA_PH8 | Batteries | Components faulty/Batteries are faulty (Site is down when the power is disconnected)
IM758980 | 0242CA | 01963_S_0242CA_10TH-RSD2 | DG Stopped , weak batteries , Recovered once DG fix | Faulty System | batt | Batteries | 356353 | 10TH-RSD2 | C4_0242CA_PH2 | Batteries | Some parts are (missing / stolen)/Battery string stolen
IM758985 | 3740DE | 0521_S_KS-MNSHT-ABS_3740DE | Access TE / Main power / stolen batteries | Faulty System | batt | Batteries | 324805 | KS-MNSHT-ABS | C1_3740DE_Ph14 | Batteries | Item(s) stolen/There is no battery for site
IM758986 | 0963CA | 02149_S_0963CA_OM-BAYOUMI-WST | down due to power problem and battery faulty @ 0646CA_OM-BAYOUMI | Faulty System | batt | Batteries | 345290 | OM-BAYOUMI-WST | C3_0963CA_PH9 | Rectifiers | Alarms reporting to the OMC/Minor alarm appears on the rectifier due to high battery temp.
IM759040 | 3526CA | U_V_3526CA_CORNISH-SAHEL | down due to power problem and stolen battery @ 0278CA_ABBOUD | Faulty System | batt | Batteries | 355732 | CORNISH-SAHEL | C1_3526CA_PH13 | Rectifiers | Alarms reporting to the OMC/Power and rectifier alarms don't appear on the OMC
IM759252 | 3499UP | 1871_S_AS-GAFAR-SADK_3499UP_X | Main Power Disconnection, stolen Batteries, PG Connected | Faulty System | batt | Batteries | 356189 | 01_S_AS-GAFAR-SADK_3499UP | C1_3499UP_PH14 | Batteries | Some parts are (missing / stolen)/Site Batteries were stolen
IM759283 | 3532DE | 0511_S_SK-NATORA_3532DE | VF GEN problem/stolen batteries/clear afetr check VF GEN | Faulty System | batt | Batteries | 356262 | SK-NATORA | C2_3532DE_PH13 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM759370 | 0983DE | 1771_S_DK-MIT-ANTAR_0983DE | Main Power / Stolen batteries / connect PG | Faulty System | batt | Batteries | 324896 | DK-MIT-ANTAR | C8_0983DE_PH11 | Batteries | Item(s) stolen/stolen batteries
IM759372 | 3955DE | 0731_S_SK-QRMT-SAHBRA_3955DE | Main Power / Weak batteries/P.G handel nodal sites | Faulty System | batt | Batteries | 356230 | SK-QRMT-SAHBRA | C1_3955DE_PH15 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM759408 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to generator problem (fuel theft case ) and restored | Faulty System | Gen | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | ATS / Engine | Wrong connection/wrong connections
IM759408 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to generator problem (fuel theft case ) and restored | Faulty System | generator | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | ATS / Engine | Wrong connection/wrong connections
IM759408 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to generator problem (fuel theft case ) and restored | Faulty System | Gen | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/floating hoses
IM759408 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to generator problem (fuel theft case ) and restored | Faulty System | generator | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/floating hoses
IM759408 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to generator problem (fuel theft case ) and restored | Faulty System | Gen | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/unprotected cable
IM759408 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to generator problem (fuel theft case ) and restored | Faulty System | generator | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/unprotected cable
IM759408 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to generator problem (fuel theft case ) and restored | Faulty System | Gen | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage
IM759408 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to generator problem (fuel theft case ) and restored | Faulty System | generator | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage
IM759411 | 3656DE | 0431_E_SK-BANI-HILAL_3656DE | GN problem/Stolen batteries/Clear after check GN | Faulty System | batt | Batteries | 345380 | SK-BANI-HILAL | C04-3656DE-PH13 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM759411 | 3656DE | 0431_E_SK-BANI-HILAL_3656DE | GN problem/Stolen batteries/Clear after check GN | Faulty System | GN | Generator | 345380 | SK-BANI-HILAL | C04-3656DE-PH13 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot
IM759424 | 0112RE | 03828_H_0112RE_QUSER-MARSA3 | DG Stopped , dead batteries , PLVD disconnected Sites , once team arrived and fix DG Site Recovered | Faulty System | DG | Generator | 355488 | 01_W_QUSER-MARSA3_0112RE | C4_0112RE_PH4 | ATS / Engine | Unit earth/Gen enclosure earth cable is missing
IM759424 | 0112RE | 03828_H_0112RE_QUSER-MARSA3 | DG Stopped , dead batteries , PLVD disconnected Sites , once team arrived and fix DG Site Recovered | Faulty System | DG | Generator | 355488 | 01_W_QUSER-MARSA3_0112RE | C4_0112RE_PH4 | ATS / Engine | Components faulty/Gen battery is faulty
IM759424 | 0112RE | 03828_H_0112RE_QUSER-MARSA3 | DG Stopped , dead batteries , PLVD disconnected Sites , once team arrived and fix DG Site Recovered | Faulty System | DG | Generator | 355488 | 01_W_QUSER-MARSA3_0112RE | C4_0112RE_PH4 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Two cables inserted in one slot and not teminated can cause bad connections
IM759438 | 0469DE | 0741_D_MF-ABU-MASHHOR_0469DE | HT. @ 0741_D_MF-ABU-MASHHOR_0469DE / clear after checking ACs | Faulty System | Acs | A/Cs | 304342 | MF-ABU-MASHHOR | C2_0469DE_PH6 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/not cooling
IM759438 | 0469DE | 0741_D_MF-ABU-MASHHOR_0469DE | HT. @ 0741_D_MF-ABU-MASHHOR_0469DE / clear after checking ACs | Faulty System | HT. | A/Cs | 304342 | MF-ABU-MASHHOR | C2_0469DE_PH6 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/not cooling
IM759438 | 0469DE | 0741_D_MF-ABU-MASHHOR_0469DE | HT. @ 0741_D_MF-ABU-MASHHOR_0469DE / clear after checking ACs | Faulty System | Acs | A/Cs | 304342 | MF-ABU-MASHHOR | C2_0469DE_PH6 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/faulty A/C
IM759438 | 0469DE | 0741_D_MF-ABU-MASHHOR_0469DE | HT. @ 0741_D_MF-ABU-MASHHOR_0469DE / clear after checking ACs | Faulty System | HT. | A/Cs | 304342 | MF-ABU-MASHHOR | C2_0469DE_PH6 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/faulty A/C
IM759452 | 0658DE | 0661_D_BH-MNSHYT-KHYAT_0658DE | GN problem @ BH-MNSHYT-KHYAT_0658DE / BDT @ 24/05/2019 is : 1.00 hr | Faulty System | GN | Generator | 356260 | BH-MNSHYT-KHYAT | C2_0658DE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has leakage
IM759452 | 0658DE | 0661_D_BH-MNSHYT-KHYAT_0658DE | GN problem @ BH-MNSHYT-KHYAT_0658DE / BDT @ 24/05/2019 is : 1.00 hr | Faulty System | GN | Generator | 356260 | BH-MNSHYT-KHYAT | C2_0658DE_PH9 | ATS / Engine | Components below/over rate (excluding main power feeder if not hot)/Generator has high voltage
IM759469 | 3499UP | 1871_S_AS-GAFAR-SADK_3499UP_X | Main Power Disconnection, Stolen Batteries, PG Connected. | Faulty System | batt | Batteries | 356189 | 01_S_AS-GAFAR-SADK_3499UP | C1_3499UP_PH14 | Batteries | Some parts are (missing / stolen)/Site Batteries were stolen
IM759484 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | access VF/VF. GN. Problem /Stolen batteries / clear on PG. | Faulty System | batt | Batteries | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | Batteries | Item(s) stolen/There is no battery for site
IM759484 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | access VF/VF. GN. Problem /Stolen batteries / clear on PG. | Faulty System | GN | Generator | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cable has damaged protective isolation
IM759508 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to DG fuel run out and PLD disconnect loads and access problem with SOC 1727 (M) | Faulty System | DG | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | ATS / Engine | Wrong connection/wrong connections
IM759508 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to DG fuel run out and PLD disconnect loads and access problem with SOC 1727 (M) | Faulty System | DG | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/floating hoses
IM759508 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to DG fuel run out and PLD disconnect loads and access problem with SOC 1727 (M) | Faulty System | DG | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/unprotected cable
IM759508 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to DG fuel run out and PLD disconnect loads and access problem with SOC 1727 (M) | Faulty System | DG | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage
IM759521 | 4251DE | 03304_S_4251DE_QL-ABU-GHIT2 | main power/stolen batteries/clear after power back | Faulty System | batt | Batteries | 355722 | QL-ABU-GHIT2 | C1_4251DE_PH17 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM759527 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to DG fuel run out and access with SOC problem No 1727 (M) | Faulty System | DG | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | ATS / Engine | Wrong connection/wrong connections
IM759527 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to DG fuel run out and access with SOC problem No 1727 (M) | Faulty System | DG | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/floating hoses
IM759527 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to DG fuel run out and access with SOC problem No 1727 (M) | Faulty System | DG | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/unprotected cable
IM759527 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to DG fuel run out and access with SOC problem No 1727 (M) | Faulty System | DG | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage
IM759548 | 3548UP | 711_S_AT-BANI-MAGD_3548UP | Commercial power cutoff and weak backup batteries VF guard night access problem till 08:00 AM P.G connected and site back on air | Faulty System | backup | Batteries | 324828 | LU-GZRT-BAIRAT | C1_4211UP_PH19 | Batteries | Item(s) stolen/Batteries were stolen
IM759548 | 3548UP | 711_S_AT-BANI-MAGD_3548UP | Commercial power cutoff and weak backup batteries VF guard night access problem till 08:00 AM P.G connected and site back on air | Faulty System | batt | Batteries | 324828 | LU-GZRT-BAIRAT | C1_4211UP_PH19 | Batteries | Item(s) stolen/Batteries were stolen
IM759612 | 3916DE | 1191_S_BH-BAYDA-2_3916DE | Main power / weak batteries / Last BDT 18/10/2018 | Faulty System | batt | Batteries | 355465 | BH-BAYDA-2 | C1_3916DE_PH14 | Batteries | Components faulty/faulty
IM759613 | 0605DE | 0041_S_DK-MAHMUDIYYA_0605DE | Main power @ DK-MAHMUDIYYA_0605DE / stolen batteries | Faulty System | batt | Batteries | 304053 | DK-MAHMUDIYYA | C2_0605DE_PH9 | Batteries | Item(s) stolen/No backup batteries.
IM759623 | 3894CA | 02231_S_3894CA_REHAB-STAGE7 | down due to DG problem and battery stolen | Faulty System | batt | Batteries | 356204 | REHAB-STAGE7 | C1_3894CA_PH17 | Batteries | Some parts are (missing / stolen)/missing batteries
IM759659 | 0433CA | 01867_S_0433CA_MENYET-SEIRG | down due to power meter problem and battery faulty and PG accessed | Faulty System | batt | Batteries | 324693 | MENYET-SEIRG | C2_0433CA_PH3 | Batteries | Item(s) stolen/Three batteries are stolen
IM759667 | 0418DE | 0081_H_DK-OLELA_0418DE | GN problem/Weak batteries/clear after check GN | Faulty System | GN | Generator | 356228 | DK-OLELA | C1_0418DE_PH4 | ATS / Engine | Alarms reporting to the OMC/Generator alarm need adjust.
IM759732 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Wrong connection/external cable to the guard connected from gen and not protected
IM759732 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Wrong connection/external cable to the guard connected from gen and not protected
IM759732 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Wrong connection/One Contactor turned on by setting wood inside it
IM759732 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Wrong connection/One Contactor turned on by setting wood inside it
IM759732 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cables not protected in tube
IM759732 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cables not protected in tube
IM759732 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cables not protected
IM759732 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cables not protected
IM759732 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Item(s) stolen/Gen battery is missing
IM759732 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Item(s) stolen/Gen battery is missing
IM759732 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/ Fuel leakage inside Gen
IM759732 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/ Fuel leakage inside Gen
IM759732 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage inside Gen
IM759732 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage inside Gen
IM759732 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage beisde Gen enclosure area need cleaning
IM759732 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage beisde Gen enclosure area need cleaning
IM759732 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Panorama pictures for each system/Open gland in Gen enclosure need insulation
IM759732 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Panorama pictures for each system/Open gland in Gen enclosure need insulation
IM759732 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM759732 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM759732 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Panorama pictures for each system/Last Gen hour meter at Audit G ( 31148 )
IM759732 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Panorama pictures for each system/Last Gen hour meter at Audit G ( 31148 )
IM759749 | 0370UP | 1961_G_CAIRO-ASWAN-12_0370UP | Main Power Disconnection, Weak Batteries, Autorecovered. | Faulty System | batt | Batteries | 304136 | 01_G_CAIRO-ASWAN-12_0370UP | C2_0370UP_PH8 | Batteries | Item(s) stolen/ Batteries were stolen
IM759755 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | Faulty System | DG | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/OIL & fuel leakage
IM759755 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | Faulty System | Gen | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/OIL & fuel leakage
IM759755 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | Faulty System | DG | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage
IM759755 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | Faulty System | Gen | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage
IM759755 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | Faulty System | DG | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Unit earth/alternator not earthed
IM759755 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | Faulty System | Gen | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Unit earth/alternator not earthed
IM759755 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | Faulty System | DG | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Unit earth/earth bar not connected to main earth bar
IM759755 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | Faulty System | Gen | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Unit earth/earth bar not connected to main earth bar
IM759755 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | Faulty System | DG | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Unit earth/earth cable not connected
IM759755 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | Faulty System | Gen | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Unit earth/earth cable not connected
IM759755 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | Faulty System | DG | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/cable not terminated
IM759755 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | Faulty System | Gen | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/cable not terminated
IM759795 | 3532DE | 0511_S_SK-NATORA_3532DE | access VF/VF GN problem/Stolen batteries/clear after GN working | Faulty System | batt | Batteries | 356262 | SK-NATORA | C2_3532DE_PH13 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM759806 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Generator stopped due to LOP as engine need overhauling action Site has weak backup batteries | Faulty System | Gen | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage of the engine
IM759806 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Generator stopped due to LOP as engine need overhauling action Site has weak backup batteries | Faulty System | generator | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage of the engine
IM759806 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Generator stopped due to LOP as engine need overhauling action Site has weak backup batteries | Faulty System | Gen | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Unit earth/Stolen earth connections of the genset panel
IM759806 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Generator stopped due to LOP as engine need overhauling action Site has weak backup batteries | Faulty System | generator | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Unit earth/Stolen earth connections of the genset panel
IM759806 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Generator stopped due to LOP as engine need overhauling action Site has weak backup batteries | Faulty System | Gen | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Components faulty/The rubber bases of the radiator are faulty
IM759806 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Generator stopped due to LOP as engine need overhauling action Site has weak backup batteries | Faulty System | generator | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Components faulty/The rubber bases of the radiator are faulty
IM759806 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Generator stopped due to LOP as engine need overhauling action Site has weak backup batteries | Faulty System | Gen | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Components faulty/The dynamo belt needs to be tensioned
IM759806 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Generator stopped due to LOP as engine need overhauling action Site has weak backup batteries | Faulty System | generator | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Components faulty/The dynamo belt needs to be tensioned
IM759806 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Generator stopped due to LOP as engine need overhauling action Site has weak backup batteries | Faulty System | Gen | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Wrong connection/The negative pole of the battery isn't connected
IM759806 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Generator stopped due to LOP as engine need overhauling action Site has weak backup batteries | Faulty System | generator | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Wrong connection/The negative pole of the battery isn't connected
IM759806 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Generator stopped due to LOP as engine need overhauling action Site has weak backup batteries | Faulty System | Gen | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Missing terminals of cables connected to contactors and CBs inside the genset panel
IM759806 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Generator stopped due to LOP as engine need overhauling action Site has weak backup batteries | Faulty System | generator | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Missing terminals of cables connected to contactors and CBs inside the genset panel
IM759808 | 0608UP | 1071_D_MN-BANI-ROH_0608UP | Owner of the site switched off the main Generator C.B due to his own problems Site has weak backup batteries | Faulty System | Gen | Generator | 356181 | 01_G_MN-BANI-ROH_0608UP | C1_0608UP_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage
IM759808 | 0608UP | 1071_D_MN-BANI-ROH_0608UP | Owner of the site switched off the main Generator C.B due to his own problems Site has weak backup batteries | Faulty System | generator | Generator | 356181 | 01_G_MN-BANI-ROH_0608UP | C1_0608UP_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage
IM759808 | 0608UP | 1071_D_MN-BANI-ROH_0608UP | Owner of the site switched off the main Generator C.B due to his own problems Site has weak backup batteries | Faulty System | Gen | Generator | 356181 | 01_G_MN-BANI-ROH_0608UP | C1_0608UP_PH9 | ATS / Engine | Components faulty/faulty battery
IM759808 | 0608UP | 1071_D_MN-BANI-ROH_0608UP | Owner of the site switched off the main Generator C.B due to his own problems Site has weak backup batteries | Faulty System | generator | Generator | 356181 | 01_G_MN-BANI-ROH_0608UP | C1_0608UP_PH9 | ATS / Engine | Components faulty/faulty battery
IM759808 | 0608UP | 1071_D_MN-BANI-ROH_0608UP | Owner of the site switched off the main Generator C.B due to his own problems Site has weak backup batteries | Faulty System | Gen | Generator | 356181 | 01_G_MN-BANI-ROH_0608UP | C1_0608UP_PH9 | ATS / Engine | Components faulty/need battery
IM759808 | 0608UP | 1071_D_MN-BANI-ROH_0608UP | Owner of the site switched off the main Generator C.B due to his own problems Site has weak backup batteries | Faulty System | generator | Generator | 356181 | 01_G_MN-BANI-ROH_0608UP | C1_0608UP_PH9 | ATS / Engine | Components faulty/need battery
IM759808 | 0608UP | 1071_D_MN-BANI-ROH_0608UP | Owner of the site switched off the main Generator C.B due to his own problems Site has weak backup batteries | Faulty System | Gen | Generator | 356181 | 01_G_MN-BANI-ROH_0608UP | C1_0608UP_PH9 | ATS / Engine | Wrong connection/remove wrong connection
IM759808 | 0608UP | 1071_D_MN-BANI-ROH_0608UP | Owner of the site switched off the main Generator C.B due to his own problems Site has weak backup batteries | Faulty System | generator | Generator | 356181 | 01_G_MN-BANI-ROH_0608UP | C1_0608UP_PH9 | ATS / Engine | Wrong connection/remove wrong connection
IM759843 | 3866DE | 2001_D_DK-SANBAKHT_3866DE | Access Guard / GN problem / stolen batteries | Faulty System | GN | Generator | 304185 | DK-SANBAKHT | C3_3866DE_PH14 | ATS / Engine | Components faulty/screen need repair
IM759843 | 3866DE | 2001_D_DK-SANBAKHT_3866DE | Access Guard / GN problem / stolen batteries | Faulty System | GN | Generator | 304185 | DK-SANBAKHT | C3_3866DE_PH14 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/protect by tray
IM759843 | 3866DE | 2001_D_DK-SANBAKHT_3866DE | Access Guard / GN problem / stolen batteries | Faulty System | GN | Generator | 304185 | DK-SANBAKHT | C3_3866DE_PH14 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/protect
IM759843 | 3866DE | 2001_D_DK-SANBAKHT_3866DE | Access Guard / GN problem / stolen batteries | Faulty System | GN | Generator | 304185 | DK-SANBAKHT | C3_3866DE_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check oil leakage
IM759856 | 3948UP | 0111_S_BS-MNSHAT-ASEM_3948UP_X | Generator stopped due to dynamo problem and changed Site has weak backup batteries | Faulty System | backup | Batteries | 356347 | 01_S_BS-MNSHAT-ASEM_3948UP | C1_3948UP_PH16 | Batteries | Some parts are (missing / stolen)/Batteries are stolen
IM759856 | 3948UP | 0111_S_BS-MNSHAT-ASEM_3948UP_X | Generator stopped due to dynamo problem and changed Site has weak backup batteries | Faulty System | batt | Batteries | 356347 | 01_S_BS-MNSHAT-ASEM_3948UP | C1_3948UP_PH16 | Batteries | Some parts are (missing / stolen)/Batteries are stolen
IM759856 | 3948UP | 0111_S_BS-MNSHAT-ASEM_3948UP_X | Generator stopped due to dynamo problem and changed Site has weak backup batteries | Faulty System | Gen | Generator | 356347 | 01_S_BS-MNSHAT-ASEM_3948UP | C1_3948UP_PH16 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil and water leakage of the engine
IM759856 | 3948UP | 0111_S_BS-MNSHAT-ASEM_3948UP_X | Generator stopped due to dynamo problem and changed Site has weak backup batteries | Faulty System | generator | Generator | 356347 | 01_S_BS-MNSHAT-ASEM_3948UP | C1_3948UP_PH16 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil and water leakage of the engine
IM759856 | 3948UP | 0111_S_BS-MNSHAT-ASEM_3948UP_X | Generator stopped due to dynamo problem and changed Site has weak backup batteries | Faulty System | Gen | Generator | 356347 | 01_S_BS-MNSHAT-ASEM_3948UP | C1_3948UP_PH16 | ATS / Engine | Components faulty/Faulty display of the genset
IM759856 | 3948UP | 0111_S_BS-MNSHAT-ASEM_3948UP_X | Generator stopped due to dynamo problem and changed Site has weak backup batteries | Faulty System | generator | Generator | 356347 | 01_S_BS-MNSHAT-ASEM_3948UP | C1_3948UP_PH16 | ATS / Engine | Components faulty/Faulty display of the genset
IM759856 | 3948UP | 0111_S_BS-MNSHAT-ASEM_3948UP_X | Generator stopped due to dynamo problem and changed Site has weak backup batteries | Faulty System | Gen | Generator | 356347 | 01_S_BS-MNSHAT-ASEM_3948UP | C1_3948UP_PH16 | ATS / Engine | Components faulty/Defected rubber bases of the radiator
IM759856 | 3948UP | 0111_S_BS-MNSHAT-ASEM_3948UP_X | Generator stopped due to dynamo problem and changed Site has weak backup batteries | Faulty System | generator | Generator | 356347 | 01_S_BS-MNSHAT-ASEM_3948UP | C1_3948UP_PH16 | ATS / Engine | Components faulty/Defected rubber bases of the radiator
IM759856 | 3948UP | 0111_S_BS-MNSHAT-ASEM_3948UP_X | Generator stopped due to dynamo problem and changed Site has weak backup batteries | Faulty System | Gen | Generator | 356347 | 01_S_BS-MNSHAT-ASEM_3948UP | C1_3948UP_PH16 | ATS / Engine | Components faulty/Broken cover of the genset
IM759856 | 3948UP | 0111_S_BS-MNSHAT-ASEM_3948UP_X | Generator stopped due to dynamo problem and changed Site has weak backup batteries | Faulty System | generator | Generator | 356347 | 01_S_BS-MNSHAT-ASEM_3948UP | C1_3948UP_PH16 | ATS / Engine | Components faulty/Broken cover of the genset
IM759856 | 3948UP | 0111_S_BS-MNSHAT-ASEM_3948UP_X | Generator stopped due to dynamo problem and changed Site has weak backup batteries | Faulty System | Gen | Generator | 356347 | 01_S_BS-MNSHAT-ASEM_3948UP | C1_3948UP_PH16 | ATS / Engine | Components faulty/The rain cap is broken
IM759856 | 3948UP | 0111_S_BS-MNSHAT-ASEM_3948UP_X | Generator stopped due to dynamo problem and changed Site has weak backup batteries | Faulty System | generator | Generator | 356347 | 01_S_BS-MNSHAT-ASEM_3948UP | C1_3948UP_PH16 | ATS / Engine | Components faulty/The rain cap is broken
IM759856 | 3948UP | 0111_S_BS-MNSHAT-ASEM_3948UP_X | Generator stopped due to dynamo problem and changed Site has weak backup batteries | Faulty System | Gen | Generator | 356347 | 01_S_BS-MNSHAT-ASEM_3948UP | C1_3948UP_PH16 | ATS / Engine | Wrong connection/The genset battery is disconnected
IM759856 | 3948UP | 0111_S_BS-MNSHAT-ASEM_3948UP_X | Generator stopped due to dynamo problem and changed Site has weak backup batteries | Faulty System | generator | Generator | 356347 | 01_S_BS-MNSHAT-ASEM_3948UP | C1_3948UP_PH16 | ATS / Engine | Wrong connection/The genset battery is disconnected
IM759856 | 3948UP | 0111_S_BS-MNSHAT-ASEM_3948UP_X | Generator stopped due to dynamo problem and changed Site has weak backup batteries | Faulty System | Gen | Generator | 356347 | 01_S_BS-MNSHAT-ASEM_3948UP | C1_3948UP_PH16 | ATS / Engine | Wrong connection/Equipments are not fixed and disconnected cables inside the genset panel
IM759856 | 3948UP | 0111_S_BS-MNSHAT-ASEM_3948UP_X | Generator stopped due to dynamo problem and changed Site has weak backup batteries | Faulty System | generator | Generator | 356347 | 01_S_BS-MNSHAT-ASEM_3948UP | C1_3948UP_PH16 | ATS / Engine | Wrong connection/Equipments are not fixed and disconnected cables inside the genset panel
IM759856 | 3948UP | 0111_S_BS-MNSHAT-ASEM_3948UP_X | Generator stopped due to dynamo problem and changed Site has weak backup batteries | Faulty System | Gen | Generator | 356347 | 01_S_BS-MNSHAT-ASEM_3948UP | C1_3948UP_PH16 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Missing terminals of power cables connected inside the genset panel
IM759856 | 3948UP | 0111_S_BS-MNSHAT-ASEM_3948UP_X | Generator stopped due to dynamo problem and changed Site has weak backup batteries | Faulty System | generator | Generator | 356347 | 01_S_BS-MNSHAT-ASEM_3948UP | C1_3948UP_PH16 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Missing terminals of power cables connected inside the genset panel
IM759856 | 3948UP | 0111_S_BS-MNSHAT-ASEM_3948UP_X | Generator stopped due to dynamo problem and changed Site has weak backup batteries | Faulty System | Gen | Generator | 356347 | 01_S_BS-MNSHAT-ASEM_3948UP | C1_3948UP_PH16 | ATS / Engine | Filters condition oil/fuel/air/The air filter and cover aren't fixed
IM759856 | 3948UP | 0111_S_BS-MNSHAT-ASEM_3948UP_X | Generator stopped due to dynamo problem and changed Site has weak backup batteries | Faulty System | generator | Generator | 356347 | 01_S_BS-MNSHAT-ASEM_3948UP | C1_3948UP_PH16 | ATS / Engine | Filters condition oil/fuel/air/The air filter and cover aren't fixed
IM759911 | 3892DE | 0171_S_BH-ZWIT-HUMOR_3892DE | Main power / stolen batteries / Rectifier Module faulty | Faulty System | batt | Batteries | 324905 | BH-ZWIT-HUMOR | C1_3892DE_PH14 | Batteries | Item(s) stolen/There is no battery for site
IM759946 | 0481UP | 0331_Q_SG-QARAN_0481UP | Owner Deliberatly switched off main Generator C.B Due to Finincial problem, solved. | Faulty System | Gen | Generator | 356515 | 01_H_SG-QARAN_0481UP | C1_0481UP_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage beside Gen enclosure
IM759946 | 0481UP | 0331_Q_SG-QARAN_0481UP | Owner Deliberatly switched off main Generator C.B Due to Finincial problem, solved. | Faulty System | generator | Generator | 356515 | 01_H_SG-QARAN_0481UP | C1_0481UP_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage beside Gen enclosure
IM759946 | 0481UP | 0331_Q_SG-QARAN_0481UP | Owner Deliberatly switched off main Generator C.B Due to Finincial problem, solved. | Faulty System | Gen | Generator | 356515 | 01_H_SG-QARAN_0481UP | C1_0481UP_PH9 | ATS / Engine | Unit earth/Gen earth bar is not fixed
IM759946 | 0481UP | 0331_Q_SG-QARAN_0481UP | Owner Deliberatly switched off main Generator C.B Due to Finincial problem, solved. | Faulty System | generator | Generator | 356515 | 01_H_SG-QARAN_0481UP | C1_0481UP_PH9 | ATS / Engine | Unit earth/Gen earth bar is not fixed
IM759946 | 0481UP | 0331_Q_SG-QARAN_0481UP | Owner Deliberatly switched off main Generator C.B Due to Finincial problem, solved. | Faulty System | Gen | Generator | 356515 | 01_H_SG-QARAN_0481UP | C1_0481UP_PH9 | ATS / Engine | Components faulty/Gen need new battery
IM759946 | 0481UP | 0331_Q_SG-QARAN_0481UP | Owner Deliberatly switched off main Generator C.B Due to Finincial problem, solved. | Faulty System | generator | Generator | 356515 | 01_H_SG-QARAN_0481UP | C1_0481UP_PH9 | ATS / Engine | Components faulty/Gen need new battery
IM759946 | 0481UP | 0331_Q_SG-QARAN_0481UP | Owner Deliberatly switched off main Generator C.B Due to Finincial problem, solved. | Faulty System | Gen | Generator | 356515 | 01_H_SG-QARAN_0481UP | C1_0481UP_PH9 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/ Missing terminals at gen C.B inside Ats panel
IM759946 | 0481UP | 0331_Q_SG-QARAN_0481UP | Owner Deliberatly switched off main Generator C.B Due to Finincial problem, solved. | Faulty System | generator | Generator | 356515 | 01_H_SG-QARAN_0481UP | C1_0481UP_PH9 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/ Missing terminals at gen C.B inside Ats panel
IM759964 | 0223RE | 03853_G_0223RE_RS-VERA-CLUB | DG Stopped , Stolen batteries , Recovered once DG problem solved | Faulty System | batt | Batteries | 355521 | 01_G_RS-VERA-CLUB_0223RE | C1_0223RE_PH9 | Rectifiers | Alarms reporting to the OMC/Rectifer alarm not appeared on the omc ( looped at ddf racl )
IM759964 | 0223RE | 03853_G_0223RE_RS-VERA-CLUB | DG Stopped , Stolen batteries , Recovered once DG problem solved | Faulty System | batt | Batteries | 355521 | 01_G_RS-VERA-CLUB_0223RE | C1_0223RE_PH9 | Batteries | Some parts are (missing / stolen)/some of site batteries missing poles covers
IM759964 | 0223RE | 03853_G_0223RE_RS-VERA-CLUB | DG Stopped , Stolen batteries , Recovered once DG problem solved | Faulty System | DG | Generator | 355521 | 01_G_RS-VERA-CLUB_0223RE | C1_0223RE_PH9 | ATS / Engine | Unit earth/Gen earth cable is missing
IM759964 | 0223RE | 03853_G_0223RE_RS-VERA-CLUB | DG Stopped , Stolen batteries , Recovered once DG problem solved | Faulty System | DG | Generator | 355521 | 01_G_RS-VERA-CLUB_0223RE | C1_0223RE_PH9 | ATS / Engine | Components faulty/Emergency stop not working
IM759964 | 0223RE | 03853_G_0223RE_RS-VERA-CLUB | DG Stopped , Stolen batteries , Recovered once DG problem solved | Faulty System | DG | Generator | 355521 | 01_G_RS-VERA-CLUB_0223RE | C1_0223RE_PH9 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Two cables inserted in one slot and not teminated can cause bad connections
IM759984 | 3124UP | 1761_S_AS-SILWA-BHRY_3124UP_X | Main Power Disconnection, Stolen Batteries, PG Connected. | Faulty System | batt | Batteries | 355937 | 01_S_AS-SILWA-BHRY_3124UP | C1_3124UP_PH13 | Rectifiers | Alarms reporting to the OMC/Rectifer minor alarm is not appeared on the omc and looped
IM759997 | 3835DE | 0651_S_SK-SHNT-HRABWA_3835DE | Main Power / stolen batteries @SK-SHNT-HRABWA_3835DE/ Clear after power back | Faulty System | batt | Batteries | 345236 | SK-SHNT-HRABWA | C1_3835DE_PH14 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM759999 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | access VF/VF GN problem/Stolen batteries | Faulty System | batt | Batteries | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | Batteries | Item(s) stolen/There is no battery for site
IM759999 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | access VF/VF GN problem/Stolen batteries | Faulty System | GN | Generator | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cable has damaged protective isolation
IM760001 | 0983DE | 1771_S_DK-MIT-ANTAR_0983DE | Main power / Stolen batteries | Faulty System | batt | Batteries | 324896 | DK-MIT-ANTAR | C8_0983DE_PH11 | Batteries | Item(s) stolen/stolen batteries
IM760036 | 0646CA | 02128_N_0646CA_OM-BAYOUMI | down due to power problem @ 0646CA_OM-BAYOUMI and weak battery | Faulty System | batt | Batteries | 345350 | OM-BAYOUMI | C3_0646CA_PH8 | Rectifiers | Alarms reporting to the OMC/Major alarm is active on the site
IM760036 | 0646CA | 02128_N_0646CA_OM-BAYOUMI | down due to power problem @ 0646CA_OM-BAYOUMI and weak battery | Faulty System | batt | Batteries | 345350 | OM-BAYOUMI | C3_0646CA_PH8 | Batteries | Components faulty/Batteries are faulty (Site is down when the power is disconnected)
IM760038 | 3089UP | 2141_S_SG-GALAWEYA_3089UP | Main Power Disconnection, Stolen Batteries, PG Connected . | Faulty System | batt | Batteries | 356371 | 01_S_SG-GALAWEYA_3089UP | C1_3089UP_PH13 | Batteries | Some parts are (missing / stolen)/site batteries were Stolen
IM760101 | 0508DE | 1151_Q_BH-KOM-BERKA_0508DE | GN problem / Solar theft case / Transfer Solar / Connect PG | Faulty System | GN | Generator | 304064 | BH-KOM-BERKA | C1_0508DE_PH8 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cable has damaged protective isolation
IM760101 | 0508DE | 1151_Q_BH-KOM-BERKA_0508DE | GN problem / Solar theft case / Transfer Solar / Connect PG | Faulty System | GN | Generator | 304064 | BH-KOM-BERKA | C1_0508DE_PH8 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Burned terminals
IM760103 | 3819CA | 02815_S_3819CA_MADINATY-11 | down due to power problem and battery stolen | Faulty System | batt | Batteries | 324704 | MADINATY-11 | C1_3819CA_PH16 | Batteries | Some parts are missing/missing batteries
IM760132 | 0427DE | 0061_D_SK-EZBA-SARYA_0427DE | GN problem/stolen batteries | Faulty System | batt | Batteries | 345382 | SK-EZBA-SARYA | C2_0427DE_PH4 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM760132 | 0427DE | 0061_D_SK-EZBA-SARYA_0427DE | GN problem/stolen batteries | Faulty System | GN | Generator | 345382 | SK-EZBA-SARYA | C2_0427DE_PH4 | ATS / Engine | Components faulty/Exhaust fan not working and another not exist
IM760146 | 0418DE | 0081_H_DK-OLELA_0418DE | GN problem/Weak batteries/clear after check GN | Faulty System | GN | Generator | 356228 | DK-OLELA | C1_0418DE_PH4 | ATS / Engine | Alarms reporting to the OMC/Generator alarm need adjust.
IM760150 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/Weak batteries/clear after check GN | Faulty System | batt | Batteries | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | Batteries | Some parts are missing/Battery cabinet need cleaning (from inside) and holes need sealing.
IM760150 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/Weak batteries/clear after check GN | Faulty System | batt | Batteries | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | Batteries | Some parts are missing/Batteries poles need have missing covers.
IM760150 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/Weak batteries/clear after check GN | Faulty System | GN | Generator | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | ATS / Engine | Components faulty/Generator has bad performance and need overall.
IM760150 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/Weak batteries/clear after check GN | Faulty System | GN | Generator | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | ATS / Engine | Panorama pictures for each system/Overview.
IM760205 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | access VF/VF. GN. Problem /Stolen batteries / clear on PG. | Faulty System | batt | Batteries | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | Batteries | Item(s) stolen/There is no battery for site
IM760205 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | access VF/VF. GN. Problem /Stolen batteries / clear on PG. | Faulty System | GN | Generator | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cable has damaged protective isolation
IM760291 | 0332UP | 0691_G_MN-GABAL-TEIR_0332UP | Commercial power cutoff and STB generator stopped , Site has weak backup batteries , Recovered | Faulty System | backup | Batteries | 325017 | 01_G_MN-GABAL-TEIR_0332UP | C1_0332UP_PH8 | Batteries | Components faulty/battery need to be changed
IM760291 | 0332UP | 0691_G_MN-GABAL-TEIR_0332UP | Commercial power cutoff and STB generator stopped , Site has weak backup batteries , Recovered | Faulty System | batt | Batteries | 325017 | 01_G_MN-GABAL-TEIR_0332UP | C1_0332UP_PH8 | Batteries | Components faulty/battery need to be changed
IM760291 | 0332UP | 0691_G_MN-GABAL-TEIR_0332UP | Commercial power cutoff and STB generator stopped , Site has weak backup batteries , Recovered | Faulty System | Gen | Generator | 325017 | 01_G_MN-GABAL-TEIR_0332UP | C1_0332UP_PH8 | ATS / Engine | Components faulty/change it
IM760291 | 0332UP | 0691_G_MN-GABAL-TEIR_0332UP | Commercial power cutoff and STB generator stopped , Site has weak backup batteries , Recovered | Faulty System | generator | Generator | 325017 | 01_G_MN-GABAL-TEIR_0332UP | C1_0332UP_PH8 | ATS / Engine | Components faulty/change it
IM760329 | 0038CA | S_MAGLESALSHAAB_64597_S1_V | down due to commercial cut and faulty batteries and access problem (MA) | Faulty System | batt | Batteries | 355810 | MAGLESALSHAAB | C2_0038CA_PH0 | Rectifiers | Alarms reporting to the OMC/Major and minor alarms are active on the rectifier (Battery fuse & Psys high)
IM760334 | 0707DE | 1081_D_GH-RGDYA-MAHLA_0707DE | GN problem @ GH-RGDYA-MAHLA_0707DE / Stolen batteries | Faulty System | GN | Generator | 324607 | GH-RGDYA-MAHLA | C1_0707DE_PH9 | ATS / Engine | Item(s) stolen/Missing battery
IM760334 | 0707DE | 1081_D_GH-RGDYA-MAHLA_0707DE | GN problem @ GH-RGDYA-MAHLA_0707DE / Stolen batteries | Faulty System | GN | Generator | 324607 | GH-RGDYA-MAHLA | C1_0707DE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Cleaning and isolation
IM760334 | 0707DE | 1081_D_GH-RGDYA-MAHLA_0707DE | GN problem @ GH-RGDYA-MAHLA_0707DE / Stolen batteries | Faulty System | GN | Generator | 324607 | GH-RGDYA-MAHLA | C1_0707DE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Clean and fix nut
IM760334 | 0707DE | 1081_D_GH-RGDYA-MAHLA_0707DE | GN problem @ GH-RGDYA-MAHLA_0707DE / Stolen batteries | Faulty System | GN | Generator | 324607 | GH-RGDYA-MAHLA | C1_0707DE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM760334 | 0707DE | 1081_D_GH-RGDYA-MAHLA_0707DE | GN problem @ GH-RGDYA-MAHLA_0707DE / Stolen batteries | Faulty System | GN | Generator | 324607 | GH-RGDYA-MAHLA | C1_0707DE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Clean
IM760347 | 3828DE | 0961_S_BH-GWAD-HUSNI_3828DE | Main power / stolen batteries / PG connected | Faulty System | batt | Batteries | 356184 | BH-GWAD-HUSNI | C1_3828DE_PH14 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM760391 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | Faulty System | DG | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/OIL & fuel leakage
IM760391 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | Faulty System | Gen | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/OIL & fuel leakage
IM760391 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | Faulty System | DG | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage
IM760391 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | Faulty System | Gen | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage
IM760391 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | Faulty System | DG | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Unit earth/alternator not earthed
IM760391 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | Faulty System | Gen | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Unit earth/alternator not earthed
IM760391 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | Faulty System | DG | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Unit earth/earth bar not connected to main earth bar
IM760391 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | Faulty System | Gen | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Unit earth/earth bar not connected to main earth bar
IM760391 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | Faulty System | DG | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Unit earth/earth cable not connected
IM760391 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | Faulty System | Gen | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Unit earth/earth cable not connected
IM760391 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | Faulty System | DG | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/cable not terminated
IM760391 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | Faulty System | Gen | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/cable not terminated
IM760422 | 0490SI | 03534_S_0490SI_IS-NASR | Outage power in area located site // access PG // weak batteries Recovered once power restored | Faulty System | batt | Batteries | 356007 | 01_S_IS-NASR_0490SI | C2_0490SI_PH14 | Rectifiers | Alarms reporting to the OMC/Rectifier alarm , A/C & door not apear on CAP
IM760422 | 0490SI | 03534_S_0490SI_IS-NASR | Outage power in area located site // access PG // weak batteries Recovered once power restored | Faulty System | batt | Batteries | 356007 | 01_S_IS-NASR_0490SI | C2_0490SI_PH14 | Batteries | Components faulty/Battery voltag reading drop to 46 volt after we disconnect th rectifier C.B (Check the batteries)
IM760456 | 3126DE | 0121_S_DK-HAGYZEYA_3126DE | main power/Stolen batteries/handel SK-SAWALEH_3338DE,SK-TELRAK_0798DE,TAMEY-AMDID_0347D | Faulty System | batt | Batteries | 355992 | DK-HAGYZEYA | C6-3126DE-PH12 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM760471 | 3628DE | 0811_S_GH-QSR-BAGHDAD_3628DE | Main power / stolen batteries / PG connected | Faulty System | batt | Batteries | 324836 | GH-QSR-BAGHDAD | C2_3628DE_PH13 | Batteries | Item(s) stolen/Stolen batteries
IM760475 | 3352DE | 0071_D_BH-SHBRA-OSEEM_3352DE | Access VF. / Main Power / Stolen batteries / Clear after power back | Faulty System | batt | Batteries | 325117 | BH-SHBRA-OSEEM | C1_3352DE_PH12 | Batteries | Item(s) stolen/There is no battery for site
IM760498 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | access VF/VF. GN. Problem /Stolen batteries / clear on PG. | Faulty System | batt | Batteries | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | Batteries | Item(s) stolen/There is no battery for site
IM760498 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | access VF/VF. GN. Problem /Stolen batteries / clear on PG. | Faulty System | GN | Generator | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cable has damaged protective isolation
IM760522 | 3385DE | 0671_S_BH-GHAZALA-VLG_3385DE | Main power / weak batteries / handle another sites BH-KFR-QASHASH_0545DE & BH-KFR-MUSTNAB_3520de / PG now in way | Faulty System | batt | Batteries | 355780 | BH-GHAZALA-VLG | C2_3385DE_PH13 | Rectifiers | Alarms reporting to the OMC/Site down due to power (Check alarms with OMC)
IM760530 | 0626DE | 0171_S_BH-KHRABA-FCT_0626DE | Main power/SCG/Weak batteries@KHRABA-FCT_0626DE/ clear after checking GN. | Faulty System | GN | Generator | 304233 | BH-KHRABA-FCT | C1_0626DE_PH9 | ATS / Engine | Components faulty/Small generator disconnected and has missing ATS components (To be connected or removed)
IM760530 | 0626DE | 0171_S_BH-KHRABA-FCT_0626DE | Main power/SCG/Weak batteries@KHRABA-FCT_0626DE/ clear after checking GN. | Faulty System | GN | Generator | 304233 | BH-KHRABA-FCT | C1_0626DE_PH9 | ATS / Engine | Components faulty/Small generator disconnected and has missing ATS components (To be installed or removed)
IM760553 | 0430CA | U_S_0430CA_MAHMASHAH | down due to Deliberately switched off by owner and battery weak and PG access | Faulty System | batt | Batteries | 356046 | SZ-MALLAHA | 0364RE | Batteries | Some parts are (missing / stolen)/Missing battery pole cover
IM760610 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Generator stopped , Site has weak backup batteries , Recovered | Faulty System | Gen | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | ATS / Engine | Components faulty/Gen battery was defected
IM760610 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Generator stopped , Site has weak backup batteries , Recovered | Faulty System | generator | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | ATS / Engine | Components faulty/Gen battery was defected
IM760610 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Generator stopped , Site has weak backup batteries , Recovered | Faulty System | Gen | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/ATS Cables not organized
IM760610 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Generator stopped , Site has weak backup batteries , Recovered | Faulty System | generator | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/ATS Cables not organized
IM760630 | 0405RE | 03878_S_0405RE_RS-MRSA-NAKARI | ET DG Stopped , No Backup installed , once DG problem solved site recovered | Faulty System | backup | Batteries | 356420 | 01_S_RS-MRSA-NAKARI_0405RE | C1_0405RE_PH15 | Batteries | Some parts are (missing / stolen)/Batteries were stolen
IM760632 | 3828DE | 0961_S_BH-GWAD-HUSNI_3828DE | Main power / stolen batteries / PG connected | Faulty System | batt | Batteries | 356184 | BH-GWAD-HUSNI | C1_3828DE_PH14 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM760635 | 3751DE | 0021_S_DK-SHRKA2-VLG_3751DE | Main power / stolen batteries | Faulty System | batt | Batteries | 304052 | DK-SHRKA2-VLG | C1_3751DE_PH14 | Batteries | Item(s) stolen/No backup batteries.
IM760657 | 3916DE | 1191_S_BH-BAYDA-2_3916DE | Main power / weak batteries (BDT @ 18/10/2018 Is: 0.10) / PG in the way / was handling other sites BH-KOMBO_3978DE and BH-GWAD-HUS NI_3828DE / BH-GWAD-HUSNI_3828DE power back now and PG moved to BAYDA-2 | Faulty System | batt | Batteries | 355465 | BH-BAYDA-2 | C1_3916DE_PH14 | Batteries | Components faulty/faulty
IM760699 | 3413DE | 0801_D_PS-KHADIGA_3413DE | GN problem @PS-KHADIGA_3413DE / last BDT @ 28 OCT 2017 is 03:00 | Faulty System | GN | Generator | 335150 | PS-KHADIGA | C2_3413DE_PH13 | ATS / Engine | Components faulty/faulty
IM760699 | 3413DE | 0801_D_PS-KHADIGA_3413DE | GN problem @PS-KHADIGA_3413DE / last BDT @ 28 OCT 2017 is 03:00 | Faulty System | GN | Generator | 335150 | PS-KHADIGA | C2_3413DE_PH13 | ATS / Engine | Wrong connection/remove cable
IM760699 | 3413DE | 0801_D_PS-KHADIGA_3413DE | GN problem @PS-KHADIGA_3413DE / last BDT @ 28 OCT 2017 is 03:00 | Faulty System | GN | Generator | 335150 | PS-KHADIGA | C2_3413DE_PH13 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM760699 | 3413DE | 0801_D_PS-KHADIGA_3413DE | GN problem @PS-KHADIGA_3413DE / last BDT @ 28 OCT 2017 is 03:00 | Faulty System | GN | Generator | 324940 | PS-KHADIGA | C2_3413DE_PH13 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/Unused cable need to be removed.
IM760699 | 3413DE | 0801_D_PS-KHADIGA_3413DE | GN problem @PS-KHADIGA_3413DE / last BDT @ 28 OCT 2017 is 03:00 | Faulty System | GN | Generator | 324940 | PS-KHADIGA | C2_3413DE_PH13 | ATS / Engine | Panorama pictures for each system/Overview.
IM760710 | 3828DE | 0961_S_BH-GWAD-HUSNI_3828DE | Main power / stolen batteries / PG connected | Faulty System | batt | Batteries | 356184 | BH-GWAD-HUSNI | C1_3828DE_PH14 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM760740 | 3249DE | 0601_D_BH-TEROUGI_3249DE | GN problem / batteries under check | Faulty System | GN | Generator | 304212 | BH-TEROUGI | C2_3249DE_PH12 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Damaged cables isolation
IM760740 | 3249DE | 0601_D_BH-TEROUGI_3249DE | GN problem / batteries under check | Faulty System | GN | Generator | 304212 | BH-TEROUGI | C2_3249DE_PH12 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Burned terminal
IM760740 | 3249DE | 0601_D_BH-TEROUGI_3249DE | GN problem / batteries under check | Faulty System | GN | Generator | 304212 | BH-TEROUGI | C2_3249DE_PH12 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot
IM760759 | 0145SI | 01_G_SS-MR66-GYPSM2_0145SI | E// link problem , access TE after 4PM Emergency permission sent , once reset MMU Site recovered | Faulty System | Gen | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure
IM760759 | 0145SI | 01_G_SS-MR66-GYPSM2_0145SI | E// link problem , access TE after 4PM Emergency permission sent , once reset MMU Site recovered | Faulty System | Gen | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Wrong connection/generator battery as used in the site and not suitable in High temp
IM760795 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due DG dynamo problem and batt. not installed (I) | Faulty System | batt | Batteries | 314391 | REHAB-G17 | C1_3492CA_PH13 | Batteries | Some parts are missing/missing batteries
IM760795 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due DG dynamo problem and batt. not installed (I) | Faulty System | DG | Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | ATS / Engine | Wrong connection/wrong connection
IM760828 | 0760DE | 0151_Q_SK-JAWSAK-VLG_0760DE | GN problem/batteries under investigation/clear after check GN | Faulty System | GN | Generator | 345385 | SK-JAWSAK-VLG | C2_0760DE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has leakage
IM760828 | 0760DE | 0151_Q_SK-JAWSAK-VLG_0760DE | GN problem/batteries under investigation/clear after check GN | Faulty System | GN | Generator | 304032 | BH-SHANDID | C2_3464DE_PH13 | ATS / Engine | Components below rate (excluding main power feeder if not hot)/Generator voltage need adjustment
IM760867 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN problem @SK-MIT-GABIR_3833DE/GN working and cascaded site Dahmasha down on progress | Faulty System | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | ATS / Engine | Wrong connection/Welding cables
IM760867 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN problem @SK-MIT-GABIR_3833DE/GN working and cascaded site Dahmasha down on progress | Faulty System | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot
IM760885 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries Caused site Down , once team arrive and fix DG problem site recovered with cascaded | Faulty System | batt | Batteries | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | Batteries | Some parts are (missing / stolen)/Battery string stolen
IM760885 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries Caused site Down , once team arrive and fix DG problem site recovered with cascaded | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage
IM760885 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries Caused site Down , once team arrive and fix DG problem site recovered with cascaded | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Unit earth/Earth cable disconnected
IM760885 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries Caused site Down , once team arrive and fix DG problem site recovered with cascaded | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Components faulty/Generator indicator broken & not work
IM760885 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries Caused site Down , once team arrive and fix DG problem site recovered with cascaded | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Components faulty/Ventilation fan not work
IM760885 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries Caused site Down , once team arrive and fix DG problem site recovered with cascaded | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Power cable has no terminal
IM760896 | 0222RE | 03824_G_0222RE_RS-FLAMNCO-HTL | DG Stopped , stolen batteries Caused site Down , once team arrive and fix DG problem site recovered | Faulty System | DG | Generator | 355690 | 01_G_RS-FLAMNCO-HTL_0222RE | C1_0222RE_PH09 | ATS / Engine | Components faulty/need battery
IM760924 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN problem @SK-MIT-GABIR_3833DE/GN working | Faulty System | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | ATS / Engine | Wrong connection/Welding cables
IM760924 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN problem @SK-MIT-GABIR_3833DE/GN working | Faulty System | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot
IM760936 | 0041SI | L_S_SS-RAS-ABU-RDS_0041SI | DG Stopped , access Nigh H&S Recovered once DG problem solved | Faulty System | DG | Generator | 356372 | 01_H_SS-RAS-ABU-RDS_0041SI | C3_0041SI_PH2 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Genset oil leakage
IM760936 | 0041SI | L_S_SS-RAS-ABU-RDS_0041SI | DG Stopped , access Nigh H&S Recovered once DG problem solved | Faulty System | DG | Generator | 356372 | 01_H_SS-RAS-ABU-RDS_0041SI | C3_0041SI_PH2 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Air filter not found & fuel around the air filter housing
IM760936 | 0041SI | L_S_SS-RAS-ABU-RDS_0041SI | DG Stopped , access Nigh H&S Recovered once DG problem solved | Faulty System | DG | Generator | 356372 | 01_H_SS-RAS-ABU-RDS_0041SI | C3_0041SI_PH2 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel on the container floor
IM760936 | 0041SI | L_S_SS-RAS-ABU-RDS_0041SI | DG Stopped , access Nigh H&S Recovered once DG problem solved | Faulty System | DG | Generator | 356372 | 01_H_SS-RAS-ABU-RDS_0041SI | C3_0041SI_PH2 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Unclean V.F genset area
IM760936 | 0041SI | L_S_SS-RAS-ABU-RDS_0041SI | DG Stopped , access Nigh H&S Recovered once DG problem solved | Faulty System | DG | Generator | 356372 | 01_H_SS-RAS-ABU-RDS_0041SI | C3_0041SI_PH2 | ATS / Engine | Components faulty/Defected genset battery
IM760936 | 0041SI | L_S_SS-RAS-ABU-RDS_0041SI | DG Stopped , access Nigh H&S Recovered once DG problem solved | Faulty System | DG | Generator | 356372 | 01_H_SS-RAS-ABU-RDS_0041SI | C3_0041SI_PH2 | ATS / Engine | Components faulty/Cables damage isolation & bad connections
IM760936 | 0041SI | L_S_SS-RAS-ABU-RDS_0041SI | DG Stopped , access Nigh H&S Recovered once DG problem solved | Faulty System | DG | Generator | 356372 | 01_H_SS-RAS-ABU-RDS_0041SI | C3_0041SI_PH2 | ATS / Engine | Wrong connection/Wrong cables connections , use double terminals
IM760936 | 0041SI | L_S_SS-RAS-ABU-RDS_0041SI | DG Stopped , access Nigh H&S Recovered once DG problem solved | Faulty System | DG | Generator | 356372 | 01_H_SS-RAS-ABU-RDS_0041SI | C3_0041SI_PH2 | ATS / Engine | Wrong connection/A.C / D.C converted used as a charger in the genset
IM760936 | 0041SI | L_S_SS-RAS-ABU-RDS_0041SI | DG Stopped , access Nigh H&S Recovered once DG problem solved | Faulty System | DG | Generator | 356372 | 01_H_SS-RAS-ABU-RDS_0041SI | C3_0041SI_PH2 | ATS / Engine | Wrong connection/Deep cycle battery used as a starter in the genset
IM760936 | 0041SI | L_S_SS-RAS-ABU-RDS_0041SI | DG Stopped , access Nigh H&S Recovered once DG problem solved | Faulty System | DG | Generator | 356372 | 01_H_SS-RAS-ABU-RDS_0041SI | C3_0041SI_PH2 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Missing ATS cables terminals
IM760936 | 0041SI | L_S_SS-RAS-ABU-RDS_0041SI | DG Stopped , access Nigh H&S Recovered once DG problem solved | Faulty System | DG | Generator | 356372 | 01_H_SS-RAS-ABU-RDS_0041SI | C3_0041SI_PH2 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Remain cables & terminals in the genset gauage indicators box
IM760939 | 0648DE | 0381_S_BH-IZ-HUSNI_0648DE | Main power @BH-IZ-HUSNI_0648DE / weak batteries / PG connected | Faulty System | batt | Batteries | 355858 | Ez Hosny LH | C1_0648DE_PH9_TRN | Batteries | Some parts are (missing / stolen)/stolen batteries
IM760939 | 0648DE | 0381_S_BH-IZ-HUSNI_0648DE | Main power @BH-IZ-HUSNI_0648DE / weak batteries / PG connected | Faulty System | batt | Batteries | 355857 | BH-IZ-HUSNI | C1_0648DE_PH9 | Batteries | Some parts are (missing / stolen)/stolen batteries
IM760949 | 0285DE | K_BH-ABU-HUMMUS_20855_1 | GN problem @ BH-ABU-HUMMUS_0285DE / weak batteries / Last BDT at 25-Oct-18 is 2 Hrs | Faulty System | batt | Batteries | 345403 | BASHTEL-ST | C3_3130CA_PH9 | Rectifiers | Alarms reporting to the OMC/Minor alarm due to temprature measurement doesn't appear on the OMC (Loop in DDF)
IM760949 | 0285DE | K_BH-ABU-HUMMUS_20855_1 | GN problem @ BH-ABU-HUMMUS_0285DE / weak batteries / Last BDT at 25-Oct-18 is 2 Hrs | Faulty System | batt | Batteries | 345403 | BASHTEL-ST | C3_3130CA_PH9 | Batteries | Some parts are (missing / stolen)/All batteries are stolen
IM760951 | 3955DE | 0731_S_SK-QRMT-SAHBRA_3955DE | access ET/ET GN problem/batteries under investigation//Stolen batteires | Faulty System | batt | Batteries | 356230 | SK-QRMT-SAHBRA | C1_3955DE_PH15 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM760979 | 0095SI | 0201_S_SS-SUN-MON-STR_0095SI | utage power in area located site , dead batteries , access PG Auto-Recovered once power restored | Faulty System | batt | Batteries | 355557 | 01_S_SS-SUN-MON-STR_0095SI | C1_0095SI_PH03 | Batteries | Components faulty/salty battery pole
IM761012 | 0954UP | 01_G_MN-DAHMARU_0954UP | Commercial power cutoff and stolen backup batteries EC power recovered and site back on air | Faulty System | backup | Batteries | 324946 | 01_G_MN-DAHMARU_0954UP | C1_0954UP_PH12 | Batteries | Item(s) stolen/site baateries were stolen
IM761012 | 0954UP | 01_G_MN-DAHMARU_0954UP | Commercial power cutoff and stolen backup batteries EC power recovered and site back on air | Faulty System | batt | Batteries | 324946 | 01_G_MN-DAHMARU_0954UP | C1_0954UP_PH12 | Batteries | Item(s) stolen/site baateries were stolen
IM761047 | 3555CA | 00042_L_3555CA_SAMA-TOWER | down due to DG problem and stolen batteries (MA) | Faulty System | batt | Batteries | 345256 | SAMA-TOWER | C2_3555CA_PH13 | Batteries | Some parts are missing/missing batteries
IM761047 | 3555CA | 00042_L_3555CA_SAMA-TOWER | down due to DG problem and stolen batteries (MA) | Faulty System | DG | Generator | 345256 | SAMA-TOWER | C2_3555CA_PH13 | ATS / Engine | Wrong connection/welded cables
IM761047 | 3555CA | 00042_L_3555CA_SAMA-TOWER | down due to DG problem and stolen batteries (MA) | Faulty System | DG | Generator | 345256 | SAMA-TOWER | C2_3555CA_PH13 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage
IM761055 | 0615DE | K_GH-KFR-BAB_20860_1 | Main power/Stolen batteries @GH-KFR-BAB_0615DE/clear after power back | Faulty System | batt | Batteries | 314420 | GH-KFR-BAB | C15_0615DE_PH14 | Batteries | Item(s) stolen/stolen batteries
IM761078 | 0016UP | 00276_I_0016UP_DES1 | down due to DG problem and weak batteries (MA) | Faulty System | DG | Generator | 324979 | DES1 | C2_0016UP_PH0 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage
IM761084 | 0479DE | 0591_S_DK-MNS-FRSKOR1_0479DE | Main power @ DK-MNS-FRSKOR1_0479DE / stolen batteries / Connect PG | Faulty System | batt | Batteries | 356389 | DK-MNS-FRSKOR1 | C3_0479DE_PH7 | Batteries | Some parts are (missing / stolen)/stolen batteries
IM761109 | 3892DE | 0171_S_BH-ZWIT-HUMOR_3892DE | Main power / stolen batteries | Faulty System | batt | Batteries | 324905 | BH-ZWIT-HUMOR | C1_3892DE_PH14 | Batteries | Item(s) stolen/There is no battery for site
IM761114 | 3191DE | 0971_D_GH-BALQINA_3191DE | GN problem / stolen batteries | Faulty System | batt | Batteries | 304240 | GH-BALQINA | C4_3191DE_PH12 | Batteries | Item(s) stolen/stolen batteries
IM761114 | 3191DE | 0971_D_GH-BALQINA_3191DE | GN problem / stolen batteries | Faulty System | GN | Generator | 304240 | GH-BALQINA | C4_3191DE_PH12 | ATS / Engine | Components faulty/connect and check
IM761114 | 3191DE | 0971_D_GH-BALQINA_3191DE | GN problem / stolen batteries | Faulty System | GN | Generator | 304240 | GH-BALQINA | C4_3191DE_PH12 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/sharp edges
IM761114 | 3191DE | 0971_D_GH-BALQINA_3191DE | GN problem / stolen batteries | Faulty System | GN | Generator | 304240 | GH-BALQINA | C4_3191DE_PH12 | ATS / Engine | Item(s) stolen/stolen battery
IM761114 | 3191DE | 0971_D_GH-BALQINA_3191DE | GN problem / stolen batteries | Faulty System | GN | Generator | 304240 | GH-BALQINA | C4_3191DE_PH12 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage
IM761119 | 3352DE | 0071_D_BH-SHBRA-OSEEM_3352DE | Main power/stolen batteries/clear on P.G | Faulty System | batt | Batteries | 325117 | BH-SHBRA-OSEEM | C1_3352DE_PH12 | Batteries | Item(s) stolen/There is no battery for site
IM761164 | 3765UP | 2251_S_SG-NAGA-ELNGAR_3765UP | Main power disconnection , Stolen batteries , P.G connected | Faulty System | batt | Batteries | 345419 | 01_S_SG-NAGA-ELNGAR_3765UP | C1_3765UP_PH15 | Batteries | Some parts are (missing / stolen)/batteries were stolen
IM761177 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem & no backup & access VF (T) | Faulty System | backup | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | Batteries | Some parts are (missing / stolen)/missing battereis
IM761287 | 3454DE | 1061_D_GH-MAHLT-MENOF_3454DE | ET Share / GN problem / Stolen batteries | Faulty System | batt | Batteries | 324838 | GH-MAHLT-MENOF | C2_3454DE_PH13 | Batteries | Item(s) stolen/Stolen Batteries
IM761287 | 3454DE | 1061_D_GH-MAHLT-MENOF_3454DE | ET Share / GN problem / Stolen batteries | Faulty System | GN | Generator | 324838 | GH-MAHLT-MENOF | C2_3454DE_PH13 | ATS / Engine | Item(s) stolen/stolen batteries
IM761287 | 3454DE | 1061_D_GH-MAHLT-MENOF_3454DE | ET Share / GN problem / Stolen batteries | Faulty System | GN | Generator | 324838 | GH-MAHLT-MENOF | C2_3454DE_PH13 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM761293 | 3191DE | 0971_D_GH-BALQINA_3191DE | GN problem / stolen batteries / Team waiting guard / and follow with SOC / connect PG | Faulty System | batt | Batteries | 304240 | GH-BALQINA | C4_3191DE_PH12 | Batteries | Item(s) stolen/stolen batteries
IM761293 | 3191DE | 0971_D_GH-BALQINA_3191DE | GN problem / stolen batteries / Team waiting guard / and follow with SOC / connect PG | Faulty System | GN | Generator | 304240 | GH-BALQINA | C4_3191DE_PH12 | ATS / Engine | Components faulty/connect and check
IM761293 | 3191DE | 0971_D_GH-BALQINA_3191DE | GN problem / stolen batteries / Team waiting guard / and follow with SOC / connect PG | Faulty System | GN | Generator | 304240 | GH-BALQINA | C4_3191DE_PH12 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/sharp edges
IM761293 | 3191DE | 0971_D_GH-BALQINA_3191DE | GN problem / stolen batteries / Team waiting guard / and follow with SOC / connect PG | Faulty System | GN | Generator | 304240 | GH-BALQINA | C4_3191DE_PH12 | ATS / Engine | Item(s) stolen/stolen battery
IM761293 | 3191DE | 0971_D_GH-BALQINA_3191DE | GN problem / stolen batteries / Team waiting guard / and follow with SOC / connect PG | Faulty System | GN | Generator | 304240 | GH-BALQINA | C4_3191DE_PH12 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage
IM761296 | 3943DE | 0921_S_SK-AKRASH_3943DE | access ET/ET GN problem/Stolen batteries@SK-AKRASH_3943DE/clear on P.G | Faulty System | batt | Batteries | 303886 | SK-AKRASH | C1_3943DE_PH15 | Batteries | Item(s) stolen/No backup batteries.
IM761339 | 0339UP | 0351_G_MN-SALEEBA_0339UP | Generator stopped , Site has weak backup batteries , Recovered | Faulty System | Gen | Generator | 324684 | 01_G_MN-SALEEBA_0339UP | C3_0339UP_PH8 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/protect cable
IM761339 | 0339UP | 0351_G_MN-SALEEBA_0339UP | Generator stopped , Site has weak backup batteries , Recovered | Faulty System | generator | Generator | 324684 | 01_G_MN-SALEEBA_0339UP | C3_0339UP_PH8 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/protect cable
IM761339 | 0339UP | 0351_G_MN-SALEEBA_0339UP | Generator stopped , Site has weak backup batteries , Recovered | Faulty System | Gen | Generator | 324684 | 01_G_MN-SALEEBA_0339UP | C3_0339UP_PH8 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage
IM761339 | 0339UP | 0351_G_MN-SALEEBA_0339UP | Generator stopped , Site has weak backup batteries , Recovered | Faulty System | generator | Generator | 324684 | 01_G_MN-SALEEBA_0339UP | C3_0339UP_PH8 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage
IM761358 | 3775DE | 0471_D_DK-DABBOS-VLG_3775DE | GN problem / BDT @ 09/09/2018 Is: 3.00 / Team work at site | Faulty System | GN | Generator | 325073 | DK-DABBOS-VLG | C1_3775DE_PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/bad terminals
IM761358 | 3775DE | 0471_D_DK-DABBOS-VLG_3775DE | GN problem / BDT @ 09/09/2018 Is: 3.00 / Team work at site | Faulty System | GN | Generator | 325073 | DK-DABBOS-VLG | C1_3775DE_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM761421 | 0618DE | 0101_G_GH-SAFT-TURAB_0618DE | Main power problem / SB GN stopped / Weak batteries BDT @ 19/11/2018 Is: 1.00/ Connect PG | Faulty System | GN | Generator | 324605 | GH-SAFT-TURAB | C11_0618DE_PH09 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Clean
IM761488 | 3943DE | 0921_S_SK-AKRASH_3943DE | access ET/ET GN problem/Stolen batteries@SK-AKRASH_3943DE | Faulty System | batt | Batteries | 303886 | SK-AKRASH | C1_3943DE_PH15 | Batteries | Item(s) stolen/No backup batteries.
IM761553 | 3955DE | 0731_S_SK-QRMT-SAHBRA_3955DE | access ET/ET GN problem/Stolen batteries | Faulty System | batt | Batteries | 356230 | SK-QRMT-SAHBRA | C1_3955DE_PH15 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM761576 | 0411RE | 03870_S_0411RE_RS-BRAYKA-BAY | DG Stopped , stolen batteries Caused site Down , once team arrive and fix DG problem site recovered | Faulty System | batt | Batteries | 356418 | 01_S_RS-BRAYKA-BAY_0411RE | C1_0411RE_PH15 | Batteries | Some parts are (missing / stolen)/Batteries were stolen
IM761576 | 0411RE | 03870_S_0411RE_RS-BRAYKA-BAY | DG Stopped , stolen batteries Caused site Down , once team arrive and fix DG problem site recovered | Faulty System | DG | Generator | 356418 | 01_S_RS-BRAYKA-BAY_0411RE | C1_0411RE_PH15 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Open gland in Gen enclosure need insulation
IM761576 | 0411RE | 03870_S_0411RE_RS-BRAYKA-BAY | DG Stopped , stolen batteries Caused site Down , once team arrive and fix DG problem site recovered | Faulty System | DG | Generator | 356418 | 01_S_RS-BRAYKA-BAY_0411RE | C1_0411RE_PH15 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Two cables inserted in one slot and not teminated can cause bad connections
IM761582 | 3681DE | 1781_D_BH-MNSHYT-HMOR_3681DE | Access Guard " 1638 " / GN problem / Weak batteries | Faulty System | GN | Generator | 355781 | BH-MNSHAT-HMOR | C5_3681DE_PH13 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals requried
IM761582 | 3681DE | 1781_D_BH-MNSHYT-HMOR_3681DE | Access Guard " 1638 " / GN problem / Weak batteries | Faulty System | GN | Generator | 355781 | BH-MNSHAT-HMOR | C5_3681DE_PH13 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminal requried
IM761599 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries Caused site Down , once team arrive and fix DG problem site recovered with cascaded | Faulty System | batt | Batteries | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | Batteries | Some parts are (missing / stolen)/Battery string stolen
IM761599 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries Caused site Down , once team arrive and fix DG problem site recovered with cascaded | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage
IM761599 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries Caused site Down , once team arrive and fix DG problem site recovered with cascaded | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Unit earth/Earth cable disconnected
IM761599 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries Caused site Down , once team arrive and fix DG problem site recovered with cascaded | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Components faulty/Generator indicator broken & not work
IM761599 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries Caused site Down , once team arrive and fix DG problem site recovered with cascaded | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Components faulty/Ventilation fan not work
IM761599 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries Caused site Down , once team arrive and fix DG problem site recovered with cascaded | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Power cable has no terminal
IM761655 | 3791DE | 1671_D_SK-ABU-HARIZ_3791DE | main Power / Stolen Batteries / clear after power back | Faulty System | batt | Batteries | 335162 | SK-ABU-HARIZ | C2_3791DE_PH14 | Batteries | Item(s) stolen/No backup batteries.
IM761657 | 0682DE | 0861_S_MF-TAHA-SHBRA2_0682DE | access T.E/Hi temp/clear after check | Faulty System | Hi Temp | A/Cs | 324623 | MF- TAHA-SHBRA2 | C1_0682DE_PH9 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/check
IM761657 | 0682DE | 0861_S_MF-TAHA-SHBRA2_0682DE | access T.E/Hi temp/clear after check | Faulty System | Hi Temp | A/Cs | 324623 | MF- TAHA-SHBRA2 | C1_0682DE_PH9 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/faulty A/C2
IM761662 | 3435DE | 1531_S_SK-AMRIT_3435DE | main Power / Weak Batteries / clear after power back | Faulty System | batt | Batteries | 324455 | SK-AMRIT | C1-3435DE-PH13 | Batteries | Components faulty/Batteries can't carry site.
IM761671 | 3751DE | 0021_S_DK-SHRKA2-VLG_3751DE | Main power / stolen batteries / PG connected | Faulty System | batt | Batteries | 304052 | DK-SHRKA2-VLG | C1_3751DE_PH14 | Batteries | Item(s) stolen/No backup batteries.
IM761675 | 2083DE | 0021_S_GH-M-KITCHENER_2083DE | Access Corp. " Kher Zaman - Hypermarket " /Main power / HDSL not secured / Weak batteries | Faulty System | batt | Batteries | 324872 | GH-M-KITCHENER | C1_2083DE_PH16 | Batteries | Some parts are missing/Clean and add poles covers
IM761675 | 2083DE | 0021_S_GH-M-KITCHENER_2083DE | Access Corp. " Kher Zaman - Hypermarket " /Main power / HDSL not secured / Weak batteries | Faulty System | batt | Batteries | 324872 | GH-M-KITCHENER | C1_2083DE_PH16 | Batteries | Some parts are missing/Clean and add covers
IM761726 | 0735DE | 0711_G_GH-TANTA-HW2_0735DE | Main power @ GH-TANTA-HW2_0735DE / Stolen batteries | Faulty System | batt | Batteries | 324537 | GH-TANTA-HW2 | C1_0735DE_PH9 | Batteries | Item(s) stolen/There is no battery for site
IM761753 | 3333DE | 0181_S_BH-OM-SABER_3333DE | main Power / Stolen Batteries / clear after power back | Faulty System | batt | Batteries | 304089 | BH-OM-SABER_SSS0 | C1_3333DE_PH12 | Batteries | Item(s) stolen/There is no battery for site
IM761755 | 3756DE | 1121_D_SK-HALAWAT_3756DE | GN problem/ batteries under investigation @SK-HALAWAT_3756DE/GN working | Faulty System | GN | Generator | 304142 | SK-HALAWAT | C1-3756DE-PH14 | ATS / Engine | Components faulty/Generator has bad condition and needs overhaul.
IM761755 | 3756DE | 1121_D_SK-HALAWAT_3756DE | GN problem/ batteries under investigation @SK-HALAWAT_3756DE/GN working | Faulty System | GN | Generator | 304142 | SK-HALAWAT | C1-3756DE-PH14 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/Sensor cables need replacement.
IM761755 | 3756DE | 1121_D_SK-HALAWAT_3756DE | GN problem/ batteries under investigation @SK-HALAWAT_3756DE/GN working | Faulty System | GN | Generator | 304142 | SK-HALAWAT | C1-3756DE-PH14 | ATS / Engine | Cables/Feeders/Jumpers/Coaxial/FO/PCM connection tightness/Neutral bar need fixation.
IM761755 | 3756DE | 1121_D_SK-HALAWAT_3756DE | GN problem/ batteries under investigation @SK-HALAWAT_3756DE/GN working | Faulty System | GN | Generator | 304142 | SK-HALAWAT | C1-3756DE-PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/ATS cables need proper terminals.
IM761755 | 3756DE | 1121_D_SK-HALAWAT_3756DE | GN problem/ batteries under investigation @SK-HALAWAT_3756DE/GN working | Faulty System | GN | Generator | 304142 | SK-HALAWAT | C1-3756DE-PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has a lot of leakage.
IM761757 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries , , Recovered once DG fix | Faulty System | batt | Batteries | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | Batteries | Some parts are (missing / stolen)/Battery string stolen
IM761757 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries , , Recovered once DG fix | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage
IM761757 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries , , Recovered once DG fix | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Unit earth/Earth cable disconnected
IM761757 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries , , Recovered once DG fix | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Components faulty/Generator indicator broken & not work
IM761757 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries , , Recovered once DG fix | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Components faulty/Ventilation fan not work
IM761757 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries , , Recovered once DG fix | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Power cable has no terminal
IM761764 | 0140AL | U_S_0140AL_ABOUYOUSIF-WST | main power problem / weak batteries / commercial power auto recovered | Faulty System | batt | Batteries | 304353 | ABU_YOUSSEF_WEST | C1_0140AL_PH3 | Batteries | Item(s) stolen/Stolen batteries
IM761768 | 0975UP | 0381_S_BS-MASID-ABYAD_0975UP_X | Commercial power cutoff and stolen backup batteries P.G connected and site back on air | Faulty System | backup | Batteries | 356360 | 01_S_BS-MASID-ABYAD_0975UP | C1_0975UP_PH12 | Rectifiers | Alarms reporting to the OMC/Minor alarm doesn't appear on the OMC
IM761768 | 0975UP | 0381_S_BS-MASID-ABYAD_0975UP_X | Commercial power cutoff and stolen backup batteries P.G connected and site back on air | Faulty System | batt | Batteries | 356360 | 01_S_BS-MASID-ABYAD_0975UP | C1_0975UP_PH12 | Rectifiers | Alarms reporting to the OMC/Minor alarm doesn't appear on the OMC
IM761768 | 0975UP | 0381_S_BS-MASID-ABYAD_0975UP_X | Commercial power cutoff and stolen backup batteries P.G connected and site back on air | Faulty System | backup | Batteries | 356360 | 01_S_BS-MASID-ABYAD_0975UP | C1_0975UP_PH12 | Batteries | Some parts are (missing / stolen)/Batteries and cables are stolen
IM761768 | 0975UP | 0381_S_BS-MASID-ABYAD_0975UP_X | Commercial power cutoff and stolen backup batteries P.G connected and site back on air | Faulty System | batt | Batteries | 356360 | 01_S_BS-MASID-ABYAD_0975UP | C1_0975UP_PH12 | Batteries | Some parts are (missing / stolen)/Batteries and cables are stolen
IM761770 | 3807UP | 0631_D_QN-MHAMID-QBLY_3807UP | due to Generator problem, stolen batteries in site QN-MHAMID-QBLY_3807UP, P.G connected | Faulty System | batt | Batteries | 355794 | 01_G_QN-MHAMID-QBLY_3807UP | C1_3807UP_PH15 | Rectifiers | Alarms reporting to the OMC/Rectifier minor alarm was looped at ddf
IM761770 | 3807UP | 0631_D_QN-MHAMID-QBLY_3807UP | due to Generator problem, stolen batteries in site QN-MHAMID-QBLY_3807UP, P.G connected | Faulty System | Gen | Generator | 355794 | 01_G_QN-MHAMID-QBLY_3807UP | C1_3807UP_PH15 | ATS / Engine | Unit earth/Earth bar is missing
IM761770 | 3807UP | 0631_D_QN-MHAMID-QBLY_3807UP | due to Generator problem, stolen batteries in site QN-MHAMID-QBLY_3807UP, P.G connected | Faulty System | generator | Generator | 355794 | 01_G_QN-MHAMID-QBLY_3807UP | C1_3807UP_PH15 | ATS / Engine | Unit earth/Earth bar is missing
IM761770 | 3807UP | 0631_D_QN-MHAMID-QBLY_3807UP | due to Generator problem, stolen batteries in site QN-MHAMID-QBLY_3807UP, P.G connected | Faulty System | Gen | Generator | 355794 | 01_G_QN-MHAMID-QBLY_3807UP | C1_3807UP_PH15 | ATS / Engine | Components faulty/Gen enclosure Screen press keys were defected
IM761770 | 3807UP | 0631_D_QN-MHAMID-QBLY_3807UP | due to Generator problem, stolen batteries in site QN-MHAMID-QBLY_3807UP, P.G connected | Faulty System | generator | Generator | 355794 | 01_G_QN-MHAMID-QBLY_3807UP | C1_3807UP_PH15 | ATS / Engine | Components faulty/Gen enclosure Screen press keys were defected
IM761770 | 3807UP | 0631_D_QN-MHAMID-QBLY_3807UP | due to Generator problem, stolen batteries in site QN-MHAMID-QBLY_3807UP, P.G connected | Faulty System | Gen | Generator | 355794 | 01_G_QN-MHAMID-QBLY_3807UP | C1_3807UP_PH15 | ATS / Engine | Filters condition oil/fuel/air/Air Filter cover is not fixed
IM761770 | 3807UP | 0631_D_QN-MHAMID-QBLY_3807UP | due to Generator problem, stolen batteries in site QN-MHAMID-QBLY_3807UP, P.G connected | Faulty System | generator | Generator | 355794 | 01_G_QN-MHAMID-QBLY_3807UP | C1_3807UP_PH15 | ATS / Engine | Filters condition oil/fuel/air/Air Filter cover is not fixed
IM761796 | 3894CA | 02231_S_3894CA_REHAB-STAGE7 | down due to VF DG problem & stolen batteries & access VF (T) | Faulty System | batt | Batteries | 356204 | REHAB-STAGE7 | C1_3894CA_PH17 | Batteries | Some parts are (missing / stolen)/missing batteries
IM761799 | 3828DE | 0961_S_BH-GWAD-HUSNI_3828DE | Main Powr problem / stolen batteries | Faulty System | batt | Batteries | 356184 | BH-GWAD-HUSNI | C1_3828DE_PH14 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM761808 | 3414UP | 0401_S_BS-AHWA_3414UP_X | Commercial power cutoff and weak backup batteries P.G connected ad site back on air | Faulty System | backup | Batteries | 356350 | 01_S_BS-AHWA_3414UP | C1_3414UP_PH14 | Rectifiers | Alarms reporting to the OMC/Loop on the major alarm in DDF
IM761808 | 3414UP | 0401_S_BS-AHWA_3414UP_X | Commercial power cutoff and weak backup batteries P.G connected ad site back on air | Faulty System | batt | Batteries | 356350 | 01_S_BS-AHWA_3414UP | C1_3414UP_PH14 | Rectifiers | Alarms reporting to the OMC/Loop on the major alarm in DDF
IM761808 | 3414UP | 0401_S_BS-AHWA_3414UP_X | Commercial power cutoff and weak backup batteries P.G connected ad site back on air | Faulty System | backup | Batteries | 356350 | 01_S_BS-AHWA_3414UP | C1_3414UP_PH14 | Batteries | Components faulty/Batteries are faulty and site is down after less than one hour of power disconnected
IM761808 | 3414UP | 0401_S_BS-AHWA_3414UP_X | Commercial power cutoff and weak backup batteries P.G connected ad site back on air | Faulty System | batt | Batteries | 356350 | 01_S_BS-AHWA_3414UP | C1_3414UP_PH14 | Batteries | Components faulty/Batteries are faulty and site is down after less than one hour of power disconnected
IM761872 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN problem/stolen batteries @MIT-GABIR_3833DE/GN working | Faulty System | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | ATS / Engine | Wrong connection/Welding cables
IM761872 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN problem/stolen batteries @MIT-GABIR_3833DE/GN working | Faulty System | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot
IM761873 | 0734DE | 0441_D_MF-TANTA-HW1_0734DE | GN problem / solar theft case / stolen batteries / PG connected | Faulty System | batt | Batteries | 356142 | MF-TANTA-HW1 | C1_0734DE_PH9 | Rectifiers | Alarms reporting to the OMC/Site has fake power alarm
IM761873 | 0734DE | 0441_D_MF-TANTA-HW1_0734DE | GN problem / solar theft case / stolen batteries / PG connected | Faulty System | batt | Batteries | 356142 | MF-TANTA-HW1 | C1_0734DE_PH9 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM761873 | 0734DE | 0441_D_MF-TANTA-HW1_0734DE | GN problem / solar theft case / stolen batteries / PG connected | Faulty System | GN | Generator | 356142 | MF-TANTA-HW1 | C1_0734DE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has leakage
IM761895 | 3290DE | 1171_D_MF-QATTA_3290DE | GN problem/batteries not installed / clear after GN working(Fuel PUMP) | Faulty System | GN | Generator | 355961 | MF-QATTA | C3_3290DE_PH12 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has leakage
IM761895 | 3290DE | 1171_D_MF-QATTA_3290DE | GN problem/batteries not installed / clear after GN working(Fuel PUMP) | Faulty System | GN | Generator | 355961 | MF-QATTA | C3_3290DE_PH12 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals requried
IM761895 | 3290DE | 1171_D_MF-QATTA_3290DE | GN problem/batteries not installed / clear after GN working(Fuel PUMP) | Faulty System | GN | Generator | 355961 | MF-QATTA | C3_3290DE_PH12 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Cable need to be terminated well
IM761918 | 0595DE | 0281_G_DK-NISHA_0595DE | Main power /weak batteries (BDT @ 30/07/2018 Is: 3.00) | Faulty System | batt | Batteries | 324924 | DK-NISHAA | C1_0595DE_PH9 | Batteries | Some parts are missing/cover
IM761926 | 3775DE | 0471_D_DK-DABBOS-VLG_3775DE | GN problem / BDT @ 09/09/2018 Is: 3.00 under check | Faulty System | GN | Generator | 325073 | DK-DABBOS-VLG | C1_3775DE_PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/bad terminals
IM761926 | 3775DE | 0471_D_DK-DABBOS-VLG_3775DE | GN problem / BDT @ 09/09/2018 Is: 3.00 under check | Faulty System | GN | Generator | 325073 | DK-DABBOS-VLG | C1_3775DE_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM761937 | 0375UP | 0561_N_CAIRO-ASWAN-17_0375UP | Main power disconnection , stolen batteries , ETS owner access problem ( Unreachable ) , Recovered after EC power back . | Faulty System | batt | Batteries | 324845 | 01_A_CAIRO-ASWAN-17_0375UP | C1_0375UP_PH8 | Batteries | Item(s) stolen/Batteries were stolen
IM761949 | 4021DE | 0181_S_BH-ABQAEEN_4021DE | Access VF Guard payment problem / Expected Main C.B switched off / Stolen batteries / Power exist at site area / Call VF office ma nager can't support / Call Mr. Hossam told inform Mabrouk/ calling Bolaky | Faulty System | batt | Batteries | 304224 | BH-ABQAEEN | C1_4021DE_PH15 | Batteries | Item(s) stolen/There is no battery for site
IM761951 | 3955DE | 0731_S_SK-QRMT-SAHBRA_3955DE | ET gen problem/ battery under invistoigation/ ET GN working | Faulty System | batt | Batteries | 356230 | SK-QRMT-SAHBRA | C1_3955DE_PH15 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM761960 | 0435UP | 02_G_SG-GAZAZRA_0435UP | Main power disconnnection , stolen batteries , P.G connected | Faulty System | batt | Batteries | 325007 | 01_G_SG-GAZAZRA_0435UP | C1_0435UP_PH9 | Batteries | Item(s) stolen/site batteries were stolen
IM761960 | 0435UP | 02_G_SG-GAZAZRA_0435UP | Main power disconnnection , stolen batteries , P.G connected | Faulty System | batt | Batteries | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | Batteries | Item(s) stolen/Batteries were stolen
IM761972 | 0127DE | 0061_H_GH-MRO4-QUTUR_0127DE | Main power @ GH-MR04-QUTUR_0127DE / Stolen batteries / Connect PG / Cells Hanged / Split request | Faulty System | batt | Batteries | 304205 | 9_S_GH-MR04-QUTUR_0127DE_SS00 | C4_0127DE_PH2 | Batteries | Item(s) stolen/stolen batteries
IM761990 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage of the engine
IM761990 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage of the engine
IM761990 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Unit earth/Stolen earth connections of the genset panel
IM761990 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Unit earth/Stolen earth connections of the genset panel
IM761990 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Components faulty/The rubber bases of the radiator are faulty
IM761990 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Components faulty/The rubber bases of the radiator are faulty
IM761990 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Components faulty/The dynamo belt needs to be tensioned
IM761990 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Components faulty/The dynamo belt needs to be tensioned
IM761990 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Wrong connection/The negative pole of the battery isn't connected
IM761990 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Wrong connection/The negative pole of the battery isn't connected
IM761990 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Missing terminals of cables connected to contactors and CBs inside the genset panel
IM761990 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Missing terminals of cables connected to contactors and CBs inside the genset panel
IM761993 | 0240RE | 03485_S_0240RE_SZ-SUEZ-NTH | Outage power in area located site , access PG , dead batteries once power restored site Recovered | Faulty System | batt | Batteries | 355923 | 01_S_SZ-SUEZ-NTH_0240RE | C1_0240RE_PH9 | Rectifiers | Alarms reporting to the OMC/Rectifier Major & Minor , A/C & door alarm not appear on CAP
IM761994 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Due to Generator problem , Stolen batteries , Recovered | Faulty System | Gen | Generator | 355484 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM761994 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Due to Generator problem , Stolen batteries , Recovered | Faulty System | generator | Generator | 355484 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM761994 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Due to Generator problem , Stolen batteries , Recovered | Faulty System | Gen | Generator | 355484 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Unit earth/fake earth
IM761994 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Due to Generator problem , Stolen batteries , Recovered | Faulty System | generator | Generator | 355484 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Unit earth/fake earth
IM761994 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Due to Generator problem , Stolen batteries , Recovered | Faulty System | Gen | Generator | 355484 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Components faulty/faulty
IM761994 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Due to Generator problem , Stolen batteries , Recovered | Faulty System | generator | Generator | 355484 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Components faulty/faulty
IM761994 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Due to Generator problem , Stolen batteries , Recovered | Faulty System | Gen | Generator | 355484 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Components faulty/replace
IM761994 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Due to Generator problem , Stolen batteries , Recovered | Faulty System | generator | Generator | 355484 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Components faulty/replace
IM761994 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Due to Generator problem , Stolen batteries , Recovered | Faulty System | Gen | Generator | 304381 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Cables at 1 slot
IM761994 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Due to Generator problem , Stolen batteries , Recovered | Faulty System | generator | Generator | 304381 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Cables at 1 slot
IM761994 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Due to Generator problem , Stolen batteries , Recovered | Faulty System | Gen | Generator | 304381 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot
IM761994 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Due to Generator problem , Stolen batteries , Recovered | Faulty System | generator | Generator | 304381 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot
IM762000 | 4005DE | 0751_D_DK-BASHALOSH_4005DE | GN problem/ batteries under invistgation /GN working | Faulty System | GN | Generator | 356229 | DK-BASHALOSH | C4_4005DE_PH15 | ATS / Engine | Unit earth/Disconnected earth cable.
IM762000 | 4005DE | 0751_D_DK-BASHALOSH_4005DE | GN problem/ batteries under invistgation /GN working | Faulty System | GN | Generator | 356229 | DK-BASHALOSH | C4_4005DE_PH15 | ATS / Engine | Components faulty/Battery poles need cleaning, wax and covers.
IM762000 | 4005DE | 0751_D_DK-BASHALOSH_4005DE | GN problem/ batteries under invistgation /GN working | Faulty System | GN | Generator | 356229 | DK-BASHALOSH | C4_4005DE_PH15 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Neutral bar need adjust.
IM762000 | 4005DE | 0751_D_DK-BASHALOSH_4005DE | GN problem/ batteries under invistgation /GN working | Faulty System | GN | Generator | 356229 | DK-BASHALOSH | C4_4005DE_PH15 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Some cables need proper terminals.
IM762004 | 0983DE | 1771_S_DK-MIT-ANTAR_0983DE | Main power / Stolen batteries | Faulty System | batt | Batteries | 324896 | DK-MIT-ANTAR | C8_0983DE_PH11 | Batteries | Item(s) stolen/stolen batteries
IM762005 | 3681DE | 1781_D_BH-MNSHYT-HMOR_3681DE | GN problem / Weak batteries | Faulty System | GN | Generator | 355781 | BH-MNSHAT-HMOR | C5_3681DE_PH13 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals requried
IM762005 | 3681DE | 1781_D_BH-MNSHYT-HMOR_3681DE | GN problem / Weak batteries | Faulty System | GN | Generator | 355781 | BH-MNSHAT-HMOR | C5_3681DE_PH13 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminal requried
IM762024 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Main power / Stolen batteries / VF Share | Faulty System | batt | Batteries | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | Batteries | Item(s) stolen/Stolen
IM762028 | 0324UP | 1421_S_MN-BARTABAT_0324UP | Due to EC power cutoff , Stolen batteries , PG Connected | Faulty System | batt | Batteries | 324919 | 01_S_MN-BARTABAT_0324UP | C1_0324UP_PH8 | Batteries | Item(s) stolen/Site batteries were stolen
IM762035 | 3514DE | 1901_S_DK-KFR-GHENINA_3514DE | Main power @ DK-KFR-GHENINA_3514DE / Weak batteries / BDT @ 04/08/2019 Is: 0.00 | Faulty System | batt | Batteries | 324923 | DK-KFR-GHENINA | C3_3514DE_PH13 | Batteries | Item(s) stolen/stolen Batteries
IM762069 | 3594DE | 1241_S_BH-TAYRIYA_3594DE | Main power/stolen battery/power back | Faulty System | batt | Batteries | 325119 | BH-TAYRIYA | C1-3594DE-PH13 | Batteries | Item(s) stolen/There is no battery for site
IM762072 | 3484DE | 0231_S_SK-MIT-BASHAR_3484DE | Main power/ battery under invitigation/power back | Faulty System | batt | Batteries | 356055 | SK-MIT-BASHAR | C2-3484DE-PH13 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM762075 | 3898DE | 0821_S_BH-ZUBAYDA_3898DE | Main power / Stolen batteries / SC GN problem / PG connected | Faulty System | batt | Batteries | 335128 | BH-ZUBAYDA | C1_3898DE_PH14 | Batteries | Item(s) stolen/There is no battery for site
IM762075 | 3898DE | 0821_S_BH-ZUBAYDA_3898DE | Main power / Stolen batteries / SC GN problem / PG connected | Faulty System | GN | Generator | 335128 | BH-ZUBAYDA | C1_3898DE_PH14 | ATS / Engine | Components faulty/There is no battery for site (Check small generator operation)
IM762124 | 3368DE | 0201_S_BH-ABO-SHIQAF_3368DE | Access VF / Main power / stolen batteries | Faulty System | batt | Batteries | 324904 | BH-ABO-SHIQAF | C1_3368DE_PH12 | Batteries | Item(s) stolen/There is no battery for site
IM762146 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem and stolen batteries and access VF problem(M) | Faulty System | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | Batteries | Some parts are (missing / stolen)/missing battereis
IM762167 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Main power / Stolen batteries / VF Share | Faulty System | batt | Batteries | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | Batteries | Item(s) stolen/Stolen
IM762196 | 3775DE | 0471_D_DK-DABBOS-VLG_3775DE | GN problem / BDT @ 09/09/2018 Is: 3.00 under check / PG connected | Faulty System | GN | Generator | 325073 | DK-DABBOS-VLG | C1_3775DE_PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/bad terminals
IM762196 | 3775DE | 0471_D_DK-DABBOS-VLG_3775DE | GN problem / BDT @ 09/09/2018 Is: 3.00 under check / PG connected | Faulty System | GN | Generator | 325073 | DK-DABBOS-VLG | C1_3775DE_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM762214 | 0736CA | 02118_D_0736CA_PETROL-PIPELINS | down due to DG filter problem and stolen batteries (M) | Faulty System | batt | Batteries | 356154 | PETROL-PIPELINS | C2_0736CA_PH9 | Batteries | Some parts are (missing / stolen)/Batteries and cables are stolen
IM762214 | 0736CA | 02118_D_0736CA_PETROL-PIPELINS | down due to DG filter problem and stolen batteries (M) | Faulty System | DG | Generator | 356154 | PETROL-PIPELINS | C2_0736CA_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Signs of oil and fuel leakage arround the genset
IM762214 | 0736CA | 02118_D_0736CA_PETROL-PIPELINS | down due to DG filter problem and stolen batteries (M) | Faulty System | DG | Generator | 356154 | PETROL-PIPELINS | C2_0736CA_PH9 | ATS / Engine | Unit earth/Stolen earth connections of the ATS panel
IM762214 | 0736CA | 02118_D_0736CA_PETROL-PIPELINS | down due to DG filter problem and stolen batteries (M) | Faulty System | DG | Generator | 356154 | PETROL-PIPELINS | C2_0736CA_PH9 | ATS / Engine | Components faulty/White exhaust of the engine
IM762214 | 0736CA | 02118_D_0736CA_PETROL-PIPELINS | down due to DG filter problem and stolen batteries (M) | Faulty System | DG | Generator | 356154 | PETROL-PIPELINS | C2_0736CA_PH9 | ATS / Engine | Wrong connection/Wrong connections of cables connected to the ATS trans.
IM762214 | 0736CA | 02118_D_0736CA_PETROL-PIPELINS | down due to DG filter problem and stolen batteries (M) | Faulty System | DG | Generator | 356154 | PETROL-PIPELINS | C2_0736CA_PH9 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Missing terminals of power cables connected to the ATS contactors
IM762247 | 3720DE | 0651_D_MF-SK-KARADIS_3720DE | GN problem/Stolen battery@SK-KARADIS_3720DE/ clear | Faulty System | batt | Batteries | 355737 | MF-SK-KARADIS | C2-3720DE-PH14 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM762247 | 3720DE | 0651_D_MF-SK-KARADIS_3720DE | GN problem/Stolen battery@SK-KARADIS_3720DE/ clear | Faulty System | GN | Generator | 355737 | MF-SK-KARADIS | C2-3720DE-PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Cables have bad connections, proper terminals and proper installtion are rerquired.
IM762248 | 0427DE | 0061_D_SK-EZBA-SARYA_0427DE | GN problem/Stolen battery/ clear | Faulty System | batt | Batteries | 345382 | SK-EZBA-SARYA | C2_0427DE_PH4 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM762248 | 0427DE | 0061_D_SK-EZBA-SARYA_0427DE | GN problem/Stolen battery/ clear | Faulty System | GN | Generator | 345382 | SK-EZBA-SARYA | C2_0427DE_PH4 | ATS / Engine | Components faulty/Exhaust fan not working and another not exist
IM762283 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to DG HT problem and stolen batt. (I) | Faulty System | batt | Batteries | 314391 | REHAB-G17 | C1_3492CA_PH13 | Batteries | Some parts are missing/missing batteries
IM762283 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to DG HT problem and stolen batt. (I) | Faulty System | DG | Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | ATS / Engine | Wrong connection/wrong connection
IM762304 | 0517RE | 03217_E_0517RE_SZ-GALALA-CAMP | Site access Night H&S unsafe road DG Stopped , stolen batteries , recovered once tea access site and fix DG | Faulty System | batt | Batteries | 304374 | SZ-GALALA-CAMP | 0517RE | Batteries | Components faulty/stolen batteries
IM762304 | 0517RE | 03217_E_0517RE_SZ-GALALA-CAMP | Site access Night H&S unsafe road DG Stopped , stolen batteries , recovered once tea access site and fix DG | Faulty System | DG | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Components faulty/missing battery
IM762304 | 0517RE | 03217_E_0517RE_SZ-GALALA-CAMP | Site access Night H&S unsafe road DG Stopped , stolen batteries , recovered once tea access site and fix DG | Faulty System | DG | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Wrong connection/wrong connection for cables
IM762304 | 0517RE | 03217_E_0517RE_SZ-GALALA-CAMP | Site access Night H&S unsafe road DG Stopped , stolen batteries , recovered once tea access site and fix DG | Faulty System | DG | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Wrong connection/welded cables
IM762304 | 0517RE | 03217_E_0517RE_SZ-GALALA-CAMP | Site access Night H&S unsafe road DG Stopped , stolen batteries , recovered once tea access site and fix DG | Faulty System | DG | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/power cable not protected inside PVC or tray
IM762304 | 0517RE | 03217_E_0517RE_SZ-GALALA-CAMP | Site access Night H&S unsafe road DG Stopped , stolen batteries , recovered once tea access site and fix DG | Faulty System | DG | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/fuel tank pipes not protected inside tray
IM762304 | 0517RE | 03217_E_0517RE_SZ-GALALA-CAMP | Site access Night H&S unsafe road DG Stopped , stolen batteries , recovered once tea access site and fix DG | Faulty System | DG | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/broken PVC
IM762304 | 0517RE | 03217_E_0517RE_SZ-GALALA-CAMP | Site access Night H&S unsafe road DG Stopped , stolen batteries , recovered once tea access site and fix DG | Faulty System | DG | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/cable not terminated
IM762304 | 0517RE | 03217_E_0517RE_SZ-GALALA-CAMP | Site access Night H&S unsafe road DG Stopped , stolen batteries , recovered once tea access site and fix DG | Faulty System | DG | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/cables not terminated
IM762304 | 0517RE | 03217_E_0517RE_SZ-GALALA-CAMP | Site access Night H&S unsafe road DG Stopped , stolen batteries , recovered once tea access site and fix DG | Faulty System | DG | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/bad termination for cable
IM762317 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem and access VF & stolen batt. (I) | Faulty System | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | Batteries | Some parts are (missing / stolen)/missing battereis
IM762350 | 0268RE | 03848_G_0268RE_RS-BDWYA-MARSA | DG Stopped , dead batteries PLVD disconnect Site to save cascaded Once team arrive and solve DG problem site recovered | Faulty System | DG | Generator | 304329 | 01_G_RS-BDWYA-MARSA_0268RE | C2_0268RE_PH9 | ATS / Engine | Components faulty/Gen battery is faulty
IM762350 | 0268RE | 03848_G_0268RE_RS-BDWYA-MARSA | DG Stopped , dead batteries PLVD disconnect Site to save cascaded Once team arrive and solve DG problem site recovered | Faulty System | DG | Generator | 304329 | 01_G_RS-BDWYA-MARSA_0268RE | C2_0268RE_PH9 | ATS / Engine | Panorama pictures for each system/Open gland in Gen enclosure need insulation
IM762350 | 0268RE | 03848_G_0268RE_RS-BDWYA-MARSA | DG Stopped , dead batteries PLVD disconnect Site to save cascaded Once team arrive and solve DG problem site recovered | Faulty System | DG | Generator | 304329 | 01_G_RS-BDWYA-MARSA_0268RE | C2_0268RE_PH9 | ATS / Engine | Panorama pictures for each system/Last Gen hour meter at Audit G ( 9838 )
IM762350 | 0268RE | 03848_G_0268RE_RS-BDWYA-MARSA | DG Stopped , dead batteries PLVD disconnect Site to save cascaded Once team arrive and solve DG problem site recovered | Faulty System | DG | Generator | 304329 | 01_G_RS-BDWYA-MARSA_0268RE | C2_0268RE_PH9 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM762355 | 3413DE | 0801_D_PS-KHADIGA_3413DE | Access GA @ PS-KHADIGA_3413DE / GN stopped / BDT @ 08/10/2018 Is: 3.00 | Faulty System | GN | Generator | 335150 | PS-KHADIGA | C2_3413DE_PH13 | ATS / Engine | Components faulty/faulty
IM762355 | 3413DE | 0801_D_PS-KHADIGA_3413DE | Access GA @ PS-KHADIGA_3413DE / GN stopped / BDT @ 08/10/2018 Is: 3.00 | Faulty System | GN | Generator | 335150 | PS-KHADIGA | C2_3413DE_PH13 | ATS / Engine | Wrong connection/remove cable
IM762355 | 3413DE | 0801_D_PS-KHADIGA_3413DE | Access GA @ PS-KHADIGA_3413DE / GN stopped / BDT @ 08/10/2018 Is: 3.00 | Faulty System | GN | Generator | 335150 | PS-KHADIGA | C2_3413DE_PH13 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM762355 | 3413DE | 0801_D_PS-KHADIGA_3413DE | Access GA @ PS-KHADIGA_3413DE / GN stopped / BDT @ 08/10/2018 Is: 3.00 | Faulty System | GN | Generator | 324940 | PS-KHADIGA | C2_3413DE_PH13 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/Unused cable need to be removed.
IM762355 | 3413DE | 0801_D_PS-KHADIGA_3413DE | Access GA @ PS-KHADIGA_3413DE / GN stopped / BDT @ 08/10/2018 Is: 3.00 | Faulty System | GN | Generator | 324940 | PS-KHADIGA | C2_3413DE_PH13 | ATS / Engine | Panorama pictures for each system/Overview.
IM762365 | 3784DE | 0661_S_KS-DAQLIT_3784DE | Main power / Weak batteries / VF Share | Faulty System | batt | Batteries | 335221 | KS-DAQLIT | C3_3784DE_PH14 | Batteries | Components faulty/Faulty battery (battearies are ballooned)
IM762405 | 3191DE | 0971_D_GH-BALQINA_3191DE | GN problem / stolen batteries | Faulty System | batt | Batteries | 304240 | GH-BALQINA | C4_3191DE_PH12 | Batteries | Item(s) stolen/stolen batteries
IM762405 | 3191DE | 0971_D_GH-BALQINA_3191DE | GN problem / stolen batteries | Faulty System | GN | Generator | 304240 | GH-BALQINA | C4_3191DE_PH12 | ATS / Engine | Components faulty/connect and check
IM762405 | 3191DE | 0971_D_GH-BALQINA_3191DE | GN problem / stolen batteries | Faulty System | GN | Generator | 304240 | GH-BALQINA | C4_3191DE_PH12 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/sharp edges
IM762405 | 3191DE | 0971_D_GH-BALQINA_3191DE | GN problem / stolen batteries | Faulty System | GN | Generator | 304240 | GH-BALQINA | C4_3191DE_PH12 | ATS / Engine | Item(s) stolen/stolen battery
IM762405 | 3191DE | 0971_D_GH-BALQINA_3191DE | GN problem / stolen batteries | Faulty System | GN | Generator | 304240 | GH-BALQINA | C4_3191DE_PH12 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage
IM762425 | 0127DE | 0061_H_GH-MRO4-QUTUR_0127DE | Main power @ GH-MR04-QUTUR_0127DE / Stolen batteries / Connect PG / Cells Hanged / Split request | Faulty System | batt | Batteries | 304205 | 9_S_GH-MR04-QUTUR_0127DE_SS00 | C4_0127DE_PH2 | Batteries | Item(s) stolen/stolen batteries
IM762436 | 3368DE | 0201_S_BH-ABO-SHIQAF_3368DE | Access VF / Main power / stolen batteries | Faulty System | batt | Batteries | 324904 | BH-ABO-SHIQAF | C1_3368DE_PH12 | Batteries | Item(s) stolen/There is no battery for site
IM762481 | 0329RE | 03838_S_0329RE_RS-SENTIDO-DRM | ET DG Stopped , stolen batteries , access PG due unsafe road , stolen batteries Once DG fix Site recovered | Faulty System | DG | Generator | 304289 | 01_S_RS-SENTIDO-DRM_0329RE | C1_0329RE_PH12 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM762484 | 3126DE | 0121_S_DK-HAGYZEYA_3126DE | Main Power/stolen battery/PG connected | Faulty System | batt | Batteries | 355992 | DK-HAGYZEYA | C6-3126DE-PH12 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM762498 | 0267RE | U_S_RS-NADA-MARSA_0267RE | Outage power in Hotel located site , dead batteries , access PG Once power restored site recovered | Faulty System | batt | Batteries | 304306 | 01_S_RS-NADA-MARSA_0267RE | C1_0267RE_PH9 | Batteries | Components faulty/No back up power ( Batteries were damged also salty )
IM762498 | 0267RE | U_S_RS-NADA-MARSA_0267RE | Outage power in Hotel located site , dead batteries , access PG Once power restored site recovered | Faulty System | batt | Batteries | 304306 | 01_S_RS-NADA-MARSA_0267RE | C1_0267RE_PH9 | Batteries | Item(s) stolen/Batteries connections were stolen also ( No back up power )
IM762500 | 3333DE | 0181_S_BH-OM-SABER_3333DE | Access VF. / Main Power / Stolen batteries/clear after power back | Faulty System | batt | Batteries | 304089 | BH-OM-SABER_SSS0 | C1_3333DE_PH12 | Batteries | Item(s) stolen/There is no battery for site
IM762584 | 3199UP | 0641_S_AT-GANADLAH_3199UP | Due to EC power cutoff , Stolen batteries , Recovered | Faulty System | batt | Batteries | 303847 | 01_S_AT-GANADLAH_3199UP | C2_3199UP_PH13 | Batteries | Item(s) stolen/site Batteries were Stolen
IM762669 | 3501DE | 0501_S_SK-SANIYA_3501DE | access owner/the owner switch MCB OFF/Finencial problem/Stolen batteries | Faulty System | batt | Batteries | 345238 | SK-SANIYA | C1-3501DE-PH13 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM762813 | 0749UP | 1251_Q_AT-MANFALOUT-2_0749UP | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 356128 | 01_H_AT-MANFALOUT-2_0749UP | C2_0749UP_PH11 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leaage
IM762813 | 0749UP | 1251_Q_AT-MANFALOUT-2_0749UP | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 356128 | 01_H_AT-MANFALOUT-2_0749UP | C2_0749UP_PH11 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leaage
IM762813 | 0749UP | 1251_Q_AT-MANFALOUT-2_0749UP | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 356128 | 01_H_AT-MANFALOUT-2_0749UP | C2_0749UP_PH11 | ATS / Engine | Components faulty/gen need new battery
IM762813 | 0749UP | 1251_Q_AT-MANFALOUT-2_0749UP | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 356128 | 01_H_AT-MANFALOUT-2_0749UP | C2_0749UP_PH11 | ATS / Engine | Components faulty/gen need new battery
IM762856 | 3521UP | 02_G_QN-HIBILAT-WST_3521UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | batt | Batteries | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | Batteries | Item(s) stolen/Batteries were stolen
IM762856 | 3521UP | 02_G_QN-HIBILAT-WST_3521UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | Gen | Generator | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | ATS / Engine | Components faulty/Gen battery is faulty need new one
IM762856 | 3521UP | 02_G_QN-HIBILAT-WST_3521UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | generator | Generator | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | ATS / Engine | Components faulty/Gen battery is faulty need new one
IM762856 | 3521UP | 02_G_QN-HIBILAT-WST_3521UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | Gen | Generator | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | ATS / Engine | Panorama pictures for each system/Last gen hour meter at Audit g ( 4570 )
IM762856 | 3521UP | 02_G_QN-HIBILAT-WST_3521UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | generator | Generator | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | ATS / Engine | Panorama pictures for each system/Last gen hour meter at Audit g ( 4570 )
IM762856 | 3521UP | 02_G_QN-HIBILAT-WST_3521UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | Gen | Generator | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM762856 | 3521UP | 02_G_QN-HIBILAT-WST_3521UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | generator | Generator | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM762870 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem & no backup & access VF (T) | Faulty System | backup | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | Batteries | Some parts are (missing / stolen)/missing battereis
IM762898 | 0711AL | 03058_G_0711AL_MM-AMWAJ | GN problem/ GN total failure/ restored on Honda till change the GN engine | Faulty System | GN | Generator | 345399 | MS-AMWAJ | C5_0711AL_PH14 | ATS / Engine | Unit earth/Earth not connected
IM762898 | 0711AL | 03058_G_0711AL_MM-AMWAJ | GN problem/ GN total failure/ restored on Honda till change the GN engine | Faulty System | GN | Generator | 345399 | MS-AMWAJ | C5_0711AL_PH14 | ATS / Engine | Components faulty/Emergency key not working
IM762898 | 0711AL | 03058_G_0711AL_MM-AMWAJ | GN problem/ GN total failure/ restored on Honda till change the GN engine | Faulty System | GN | Generator | 345399 | MS-AMWAJ | C5_0711AL_PH14 | ATS / Engine | Components faulty/Housing so broken
IM762914 | 3898DE | 0821_S_BH-ZUBAYDA_3898DE | Main power / Stolen batteries / SC GN problem | Faulty System | batt | Batteries | 335128 | BH-ZUBAYDA | C1_3898DE_PH14 | Batteries | Item(s) stolen/There is no battery for site
IM762914 | 3898DE | 0821_S_BH-ZUBAYDA_3898DE | Main power / Stolen batteries / SC GN problem | Faulty System | GN | Generator | 335128 | BH-ZUBAYDA | C1_3898DE_PH14 | ATS / Engine | Components faulty/There is no battery for site (Check small generator operation)
IM762924 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | ATS / Engine | Components faulty/Gen battery was defected
IM762924 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | ATS / Engine | Components faulty/Gen battery was defected
IM762924 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/ATS Cables not organized
IM762924 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/ATS Cables not organized
IM762933 | 0711AL | 03058_G_0711AL_MM-AMWAJ | GN problem/ GN total failure/ Honda connected continuously/ honda failed/ restored on another honda till change the GN engine | Faulty System | GN | Generator | 345399 | MS-AMWAJ | C5_0711AL_PH14 | ATS / Engine | Unit earth/Earth not connected
IM762933 | 0711AL | 03058_G_0711AL_MM-AMWAJ | GN problem/ GN total failure/ Honda connected continuously/ honda failed/ restored on another honda till change the GN engine | Faulty System | GN | Generator | 345399 | MS-AMWAJ | C5_0711AL_PH14 | ATS / Engine | Components faulty/Emergency key not working
IM762933 | 0711AL | 03058_G_0711AL_MM-AMWAJ | GN problem/ GN total failure/ Honda connected continuously/ honda failed/ restored on another honda till change the GN engine | Faulty System | GN | Generator | 345399 | MS-AMWAJ | C5_0711AL_PH14 | ATS / Engine | Components faulty/Housing so broken
IM762966 | 3590DE | 1631_S_BH-HADIN_3590DE | Main power / Stolen batteries / SC GN problem | Faulty System | batt | Batteries | 324439 | BH-HADIN | C2_3590DE_PH13 | Batteries | Item(s) stolen/There is no battery for site
IM762966 | 3590DE | 1631_S_BH-HADIN_3590DE | Main power / Stolen batteries / SC GN problem | Faulty System | GN | Generator | 324439 | BH-HADIN | C2_3590DE_PH13 | ATS / Engine | Components faulty/Check small generator operation (There is no battery for site)
IM762985 | 3065UP | 0641_S_QN-ELARAKI_3065UP | Main power disconnection , Stolen batteries , P.G connected | Faulty System | batt | Batteries | 356496 | 01_S_QN-ELARAKI_3065UP | C1_3065UP_PH13 | Batteries | Some parts are (missing / stolen)/Batteries were stolen
IM762994 | 3590DE | 1631_S_BH-HADIN_3590DE | GN problem / stolen batteries | Faulty System | batt | Batteries | 324439 | BH-HADIN | C2_3590DE_PH13 | Batteries | Item(s) stolen/There is no battery for site
IM762994 | 3590DE | 1631_S_BH-HADIN_3590DE | GN problem / stolen batteries | Faulty System | GN | Generator | 324439 | BH-HADIN | C2_3590DE_PH13 | ATS / Engine | Components faulty/Check small generator operation (There is no battery for site)
IM763020 | 3828DE | 0961_S_BH-GWAD-HUSNI_3828DE | Main power / stolen batteries | Faulty System | batt | Batteries | 356184 | BH-GWAD-HUSNI | C1_3828DE_PH14 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM763033 | 0964UP | 0181_S_SG-SALLA_0964UP | Main power disconnection ,batteries are suspected to be weak , P.G connected | Faulty System | batt | Batteries | 345407 | SG-SALLA | C2_0964UP_PH12 | Batteries | Some parts are (missing / stolen)/site Batteries were stolen
IM763052 | 3151UP | 1561_S_BS-QIMAN-AROS_3151UP | Due to EC power cutoff , weak batteries , PG Connected | Faulty System | batt | Batteries | 355911 | 01_S_BS-QIMAN-AROS_3151UP | C2_3151UP_PH13 | Rectifiers | Alarms reporting to the OMC/Loop on the minor alarm in DDF (Port 6)
IM763052 | 3151UP | 1561_S_BS-QIMAN-AROS_3151UP | Due to EC power cutoff , weak batteries , PG Connected | Faulty System | batt | Batteries | 355911 | 01_S_BS-QIMAN-AROS_3151UP | C2_3151UP_PH13 | Rectifiers | Alarms reporting to the OMC/The power alarm is faulty (Always active on the rectifier and OMC)
IM763087 | 0711AL | 03058_G_0711AL_MM-AMWAJ | GN problem/ GN total failure/ Honda connected continuously/ honda failed/ restored on another honda till change the GN engine | Faulty System | GN | Generator | 345399 | MS-AMWAJ | C5_0711AL_PH14 | ATS / Engine | Unit earth/Earth not connected
IM763087 | 0711AL | 03058_G_0711AL_MM-AMWAJ | GN problem/ GN total failure/ Honda connected continuously/ honda failed/ restored on another honda till change the GN engine | Faulty System | GN | Generator | 345399 | MS-AMWAJ | C5_0711AL_PH14 | ATS / Engine | Components faulty/Emergency key not working
IM763087 | 0711AL | 03058_G_0711AL_MM-AMWAJ | GN problem/ GN total failure/ Honda connected continuously/ honda failed/ restored on another honda till change the GN engine | Faulty System | GN | Generator | 345399 | MS-AMWAJ | C5_0711AL_PH14 | ATS / Engine | Components faulty/Housing so broken
IM763104 | 0324UP | 1421_S_MN-BARTABAT_0324UP | Due to EC power cutoff , Stolen batteries , PG Connected | Faulty System | batt | Batteries | 324919 | 01_S_MN-BARTABAT_0324UP | C1_0324UP_PH8 | Batteries | Item(s) stolen/Site batteries were stolen
IM763115 | 3628DE | 0811_S_GH-QSR-BAGHDAD_3628DE | Main power / Stolen batteries | Faulty System | batt | Batteries | 324836 | GH-QSR-BAGHDAD | C2_3628DE_PH13 | Batteries | Item(s) stolen/Stolen batteries
IM763132 | 3836DE | 0661_S_SK-HAGARSA_3836DE | Main power at site SK-HAGARSA_3836DE/Stolen battery/site clear@EC come back | Faulty System | batt | Batteries | 345237 | SK-HAGARSA | C1-3836DE-PH14 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM763166 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Due to Generator problem , weak batteries , PG Connected | Faulty System | Gen | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | ATS / Engine | Components faulty/Gen battery was defected
IM763166 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Due to Generator problem , weak batteries , PG Connected | Faulty System | generator | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | ATS / Engine | Components faulty/Gen battery was defected
IM763166 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Due to Generator problem , weak batteries , PG Connected | Faulty System | Gen | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/ATS Cables not organized
IM763166 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Due to Generator problem , weak batteries , PG Connected | Faulty System | generator | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/ATS Cables not organized
IM763198 | 0149CA | 02181_S_0149CA_HAKIME | down due to power problem and battery stolen | Faulty System | batt | Batteries | 324801 | HAKIME | C1_0149CA_PH1 | Batteries | Item(s) stolen/All batteries are stolen
IM763198 | 0149CA | 02181_S_0149CA_HAKIME | down due to power problem and battery stolen | Faulty System | batt | Batteries | 324801 | HAKIME | C1_0149CA_PH1 | Batteries | Item(s) stolen/All batteries are stolen and cables are disconnected
IM763203 | 4342DE | U_S_4342DE_BAHTIM8 | down due to commercial cut and stolen batteries at 4342DE_BAHTIM8 | Faulty System | batt | Batteries | 356147 | U_S_4342DE_BAHTIM8 | C1_4342DE_PH18 | Rectifiers | Alarms reporting to the OMC/Rectifier alarms don't appear on the OMC
IM763203 | 4342DE | U_S_4342DE_BAHTIM8 | down due to commercial cut and stolen batteries at 4342DE_BAHTIM8 | Faulty System | batt | Batteries | 356147 | U_S_4342DE_BAHTIM8 | C1_4342DE_PH18 | Batteries | Some parts are (missing / stolen)/All batteries are stolen
IM763219 | 3344DE | 0681_S_BH-ELNEGILY_3344DE | Share VF / VF guard switched off Orange C.B / Main power / stolen batteries | Faulty System | batt | Batteries | 304214 | BH-ELNEGILY | C3_3344DE_PH12 | Batteries | Item(s) stolen/There is no battery for site
IM763221 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Share VF / VF GN problem / stolen batteries / PG handle other sites | Faulty System | batt | Batteries | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | Batteries | Item(s) stolen/Stolen
IM763221 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Share VF / VF GN problem / stolen batteries / PG handle other sites | Faulty System | GN | Generator | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | ATS / Engine | Item(s) stolen/missing battery
IM763221 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Share VF / VF GN problem / stolen batteries / PG handle other sites | Faulty System | GN | Generator | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM763307 | 0954UP | 01_G_MN-DAHMARU_0954UP | Due to EC power cutoff , Stolen batteries , Recovered | Faulty System | batt | Batteries | 324946 | 01_G_MN-DAHMARU_0954UP | C1_0954UP_PH12 | Batteries | Item(s) stolen/site baateries were stolen
IM763323 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , PG Connected | Faulty System | Gen | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage of the engine
IM763323 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , PG Connected | Faulty System | generator | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage of the engine
IM763323 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , PG Connected | Faulty System | Gen | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Unit earth/Stolen earth connections of the genset panel
IM763323 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , PG Connected | Faulty System | generator | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Unit earth/Stolen earth connections of the genset panel
IM763323 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , PG Connected | Faulty System | Gen | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Components faulty/The rubber bases of the radiator are faulty
IM763323 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , PG Connected | Faulty System | generator | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Components faulty/The rubber bases of the radiator are faulty
IM763323 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , PG Connected | Faulty System | Gen | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Components faulty/The dynamo belt needs to be tensioned
IM763323 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , PG Connected | Faulty System | generator | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Components faulty/The dynamo belt needs to be tensioned
IM763323 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , PG Connected | Faulty System | Gen | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Wrong connection/The negative pole of the battery isn't connected
IM763323 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , PG Connected | Faulty System | generator | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Wrong connection/The negative pole of the battery isn't connected
IM763323 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , PG Connected | Faulty System | Gen | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Missing terminals of cables connected to contactors and CBs inside the genset panel
IM763323 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , PG Connected | Faulty System | generator | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Missing terminals of cables connected to contactors and CBs inside the genset panel
IM763382 | 3776UP | 02_G_SG-HARJA-QARAN_3776UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | batt | Batteries | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | Batteries | Item(s) stolen/Batteries were stolen
IM763382 | 3776UP | 02_G_SG-HARJA-QARAN_3776UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | Gen | Generator | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | ATS / Engine | Components faulty/Gen battery is faulty need new one
IM763382 | 3776UP | 02_G_SG-HARJA-QARAN_3776UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | generator | Generator | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | ATS / Engine | Components faulty/Gen battery is faulty need new one
IM763382 | 3776UP | 02_G_SG-HARJA-QARAN_3776UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | Gen | Generator | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | ATS / Engine | Panorama pictures for each system/Last gen hour meter at Audit g ( 4570 )
IM763382 | 3776UP | 02_G_SG-HARJA-QARAN_3776UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | generator | Generator | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | ATS / Engine | Panorama pictures for each system/Last gen hour meter at Audit g ( 4570 )
IM763382 | 3776UP | 02_G_SG-HARJA-QARAN_3776UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | Gen | Generator | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM763382 | 3776UP | 02_G_SG-HARJA-QARAN_3776UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | generator | Generator | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM763429 | 0370UP | 1961_G_CAIRO-ASWAN-12_0370UP | Main power disconnection ,batteries are suspected to be weak , P.G connected | Faulty System | batt | Batteries | 304136 | 01_G_CAIRO-ASWAN-12_0370UP | C2_0370UP_PH8 | Batteries | Item(s) stolen/ Batteries were stolen
IM763540 | 3349CA | 01126_S_3349CA_IMBABA-6 | down due to commercial cut and stolen batteries (MA) | Faulty System | batt | Batteries | 303961 | IMBABA-6 | C2_3349CA_PH12 | Batteries | Components faulty/Batteries are in a very bad condition (DC voltage dropped to 42.7V. after 1 min of power disconnecting)
IM763568 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem and no battery and PG access | Faulty System | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | Batteries | Some parts are (missing / stolen)/missing battereis
IM763574 | 3955DE | 0731_S_SK-QRMT-SAHBRA_3955DE | access ET/ET GN peoblem/Stolen batteries/clear after GN working | Faulty System | batt | Batteries | 356230 | SK-QRMT-SAHBRA | C1_3955DE_PH15 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM763607 | 0076DE | 0561_H_DK-BATRAH_0076DE | Main power / stolen batteries | Faulty System | batt | Batteries | 304322 | BATRAH | C1_0076DE_PH1 | Batteries | Item(s) stolen/stolen batteries
IM763629 | 0517RE | 03217_E_0517RE_SZ-GALALA-CAMP | Site Down Due To DG Power Alarm - Access RD H&S - Recovered once DG problem solved | Faulty System | DG | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Components faulty/missing battery
IM763629 | 0517RE | 03217_E_0517RE_SZ-GALALA-CAMP | Site Down Due To DG Power Alarm - Access RD H&S - Recovered once DG problem solved | Faulty System | DG | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Wrong connection/wrong connection for cables
IM763629 | 0517RE | 03217_E_0517RE_SZ-GALALA-CAMP | Site Down Due To DG Power Alarm - Access RD H&S - Recovered once DG problem solved | Faulty System | DG | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Wrong connection/welded cables
IM763629 | 0517RE | 03217_E_0517RE_SZ-GALALA-CAMP | Site Down Due To DG Power Alarm - Access RD H&S - Recovered once DG problem solved | Faulty System | DG | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/power cable not protected inside PVC or tray
IM763629 | 0517RE | 03217_E_0517RE_SZ-GALALA-CAMP | Site Down Due To DG Power Alarm - Access RD H&S - Recovered once DG problem solved | Faulty System | DG | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/fuel tank pipes not protected inside tray
IM763629 | 0517RE | 03217_E_0517RE_SZ-GALALA-CAMP | Site Down Due To DG Power Alarm - Access RD H&S - Recovered once DG problem solved | Faulty System | DG | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/broken PVC
IM763629 | 0517RE | 03217_E_0517RE_SZ-GALALA-CAMP | Site Down Due To DG Power Alarm - Access RD H&S - Recovered once DG problem solved | Faulty System | DG | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/cable not terminated
IM763629 | 0517RE | 03217_E_0517RE_SZ-GALALA-CAMP | Site Down Due To DG Power Alarm - Access RD H&S - Recovered once DG problem solved | Faulty System | DG | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/cables not terminated
IM763629 | 0517RE | 03217_E_0517RE_SZ-GALALA-CAMP | Site Down Due To DG Power Alarm - Access RD H&S - Recovered once DG problem solved | Faulty System | DG | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/bad termination for cable
IM763724 | 0268RE | 03848_G_0268RE_RS-BDWYA-MARSA | Site Down Due To DG Power Alarm - weak batteries - Recovered once DG problem solved | Faulty System | DG | Generator | 304329 | 01_G_RS-BDWYA-MARSA_0268RE | C2_0268RE_PH9 | ATS / Engine | Components faulty/Gen battery is faulty
IM763724 | 0268RE | 03848_G_0268RE_RS-BDWYA-MARSA | Site Down Due To DG Power Alarm - weak batteries - Recovered once DG problem solved | Faulty System | DG | Generator | 304329 | 01_G_RS-BDWYA-MARSA_0268RE | C2_0268RE_PH9 | ATS / Engine | Panorama pictures for each system/Open gland in Gen enclosure need insulation
IM763724 | 0268RE | 03848_G_0268RE_RS-BDWYA-MARSA | Site Down Due To DG Power Alarm - weak batteries - Recovered once DG problem solved | Faulty System | DG | Generator | 304329 | 01_G_RS-BDWYA-MARSA_0268RE | C2_0268RE_PH9 | ATS / Engine | Panorama pictures for each system/Last Gen hour meter at Audit G ( 9838 )
IM763724 | 0268RE | 03848_G_0268RE_RS-BDWYA-MARSA | Site Down Due To DG Power Alarm - weak batteries - Recovered once DG problem solved | Faulty System | DG | Generator | 304329 | 01_G_RS-BDWYA-MARSA_0268RE | C2_0268RE_PH9 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM763752 | 3729UP | 01_E_WAHT-BHREY-ENT_3729UP | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure
IM763752 | 3729UP | 01_E_WAHT-BHREY-ENT_3729UP | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure
IM763752 | 3729UP | 01_E_WAHT-BHREY-ENT_3729UP | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Wrong connection/generator battery as used in the site and not suitable in High temp
IM763752 | 3729UP | 01_E_WAHT-BHREY-ENT_3729UP | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Wrong connection/generator battery as used in the site and not suitable in High temp
IM763765 | 3199UP | 0641_S_AT-GANADLAH_3199UP | Due to EC power cutoff , Stolen batteries , Recovered | Faulty System | batt | Batteries | 303847 | 01_S_AT-GANADLAH_3199UP | C2_3199UP_PH13 | Batteries | Item(s) stolen/site Batteries were Stolen
IM763843 | 3009AL | 03232_D_3009AL_MM-ALMN-APT2 | GN problem/ weak batteries/ restored after solve GN problem | Faulty System | batt | Batteries | 304374 | SZ-GALALA-CAMP | 0517RE | Batteries | Components faulty/stolen batteries
IM763843 | 3009AL | 03232_D_3009AL_MM-ALMN-APT2 | GN problem/ weak batteries/ restored after solve GN problem | Faulty System | GN | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Components faulty/missing battery
IM763843 | 3009AL | 03232_D_3009AL_MM-ALMN-APT2 | GN problem/ weak batteries/ restored after solve GN problem | Faulty System | GN | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Wrong connection/wrong connection for cables
IM763843 | 3009AL | 03232_D_3009AL_MM-ALMN-APT2 | GN problem/ weak batteries/ restored after solve GN problem | Faulty System | GN | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Wrong connection/welded cables
IM763843 | 3009AL | 03232_D_3009AL_MM-ALMN-APT2 | GN problem/ weak batteries/ restored after solve GN problem | Faulty System | GN | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/power cable not protected inside PVC or tray
IM763843 | 3009AL | 03232_D_3009AL_MM-ALMN-APT2 | GN problem/ weak batteries/ restored after solve GN problem | Faulty System | GN | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/fuel tank pipes not protected inside tray
IM763843 | 3009AL | 03232_D_3009AL_MM-ALMN-APT2 | GN problem/ weak batteries/ restored after solve GN problem | Faulty System | GN | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/broken PVC
IM763843 | 3009AL | 03232_D_3009AL_MM-ALMN-APT2 | GN problem/ weak batteries/ restored after solve GN problem | Faulty System | GN | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/cable not terminated
IM763843 | 3009AL | 03232_D_3009AL_MM-ALMN-APT2 | GN problem/ weak batteries/ restored after solve GN problem | Faulty System | GN | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/cables not terminated
IM763843 | 3009AL | 03232_D_3009AL_MM-ALMN-APT2 | GN problem/ weak batteries/ restored after solve GN problem | Faulty System | GN | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/bad termination for cable
IM763843 | 3009AL | 03232_D_3009AL_MM-ALMN-APT2 | GN problem/ weak batteries/ restored after solve GN problem | Faulty System | GN | Generator | 324992 | MM-ALMN-APT2 | C1_3009AL_PH19 | ATS / Engine | Components faulty/Burned generator need to be replaced.
IM763843 | 3009AL | 03232_D_3009AL_MM-ALMN-APT2 | GN problem/ weak batteries/ restored after solve GN problem | Faulty System | GN | Generator | 324992 | MM-ALMN-APT2 | C1_3009AL_PH19 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Vodafone gen has leakage.
IM763844 | 0964UP | 0181_S_SG-SALLA_0964UP | Main power disconnection ,batteries are suspected to be weak , recovered when EC power come back | Faulty System | batt | Batteries | 345407 | SG-SALLA | C2_0964UP_PH12 | Batteries | Some parts are (missing / stolen)/site Batteries were stolen
IM763849 | 3333DE | 0181_S_BH-OM-SABER_3333DE | main power/stolen battery/power back | Faulty System | batt | Batteries | 304089 | BH-OM-SABER_SSS0 | C1_3333DE_PH12 | Batteries | Item(s) stolen/There is no battery for site
IM763850 | 3489DE | 0461_S_DK-KFR-GHANNAM_3489DE | main power/stolen battery/power back | Faulty System | batt | Batteries | 325088 | DK-KFR-GHANNAM | C1-3489DE-PH13 | Batteries | Item(s) stolen/No backup batteries.
IM763876 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to DG VF problem and no battery and PG access | Faulty System | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | Batteries | Some parts are (missing / stolen)/missing battereis
IM763908 | 0316RE | 03493_S_0316RE_SZ-GHAZZALY | Power outage // access PG // Weak batteries // Recovered | Faulty System | batt | Batteries | 355925 | 01_S_SZ-GHAZZALY_0316RE | C2_0316RE_PH12 | Rectifiers | Alarms reporting to the OMC/Alarm on the rectifier
IM763929 | 3490UP | 01_D_AT-ELHASANI_3490UP | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 356124 | 01_G_AT-ELHASANI_3490UP | C2_3490UP_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage
IM763929 | 3490UP | 01_D_AT-ELHASANI_3490UP | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 356124 | 01_G_AT-ELHASANI_3490UP | C2_3490UP_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage
IM763929 | 3490UP | 01_D_AT-ELHASANI_3490UP | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 356124 | 01_G_AT-ELHASANI_3490UP | C2_3490UP_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leaage from ET gen
IM763929 | 3490UP | 01_D_AT-ELHASANI_3490UP | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 356124 | 01_G_AT-ELHASANI_3490UP | C2_3490UP_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leaage from ET gen
IM763929 | 3490UP | 01_D_AT-ELHASANI_3490UP | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 356124 | 01_G_AT-ELHASANI_3490UP | C2_3490UP_PH14 | ATS / Engine | Components faulty/Gen need new battery
IM763929 | 3490UP | 01_D_AT-ELHASANI_3490UP | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 356124 | 01_G_AT-ELHASANI_3490UP | C2_3490UP_PH14 | ATS / Engine | Components faulty/Gen need new battery
IM764013 | 3798DE | 1471_S_SK-MNZL-MYMON_3798DE | Main power/stolen battery/connect PG | Faulty System | batt | Batteries | 355763 | SK-MNZL-MYMON | C2-3798DE-PH14 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM764022 | 0076DE | 0561_H_DK-BATRAH_0076DE | Main Power / stolen batteries | Faulty System | batt | Batteries | 304322 | BATRAH | C1_0076DE_PH1 | Batteries | Item(s) stolen/stolen batteries
IM764033 | 0421DE | 0721_H_MF-MANSH-SOLTN_0421DE | Main power/battery under invistigation/power back | Faulty System | batt | Batteries | 304300 | MF-MANSH-SOLTN | C1_0421DE_PH4 | Batteries | Some parts are missing/Battery racks are placed directly under A/C IDU
IM764120 | 0427DE | 0061_D_SK-EZBA-SARYA_0427DE | GEN problem/stolen battery/generator working | Faulty System | batt | Batteries | 345382 | SK-EZBA-SARYA | C2_0427DE_PH4 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM764120 | 0427DE | 0061_D_SK-EZBA-SARYA_0427DE | GEN problem/stolen battery/generator working | Faulty System | Gen | Generator | 345382 | SK-EZBA-SARYA | C2_0427DE_PH4 | ATS / Engine | Components faulty/Exhaust fan not working and another not exist
IM764120 | 0427DE | 0061_D_SK-EZBA-SARYA_0427DE | GEN problem/stolen battery/generator working | Faulty System | generator | Generator | 345382 | SK-EZBA-SARYA | C2_0427DE_PH4 | ATS / Engine | Components faulty/Exhaust fan not working and another not exist
IM764182 | 3777UP | 1281_E_AS-RAGHAMA_3777UP_X | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | batt | Batteries | 355941 | 01_G_AS-RAGHAMA_3777UP | C2_3777UP_PH15 | Batteries | Components faulty/One Battery was explosion
IM764182 | 3777UP | 1281_E_AS-RAGHAMA_3777UP_X | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | Gen | Generator | 355941 | 01_G_AS-RAGHAMA_3777UP | C2_3777UP_PH15 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage
IM764182 | 3777UP | 1281_E_AS-RAGHAMA_3777UP_X | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | generator | Generator | 355941 | 01_G_AS-RAGHAMA_3777UP | C2_3777UP_PH15 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage
IM764182 | 3777UP | 1281_E_AS-RAGHAMA_3777UP_X | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | Gen | Generator | 355941 | 01_G_AS-RAGHAMA_3777UP | C2_3777UP_PH15 | ATS / Engine | Unit earth/Gen earth cable is missing
IM764182 | 3777UP | 1281_E_AS-RAGHAMA_3777UP_X | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | generator | Generator | 355941 | 01_G_AS-RAGHAMA_3777UP | C2_3777UP_PH15 | ATS / Engine | Unit earth/Gen earth cable is missing
IM764214 | 3775DE | 0471_D_DK-DABBOS-VLG_3775DE | GN problem / batteries under check | Faulty System | GN | Generator | 325073 | DK-DABBOS-VLG | C1_3775DE_PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/bad terminals
IM764214 | 3775DE | 0471_D_DK-DABBOS-VLG_3775DE | GN problem / batteries under check | Faulty System | GN | Generator | 325073 | DK-DABBOS-VLG | C1_3775DE_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM764243 | 3578UP | 01_N_SG-KOUM-ELASFR_3578UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | Gen | Generator | 355944 | 01_N_SG-KOUM-ELASFR_3578UP | C3_3578UP_PH14 | ATS / Engine | Components faulty/Gen battery is faulty
IM764243 | 3578UP | 01_N_SG-KOUM-ELASFR_3578UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | generator | Generator | 355944 | 01_N_SG-KOUM-ELASFR_3578UP | C3_3578UP_PH14 | ATS / Engine | Components faulty/Gen battery is faulty
IM764243 | 3578UP | 01_N_SG-KOUM-ELASFR_3578UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | Gen | Generator | 355944 | 01_N_SG-KOUM-ELASFR_3578UP | C3_3578UP_PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Missing terminals
IM764243 | 3578UP | 01_N_SG-KOUM-ELASFR_3578UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | generator | Generator | 355944 | 01_N_SG-KOUM-ELASFR_3578UP | C3_3578UP_PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Missing terminals
IM764243 | 3578UP | 01_N_SG-KOUM-ELASFR_3578UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | Gen | Generator | 355944 | 01_N_SG-KOUM-ELASFR_3578UP | C3_3578UP_PH14 | ATS / Engine | Filters condition oil/fuel/air/Air filter need clean
IM764243 | 3578UP | 01_N_SG-KOUM-ELASFR_3578UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | generator | Generator | 355944 | 01_N_SG-KOUM-ELASFR_3578UP | C3_3578UP_PH14 | ATS / Engine | Filters condition oil/fuel/air/Air filter need clean
IM764261 | 3298UP | 01_S_SG-SHOHADAA_3298UP | Main power disconnection , Stolen batteries , P.G connected | Faulty System | batt | Batteries | 356366 | 01_O_SG-RYAYNA-HAGR_3744UP | C1_3744UP_PH16 | Batteries | Some parts are (missing / stolen)/Site batteries were Stolen
IM764301 | 3744UP | 01_S_SG-RYAYNA-HAGR_3744UP | Generator Problem ,Stolen batteries ,Recovered after solvig the generator problem . | Faulty System | batt | Batteries | 356366 | 01_O_SG-RYAYNA-HAGR_3744UP | C1_3744UP_PH16 | Batteries | Some parts are (missing / stolen)/Site batteries were Stolen
IM764301 | 3744UP | 01_S_SG-RYAYNA-HAGR_3744UP | Generator Problem ,Stolen batteries ,Recovered after solvig the generator problem . | Faulty System | Gen | Generator | 356366 | 01_O_SG-RYAYNA-HAGR_3744UP | C1_3744UP_PH16 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Missing terminals in power cables
IM764301 | 3744UP | 01_S_SG-RYAYNA-HAGR_3744UP | Generator Problem ,Stolen batteries ,Recovered after solvig the generator problem . | Faulty System | generator | Generator | 356366 | 01_O_SG-RYAYNA-HAGR_3744UP | C1_3744UP_PH16 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Missing terminals in power cables
IM764305 | 3170DE | 0971_S_MF-WARDAN-2_3170DE | main power/battery under ivistigation/connect @MF-KHTATBA-FRM& MF-KHATATBA-RD | Faulty System | batt | Batteries | 355958 | MF-WARDAN-2 | C1_3170DE_PH12 | Batteries | Some parts are (missing / stolen)/Disconnected battery strng
IM764307 | 3276UP | 02_G_QN-BAKHANES_3276UP | Generator Problem- Alternator problem , Stolen Batteries , P.G Connected | Faulty System | batt | Batteries | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | Batteries | Item(s) stolen/Batteries were stolen
IM764307 | 3276UP | 02_G_QN-BAKHANES_3276UP | Generator Problem- Alternator problem , Stolen Batteries , P.G Connected | Faulty System | Gen | Generator | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | ATS / Engine | Components faulty/Gen battery is faulty need new one
IM764307 | 3276UP | 02_G_QN-BAKHANES_3276UP | Generator Problem- Alternator problem , Stolen Batteries , P.G Connected | Faulty System | generator | Generator | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | ATS / Engine | Components faulty/Gen battery is faulty need new one
IM764307 | 3276UP | 02_G_QN-BAKHANES_3276UP | Generator Problem- Alternator problem , Stolen Batteries , P.G Connected | Faulty System | Gen | Generator | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | ATS / Engine | Panorama pictures for each system/Last gen hour meter at Audit g ( 4570 )
IM764307 | 3276UP | 02_G_QN-BAKHANES_3276UP | Generator Problem- Alternator problem , Stolen Batteries , P.G Connected | Faulty System | generator | Generator | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | ATS / Engine | Panorama pictures for each system/Last gen hour meter at Audit g ( 4570 )
IM764307 | 3276UP | 02_G_QN-BAKHANES_3276UP | Generator Problem- Alternator problem , Stolen Batteries , P.G Connected | Faulty System | Gen | Generator | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM764307 | 3276UP | 02_G_QN-BAKHANES_3276UP | Generator Problem- Alternator problem , Stolen Batteries , P.G Connected | Faulty System | generator | Generator | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM764311 | 3454DE | 1061_D_GH-MAHLT-MENOF_3454DE | Access ET / GN problem / stolen batteries | Faulty System | batt | Batteries | 324838 | GH-MAHLT-MENOF | C2_3454DE_PH13 | Batteries | Item(s) stolen/Stolen Batteries
IM764311 | 3454DE | 1061_D_GH-MAHLT-MENOF_3454DE | Access ET / GN problem / stolen batteries | Faulty System | GN | Generator | 324838 | GH-MAHLT-MENOF | C2_3454DE_PH13 | ATS / Engine | Item(s) stolen/stolen batteries
IM764311 | 3454DE | 1061_D_GH-MAHLT-MENOF_3454DE | Access ET / GN problem / stolen batteries | Faulty System | GN | Generator | 324838 | GH-MAHLT-MENOF | C2_3454DE_PH13 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM764360 | 0038RE | 00210_C_0038RE_3P-SZ-RAS-ABU-DRAJ | Site Down Due To DG Power Alarm - dead batteries PLVD disconnect site to save cascaded Recovered once DG problem solved | Faulty System | DG | Generator | 304375 | SZ-RAS-ABU-DRAJ | C3_0038RE_PH2 | ATS / Engine | Components faulty/missing battery
IM764360 | 0038RE | 00210_C_0038RE_3P-SZ-RAS-ABU-DRAJ | Site Down Due To DG Power Alarm - dead batteries PLVD disconnect site to save cascaded Recovered once DG problem solved | Faulty System | DG | Generator | 304375 | SZ-RAS-ABU-DRAJ | C3_0038RE_PH2 | ATS / Engine | Wrong connection/welded cables
IM764360 | 0038RE | 00210_C_0038RE_3P-SZ-RAS-ABU-DRAJ | Site Down Due To DG Power Alarm - dead batteries PLVD disconnect site to save cascaded Recovered once DG problem solved | Faulty System | DG | Generator | 304375 | SZ-RAS-ABU-DRAJ | C3_0038RE_PH2 | ATS / Engine | Wrong connection/wrong connection & jumper on the contactor
IM764360 | 0038RE | 00210_C_0038RE_3P-SZ-RAS-ABU-DRAJ | Site Down Due To DG Power Alarm - dead batteries PLVD disconnect site to save cascaded Recovered once DG problem solved | Faulty System | DG | Generator | 304375 | SZ-RAS-ABU-DRAJ | C3_0038RE_PH2 | ATS / Engine | Wrong connection/cable not isolated
IM764360 | 0038RE | 00210_C_0038RE_3P-SZ-RAS-ABU-DRAJ | Site Down Due To DG Power Alarm - dead batteries PLVD disconnect site to save cascaded Recovered once DG problem solved | Faulty System | DG | Generator | 304375 | SZ-RAS-ABU-DRAJ | C3_0038RE_PH2 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/cables not terminated
IM764360 | 0038RE | 00210_C_0038RE_3P-SZ-RAS-ABU-DRAJ | Site Down Due To DG Power Alarm - dead batteries PLVD disconnect site to save cascaded Recovered once DG problem solved | Faulty System | DG | Generator | 304375 | SZ-RAS-ABU-DRAJ | C3_0038RE_PH2 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage
IM764363 | 0316RE | 03493_S_0316RE_SZ-GHAZZALY | Power outage // access PG // Weak batteries // Recovered | Faulty System | batt | Batteries | 355925 | 01_S_SZ-GHAZZALY_0316RE | C2_0316RE_PH12 | Rectifiers | Alarms reporting to the OMC/Alarm on the rectifier
IM764374 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to DG low water level and stolen batteries (M) | Faulty System | batt | Batteries | 314391 | REHAB-G17 | C1_3492CA_PH13 | Batteries | Some parts are missing/missing batteries
IM764374 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to DG low water level and stolen batteries (M) | Faulty System | DG | Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | ATS / Engine | Wrong connection/wrong connection
IM764388 | 3712DE | 0221_G_BH-QAMHA_3712DE | Main power problem " Disconnected by EC" @ BH-QAMHA_3712DE / SC GN not work due to SC / Solved and work on SC GN | Faulty System | GN | Generator | 304258 | BH-QAMHA | C1_3712DE_PH14 | ATS / Engine | Components faulty/Small generator not working // Site has history generator status alarm
IM764412 | 0646CA | 02128_N_0646CA_OM-BAYOUMI | down due to power failure and faulty batteries and no PG access (M) | Faulty System | batt | Batteries | 345350 | OM-BAYOUMI | C3_0646CA_PH8 | Rectifiers | Alarms reporting to the OMC/Major alarm is active on the site
IM764412 | 0646CA | 02128_N_0646CA_OM-BAYOUMI | down due to power failure and faulty batteries and no PG access (M) | Faulty System | batt | Batteries | 345350 | OM-BAYOUMI | C3_0646CA_PH8 | Batteries | Components faulty/Batteries are faulty (Site is down when the power is disconnected)
IM764445 | 3454DE | 1061_D_GH-MAHLT-MENOF_3454DE | ET Share / GN problem / Stolen batteries | Faulty System | batt | Batteries | 324838 | GH-MAHLT-MENOF | C2_3454DE_PH13 | Batteries | Item(s) stolen/Stolen Batteries
IM764445 | 3454DE | 1061_D_GH-MAHLT-MENOF_3454DE | ET Share / GN problem / Stolen batteries | Faulty System | GN | Generator | 324838 | GH-MAHLT-MENOF | C2_3454DE_PH13 | ATS / Engine | Item(s) stolen/stolen batteries
IM764445 | 3454DE | 1061_D_GH-MAHLT-MENOF_3454DE | ET Share / GN problem / Stolen batteries | Faulty System | GN | Generator | 324838 | GH-MAHLT-MENOF | C2_3454DE_PH13 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM764493 | 3639UP | 0501_G_LU-ODYSAT-QBLY_3639UP | PM generator ; Stolen batteries , Recovered | Faulty System | batt | Batteries | 356474 | 01_G_LU-ODYSAT-QBLY_3639UP | C1_3639UP_PH14 | Batteries | Some parts are (missing / stolen)/Batteries were stolen
IM764493 | 3639UP | 0501_G_LU-ODYSAT-QBLY_3639UP | PM generator ; Stolen batteries , Recovered | Faulty System | Gen | Generator | 356474 | 01_G_LU-ODYSAT-QBLY_3639UP | C1_3639UP_PH14 | ATS / Engine | Unit earth/Gen enclosure earth cable is missing
IM764493 | 3639UP | 0501_G_LU-ODYSAT-QBLY_3639UP | PM generator ; Stolen batteries , Recovered | Faulty System | generator | Generator | 356474 | 01_G_LU-ODYSAT-QBLY_3639UP | C1_3639UP_PH14 | ATS / Engine | Unit earth/Gen enclosure earth cable is missing
IM764493 | 3639UP | 0501_G_LU-ODYSAT-QBLY_3639UP | PM generator ; Stolen batteries , Recovered | Faulty System | Gen | Generator | 356474 | 01_G_LU-ODYSAT-QBLY_3639UP | C1_3639UP_PH14 | ATS / Engine | Unit earth/Missing earth cable at ATS panel
IM764493 | 3639UP | 0501_G_LU-ODYSAT-QBLY_3639UP | PM generator ; Stolen batteries , Recovered | Faulty System | generator | Generator | 356474 | 01_G_LU-ODYSAT-QBLY_3639UP | C1_3639UP_PH14 | ATS / Engine | Unit earth/Missing earth cable at ATS panel
IM764493 | 3639UP | 0501_G_LU-ODYSAT-QBLY_3639UP | PM generator ; Stolen batteries , Recovered | Faulty System | Gen | Generator | 356474 | 01_G_LU-ODYSAT-QBLY_3639UP | C1_3639UP_PH14 | ATS / Engine | Wrong connection/Two cables inserted in one slot can cause bad connections
IM764493 | 3639UP | 0501_G_LU-ODYSAT-QBLY_3639UP | PM generator ; Stolen batteries , Recovered | Faulty System | generator | Generator | 356474 | 01_G_LU-ODYSAT-QBLY_3639UP | C1_3639UP_PH14 | ATS / Engine | Wrong connection/Two cables inserted in one slot can cause bad connections
IM764493 | 3639UP | 0501_G_LU-ODYSAT-QBLY_3639UP | PM generator ; Stolen batteries , Recovered | Faulty System | Gen | Generator | 356474 | 01_G_LU-ODYSAT-QBLY_3639UP | C1_3639UP_PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/ cable is loose inside ATS panel
IM764493 | 3639UP | 0501_G_LU-ODYSAT-QBLY_3639UP | PM generator ; Stolen batteries , Recovered | Faulty System | generator | Generator | 356474 | 01_G_LU-ODYSAT-QBLY_3639UP | C1_3639UP_PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/ cable is loose inside ATS panel
IM764511 | 3464DE | 0151_Q_BH-SHANDID_3464DE | GN problem @BH-SHANDID_3464DE / stolen batteries | Faulty System | GN | Generator | 304032 | BH-SHANDID | C2_3464DE_PH13 | ATS / Engine | Components below rate (excluding main power feeder if not hot)/Generator voltage need adjustment
IM764516 | 0324UP | 1421_S_MN-BARTABAT_0324UP | Due to EC power cutoff , Stolen batteries , PG Connected | Faulty System | batt | Batteries | 324919 | 01_S_MN-BARTABAT_0324UP | C1_0324UP_PH8 | Batteries | Item(s) stolen/Site batteries were stolen
IM764615 | 0022SI | 03519_H_0022SI_IS-ABU-ATWA | Outage power in area located site , stolen batteries , once team arrive to connect PG power restored and site recovered | Faulty System | batt | Batteries | 325082 | 01_H_IS-ABU-ATWA_0022SI | C8_0022SI_PH1 | Batteries | Item(s) stolen/Battery string stolen
IM764618 | 0427DE | 0061_D_SK-EZBA-SARYA_0427DE | access Guard/GN problem/Stolen batteries/clear | Faulty System | batt | Batteries | 345382 | SK-EZBA-SARYA | C2_0427DE_PH4 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM764618 | 0427DE | 0061_D_SK-EZBA-SARYA_0427DE | access Guard/GN problem/Stolen batteries/clear | Faulty System | GN | Generator | 345382 | SK-EZBA-SARYA | C2_0427DE_PH4 | ATS / Engine | Components faulty/Exhaust fan not working and another not exist
IM764621 | 3126DE | 0121_S_DK-HAGYZEYA_3126DE | main power/Stolen batteries handel SK Roda,,DK-TAG-ELIZZ_ | Faulty System | batt | Batteries | 355992 | DK-HAGYZEYA | C6-3126DE-PH12 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM764623 | 3830DE | 1311_S_BH-MHLT-KYL_3830DE | Share VF / Main power / Stolen batteries | Faulty System | batt | Batteries | 356185 | BH-MHLT-KYL | C1_3830DE_PH14 | Batteries | Some parts are (missing / stolen)/No battery for site
IM764624 | 3532DE | 0511_S_SK-NATORA_3532DE | access Guard/week battery/clear after power back | Faulty System | batt | Batteries | 356262 | SK-NATORA | C2_3532DE_PH13 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM764654 | 0993UP | 0041_S_AT-ELOUNA_0993UP | Due to EC power cutoff , weak batteries , PG Connected | Faulty System | batt | Batteries | 355474 | 01_S_AT-ELOUNA_0993UP | C1_0993UP_PH12 | Rectifiers | Alarms reporting to the OMC/Power alarm not appeared on the omc
IM764707 | 3953DE | 0361_G_BH-MAARKA_3953DE | access ET/main power/weak batteries/clear after power back | Faulty System | batt | Batteries | 304235 | BH-MAARKA | C1_3953DE_PH15 | Batteries | Components faulty/Faulty battery and cable disconnected
IM764717 | 3784DE | 0661_S_KS-DAQLIT_3784DE | Share VF / Main power / faulty batteries | Faulty System | batt | Batteries | 335221 | KS-DAQLIT | C3_3784DE_PH14 | Batteries | Components faulty/Faulty battery (battearies are ballooned)
IM764723 | 3628DE | 0811_S_GH-QSR-BAGHDAD_3628DE | Main power / stolen batteries | Faulty System | batt | Batteries | 324836 | GH-QSR-BAGHDAD | C2_3628DE_PH13 | Batteries | Item(s) stolen/Stolen batteries
IM764745 | 0285DE | 1401_G_BH-ABU-HUMMUS_0285DE | GN problem / weak batteries | Faulty System | GN | Generator | 355484 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM764745 | 0285DE | 1401_G_BH-ABU-HUMMUS_0285DE | GN problem / weak batteries | Faulty System | GN | Generator | 355484 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Unit earth/fake earth
IM764745 | 0285DE | 1401_G_BH-ABU-HUMMUS_0285DE | GN problem / weak batteries | Faulty System | GN | Generator | 355484 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Components faulty/faulty
IM764745 | 0285DE | 1401_G_BH-ABU-HUMMUS_0285DE | GN problem / weak batteries | Faulty System | GN | Generator | 355484 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Components faulty/replace
IM764745 | 0285DE | 1401_G_BH-ABU-HUMMUS_0285DE | GN problem / weak batteries | Faulty System | GN | Generator | 304381 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Cables at 1 slot
IM764745 | 0285DE | 1401_G_BH-ABU-HUMMUS_0285DE | GN problem / weak batteries | Faulty System | GN | Generator | 304381 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot
IM764750 | 0490SI | 03534_S_0490SI_IS-NASR | Outage power in area located site , dead batteries , once team arrive to connect PG power restored and site recovered | Faulty System | batt | Batteries | 356007 | 01_S_IS-NASR_0490SI | C2_0490SI_PH14 | Rectifiers | Alarms reporting to the OMC/Rectifier alarm , A/C & door not apear on CAP
IM764750 | 0490SI | 03534_S_0490SI_IS-NASR | Outage power in area located site , dead batteries , once team arrive to connect PG power restored and site recovered | Faulty System | batt | Batteries | 356007 | 01_S_IS-NASR_0490SI | C2_0490SI_PH14 | Batteries | Components faulty/Battery voltag reading drop to 46 volt after we disconnect th rectifier C.B (Check the batteries)
IM764782 | 0003UP | 0311_N_AS-TROMBAT-AS_0003UP | Main power disconnection ,batteries are suspected to be weak , recovered when EC power come back | Faulty System | batt | Batteries | 345338 | 01_N_AS-TROMBAT-AS_0003UP | C1_0003UP_PH0 | Batteries | Some parts are (missing / stolen)/one Batteries string was stolen
IM764806 | 0517DE | 1541_G_QL-TUKH-TRAIN_0517DE | access Guard/main power/weak batteries/clear after power back | Faulty System | batt | Batteries | 303890 | QL-TUKH-TRAIN BSC | C1_0517DE_PH8 | Batteries | Item(s) stolen/stolen batteries
IM764852 | 4057DE | 0011_D_SK-SALHIYA-NTH_4057DE | GN problem/Stolen batteries/clear after check GN | Faulty System | batt | Batteries | 324501 | SK-SALHIYA-NTH | C3_4057DE_PH15 | Batteries | Item(s) stolen/No backup batteries.
IM764852 | 4057DE | 0011_D_SK-SALHIYA-NTH_4057DE | GN problem/Stolen batteries/clear after check GN | Faulty System | GN | Generator | 324501 | SK-SALHIYA-NTH | C3_4057DE_PH15 | ATS / Engine | Components faulty/Faulty GCM module.
IM764852 | 4057DE | 0011_D_SK-SALHIYA-NTH_4057DE | GN problem/Stolen batteries/clear after check GN | Faulty System | GN | Generator | 324501 | SK-SALHIYA-NTH | C3_4057DE_PH15 | ATS / Engine | Wrong connection/Some cables disconnected.
IM764852 | 4057DE | 0011_D_SK-SALHIYA-NTH_4057DE | GN problem/Stolen batteries/clear after check GN | Faulty System | GN | Generator | 324501 | SK-SALHIYA-NTH | C3_4057DE_PH15 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has oil leakage and bad condition.
IM764852 | 4057DE | 0011_D_SK-SALHIYA-NTH_4057DE | GN problem/Stolen batteries/clear after check GN | Faulty System | GN | Generator | 324501 | SK-SALHIYA-NTH | C3_4057DE_PH15 | ATS / Engine | Panorama pictures for each system/Overview.
IM764857 | 3628DE | 0811_S_GH-QSR-BAGHDAD_3628DE | Main power / stolen batteries / connected PG | Faulty System | batt | Batteries | 324836 | GH-QSR-BAGHDAD | C2_3628DE_PH13 | Batteries | Item(s) stolen/Stolen batteries
IM764871 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to DG problem and restored after clean fuel cycle and stolen batteries | Faulty System | batt | Batteries | 314391 | REHAB-G17 | C1_3492CA_PH13 | Batteries | Some parts are missing/missing batteries
IM764871 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to DG problem and restored after clean fuel cycle and stolen batteries | Faulty System | DG | Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | ATS / Engine | Wrong connection/wrong connection
IM764884 | 3743UP | 01_E_MN-EBAD-SHRONA_3743UP | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 324960 | 01_S_MN-EBAD-SHRONA_3743UP | C3_3743UP_PH15 | ATS / Engine | Components faulty/Gen battery is missing
IM764884 | 3743UP | 01_E_MN-EBAD-SHRONA_3743UP | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 324960 | 01_S_MN-EBAD-SHRONA_3743UP | C3_3743UP_PH15 | ATS / Engine | Components faulty/Gen battery is missing
IM764884 | 3743UP | 01_E_MN-EBAD-SHRONA_3743UP | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 324960 | 01_S_MN-EBAD-SHRONA_3743UP | C3_3743UP_PH15 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Main power cable is not protected in Pac Tube
IM764884 | 3743UP | 01_E_MN-EBAD-SHRONA_3743UP | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 324960 | 01_S_MN-EBAD-SHRONA_3743UP | C3_3743UP_PH15 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Main power cable is not protected in Pac Tube
IM764884 | 3743UP | 01_E_MN-EBAD-SHRONA_3743UP | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 324960 | 01_S_MN-EBAD-SHRONA_3743UP | C3_3743UP_PH15 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Battery cables not isolated
IM764884 | 3743UP | 01_E_MN-EBAD-SHRONA_3743UP | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 324960 | 01_S_MN-EBAD-SHRONA_3743UP | C3_3743UP_PH15 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Battery cables not isolated
IM764884 | 3743UP | 01_E_MN-EBAD-SHRONA_3743UP | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 324960 | 01_S_MN-EBAD-SHRONA_3743UP | C3_3743UP_PH15 | ATS / Engine | Panorama pictures for each system/Panorama
IM764884 | 3743UP | 01_E_MN-EBAD-SHRONA_3743UP | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 324960 | 01_S_MN-EBAD-SHRONA_3743UP | C3_3743UP_PH15 | ATS / Engine | Panorama pictures for each system/Panorama
IM764889 | 3445UP | 591_D_MN-TOKH_3445UP | Due to Generator problem , Stolen batteries , Recovered | Faulty System | Gen | Generator | 356182 | 01_G_MN-TOKH_3445UP | C1_3445UP_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage
IM764889 | 3445UP | 591_D_MN-TOKH_3445UP | Due to Generator problem , Stolen batteries , Recovered | Faulty System | generator | Generator | 356182 | 01_G_MN-TOKH_3445UP | C1_3445UP_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage
IM764889 | 3445UP | 591_D_MN-TOKH_3445UP | Due to Generator problem , Stolen batteries , Recovered | Faulty System | Gen | Generator | 356182 | 01_G_MN-TOKH_3445UP | C1_3445UP_PH14 | ATS / Engine | Components faulty/need battery
IM764889 | 3445UP | 591_D_MN-TOKH_3445UP | Due to Generator problem , Stolen batteries , Recovered | Faulty System | generator | Generator | 356182 | 01_G_MN-TOKH_3445UP | C1_3445UP_PH14 | ATS / Engine | Components faulty/need battery
IM764924 | 3712DE | 0221_G_BH-QAMHA_3712DE | GN problem @BH-QAMHA_3712DE / batteries under check | Faulty System | GN | Generator | 304258 | BH-QAMHA | C1_3712DE_PH14 | ATS / Engine | Components faulty/Small generator not working // Site has history generator status alarm
IM764934 | 0370UP | 1961_G_CAIRO-ASWAN-12_0370UP | Main power disconnection , stolen batteries , recovered when EC power come back | Faulty System | batt | Batteries | 304136 | 01_G_CAIRO-ASWAN-12_0370UP | C2_0370UP_PH8 | Batteries | Item(s) stolen/ Batteries were stolen
IM764954 | 3074UP | 01_D_QN-QENAWEYA_3074UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | Gen | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | ATS / Engine | Components faulty/Gen battery is faulty
IM764954 | 3074UP | 01_D_QN-QENAWEYA_3074UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | generator | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | ATS / Engine | Components faulty/Gen battery is faulty
IM764954 | 3074UP | 01_D_QN-QENAWEYA_3074UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | Gen | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | ATS / Engine | Components faulty/Main c.b inside gen had one faulty slot and one phase welded directly
IM764954 | 3074UP | 01_D_QN-QENAWEYA_3074UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | generator | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | ATS / Engine | Components faulty/Main c.b inside gen had one faulty slot and one phase welded directly
IM764954 | 3074UP | 01_D_QN-QENAWEYA_3074UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | Gen | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage exist under fuel tank
IM764954 | 3074UP | 01_D_QN-QENAWEYA_3074UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | generator | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage exist under fuel tank
IM764954 | 3074UP | 01_D_QN-QENAWEYA_3074UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | Gen | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | ATS / Engine | Panorama pictures for each system/Open gland in Gen enclosure need insulation
IM764954 | 3074UP | 01_D_QN-QENAWEYA_3074UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | generator | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | ATS / Engine | Panorama pictures for each system/Open gland in Gen enclosure need insulation
IM764954 | 3074UP | 01_D_QN-QENAWEYA_3074UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | Gen | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM764954 | 3074UP | 01_D_QN-QENAWEYA_3074UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | generator | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM764954 | 3074UP | 01_D_QN-QENAWEYA_3074UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | Gen | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | ATS / Engine | Panorama pictures for each system/Last Gen hour meter at Audit G (18510 )
IM764954 | 3074UP | 01_D_QN-QENAWEYA_3074UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | generator | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | ATS / Engine | Panorama pictures for each system/Last Gen hour meter at Audit G (18510 )
IM765018 | 0280DE | 0601_Q_BH-KOMHMADA-NTH_0280DE | GN problem @ BH-KOMHMADA-NTH_0280DE / Stolen batteries | Faulty System | batt | Batteries | 355878 | BH-KOMHMDA-NTH | C6_0280DE_PH3 | Batteries | Some parts are (missing / stolen)/Stolen
IM765018 | 0280DE | 0601_Q_BH-KOMHMADA-NTH_0280DE | GN problem @ BH-KOMHMADA-NTH_0280DE / Stolen batteries | Faulty System | GN | Generator | 355878 | BH-KOMHMDA-NTH | C6_0280DE_PH3 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Leakage
IM765018 | 0280DE | 0601_Q_BH-KOMHMADA-NTH_0280DE | GN problem @ BH-KOMHMADA-NTH_0280DE / Stolen batteries | Faulty System | GN | Generator | 355878 | BH-KOMHMDA-NTH | C6_0280DE_PH3 | ATS / Engine | Unit earth/Disconnected
IM765025 | 0613DE | 00167_D_0613DE_SANDORINI-CLUB | GN problem/Batteries under investigation/clear after check GN | Faulty System | GN | Generator | 303981 | Sandorini Country Club | C1_0613DE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check and clean
IM765048 | 0339UP | 0351_G_MN-SALEEBA_0339UP | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 324684 | 01_G_MN-SALEEBA_0339UP | C3_0339UP_PH8 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/protect cable
IM765048 | 0339UP | 0351_G_MN-SALEEBA_0339UP | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 324684 | 01_G_MN-SALEEBA_0339UP | C3_0339UP_PH8 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/protect cable
IM765048 | 0339UP | 0351_G_MN-SALEEBA_0339UP | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 324684 | 01_G_MN-SALEEBA_0339UP | C3_0339UP_PH8 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage
IM765048 | 0339UP | 0351_G_MN-SALEEBA_0339UP | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 324684 | 01_G_MN-SALEEBA_0339UP | C3_0339UP_PH8 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage
IM765069 | 0164RE | 03835_S_0164RE_RS-QUSEIR-ENT | Outage power in area located site , dead batteries , access PG Recovered once power restored | Faulty System | batt | Batteries | 356402 | 01_S_RS-QUSEIR-ENT_0164RE | C1_0164RE_PH9 | Rectifiers | Alarms reporting to the OMC/Rectifer minor alarm was looped at ddf rack
IM765125 | 0658DE | 0661_D_BH-MNSHYT-KHYAT_0658DE | GN problem @ BH-MNSHYT-KHYAT_0658DE / weak batteries / power alarm received 10:30 PM | Faulty System | GN | Generator | 356260 | BH-MNSHYT-KHYAT | C2_0658DE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has leakage
IM765125 | 0658DE | 0661_D_BH-MNSHYT-KHYAT_0658DE | GN problem @ BH-MNSHYT-KHYAT_0658DE / weak batteries / power alarm received 10:30 PM | Faulty System | GN | Generator | 356260 | BH-MNSHYT-KHYAT | C2_0658DE_PH9 | ATS / Engine | Components below/over rate (excluding main power feeder if not hot)/Generator has high voltage
IM765159 | 0427DE | 0061_D_SK-EZBA-SARYA_0427DE | GN. Problem /Stolen batteries / clear after checking GN. | Faulty System | batt | Batteries | 345382 | SK-EZBA-SARYA | C2_0427DE_PH4 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM765159 | 0427DE | 0061_D_SK-EZBA-SARYA_0427DE | GN. Problem /Stolen batteries / clear after checking GN. | Faulty System | GN | Generator | 345382 | SK-EZBA-SARYA | C2_0427DE_PH4 | ATS / Engine | Components faulty/Exhaust fan not working and another not exist
IM765165 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Generator stopped due to LOP alarm and site has stolen backup batteries | Faulty System | Gen | Generator | 355484 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM765165 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Generator stopped due to LOP alarm and site has stolen backup batteries | Faulty System | generator | Generator | 355484 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM765165 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Generator stopped due to LOP alarm and site has stolen backup batteries | Faulty System | Gen | Generator | 355484 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Unit earth/fake earth
IM765165 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Generator stopped due to LOP alarm and site has stolen backup batteries | Faulty System | generator | Generator | 355484 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Unit earth/fake earth
IM765165 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Generator stopped due to LOP alarm and site has stolen backup batteries | Faulty System | Gen | Generator | 355484 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Components faulty/faulty
IM765165 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Generator stopped due to LOP alarm and site has stolen backup batteries | Faulty System | generator | Generator | 355484 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Components faulty/faulty
IM765165 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Generator stopped due to LOP alarm and site has stolen backup batteries | Faulty System | Gen | Generator | 355484 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Components faulty/replace
IM765165 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Generator stopped due to LOP alarm and site has stolen backup batteries | Faulty System | generator | Generator | 355484 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Components faulty/replace
IM765165 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Generator stopped due to LOP alarm and site has stolen backup batteries | Faulty System | Gen | Generator | 304381 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Cables at 1 slot
IM765165 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Generator stopped due to LOP alarm and site has stolen backup batteries | Faulty System | generator | Generator | 304381 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Cables at 1 slot
IM765165 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Generator stopped due to LOP alarm and site has stolen backup batteries | Faulty System | Gen | Generator | 304381 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot
IM765165 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Generator stopped due to LOP alarm and site has stolen backup batteries | Faulty System | generator | Generator | 304381 | BH-ABU-HUMMUS | C2_0285DE_PH3 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot
IM765200 | 3551UP | 1981_D_SG-ABOU-AZIZ_3551UP | TT will be modified as we received automation mails at 04:05 am , Generator Stoppage , Weak batteries ; Solved | Faulty System | Gen | Generator | 304169 | 01_G_SG-ABOU-AZIZ_3551UP | C2_3551UP_PH14 | ATS / Engine | Components faulty/Gen battery is faulty
IM765200 | 3551UP | 1981_D_SG-ABOU-AZIZ_3551UP | TT will be modified as we received automation mails at 04:05 am , Generator Stoppage , Weak batteries ; Solved | Faulty System | generator | Generator | 304169 | 01_G_SG-ABOU-AZIZ_3551UP | C2_3551UP_PH14 | ATS / Engine | Components faulty/Gen battery is faulty
IM765210 | 3712DE | 0221_G_BH-QAMHA_3712DE | GN problem @BH-QAMHA_3712DE / batteries under check | Faulty System | GN | Generator | 304258 | BH-QAMHA | C1_3712DE_PH14 | ATS / Engine | Components faulty/Small generator not working // Site has history generator status alarm
IM765211 | 0102RE | 00086_S_0102RE_SZ-STLLADEMARE | Outage power in area located site , dead batteries , access PG Recovered once power restored | Faulty System | batt | Batteries | 324988 | SZ-STLLADEMARE | C3_0102RE_PH3 | Batteries | Item(s) stolen/Battery string stolen
IM765231 | 3594DE | 1241_S_BH-TAYRIYA_3594DE | Main Power / stolen batteries / clear after power back | Faulty System | batt | Batteries | 325119 | BH-TAYRIYA | C1-3594DE-PH13 | Batteries | Item(s) stolen/There is no battery for site
IM765233 | 3352DE | 0071_D_BH-SHBRA-OSEEM_3352DE | Access VF. / Main Power / Stolen batteries / Clear after power back | Faulty System | batt | Batteries | 325117 | BH-SHBRA-OSEEM | C1_3352DE_PH12 | Batteries | Item(s) stolen/There is no battery for site
IM765234 | 3102UP | 1431_K_QN-MOSTAAMARA_3102UP_X | Due to Gen stopped Problem , stolen batteries , solved. | Faulty System | batt | Batteries | 324765 | 01_G_QN-MOSTAAMARA_3102UP | C1_3102UP_PH13 | Batteries | Item(s) stolen/Batteries were stolen
IM765234 | 3102UP | 1431_K_QN-MOSTAAMARA_3102UP_X | Due to Gen stopped Problem , stolen batteries , solved. | Faulty System | Gen | Generator | 324765 | 01_G_QN-MOSTAAMARA_3102UP | C1_3102UP_PH13 | ATS / Engine | Wrong connection/cables were welded in Gen
IM765234 | 3102UP | 1431_K_QN-MOSTAAMARA_3102UP_X | Due to Gen stopped Problem , stolen batteries , solved. | Faulty System | Gen | Generator | 324765 | 01_G_QN-MOSTAAMARA_3102UP | C1_3102UP_PH13 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Missing terminals at gen C.B inside Ats panel
IM765234 | 3102UP | 1431_K_QN-MOSTAAMARA_3102UP_X | Due to Gen stopped Problem , stolen batteries , solved. | Faulty System | Gen | Generator | 324765 | 01_G_QN-MOSTAAMARA_3102UP | C1_3102UP_PH13 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/bad connection inside ats panel
IM765234 | 3102UP | 1431_K_QN-MOSTAAMARA_3102UP_X | Due to Gen stopped Problem , stolen batteries , solved. | Faulty System | Gen | Generator | 324765 | 01_G_QN-MOSTAAMARA_3102UP | C1_3102UP_PH13 | ATS / Engine | Item(s) stolen/Gen battery is missing
IM765234 | 3102UP | 1431_K_QN-MOSTAAMARA_3102UP_X | Due to Gen stopped Problem , stolen batteries , solved. | Faulty System | Gen | Generator | 324765 | 01_G_QN-MOSTAAMARA_3102UP | C1_3102UP_PH13 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage inside Gen
IM765234 | 3102UP | 1431_K_QN-MOSTAAMARA_3102UP_X | Due to Gen stopped Problem , stolen batteries , solved. | Faulty System | Gen | Generator | 324765 | 01_G_QN-MOSTAAMARA_3102UP | C1_3102UP_PH13 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage beside Gen enclosure
IM765234 | 3102UP | 1431_K_QN-MOSTAAMARA_3102UP_X | Due to Gen stopped Problem , stolen batteries , solved. | Faulty System | Gen | Generator | 324765 | 01_G_QN-MOSTAAMARA_3102UP | C1_3102UP_PH13 | ATS / Engine | Panorama pictures for each system/Open gland in Gen enclosure need insulation
IM765234 | 3102UP | 1431_K_QN-MOSTAAMARA_3102UP_X | Due to Gen stopped Problem , stolen batteries , solved. | Faulty System | Gen | Generator | 324765 | 01_G_QN-MOSTAAMARA_3102UP | C1_3102UP_PH13 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM765268 | 3454DE | 1061_D_GH-MAHLT-MENOF_3454DE | Share ET / GN stopped / Stolen batteries | Faulty System | batt | Batteries | 324838 | GH-MAHLT-MENOF | C2_3454DE_PH13 | Batteries | Item(s) stolen/Stolen Batteries
IM765268 | 3454DE | 1061_D_GH-MAHLT-MENOF_3454DE | Share ET / GN stopped / Stolen batteries | Faulty System | GN | Generator | 324838 | GH-MAHLT-MENOF | C2_3454DE_PH13 | ATS / Engine | Item(s) stolen/stolen batteries
IM765268 | 3454DE | 1061_D_GH-MAHLT-MENOF_3454DE | Share ET / GN stopped / Stolen batteries | Faulty System | GN | Generator | 324838 | GH-MAHLT-MENOF | C2_3454DE_PH13 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM765278 | 0029RE | 03478_S_0029RE_SZ-SUEZ9 | Outage power in area located site , dead batteries , access PG Recovered once power restored | Faulty System | batt | Batteries | 345368 | 01_S_SZ-SUEZ9_0029RE | C1_0029RE_PH1 | Batteries | Cables termination/lugs (AC side), lugs (DC side)/Loose in the battery cable
IM765379 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN. Problem / batteries under investigation@MIT-GABIR_3833DE / Clear after checking GN | Faulty System | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | ATS / Engine | Wrong connection/Welding cables
IM765379 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN. Problem / batteries under investigation@MIT-GABIR_3833DE / Clear after checking GN | Faulty System | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot
IM765386 | 0150UP | 0191_H_GIZA-LUXOR-19_0150UP | Main power disconnection ,batteries are suspected to be weak , P.G connected | Faulty System | batt | Batteries | 356518 | 01_W_GIZA-LUXOR-19_0150UP | C1_0150UP_PH3 | Batteries | Components faulty/backup voltage drop too fast ( batteries need recheck)
IM765438 | 3551CA | 02797_G_3551CA_MADINATY-2 | down due to PM problem & no backup & access PG (T) | Faulty System | backup | Batteries | 324699 | MADINATY-2 | C1_3551CA_PH13 | Batteries | Some parts are missing/missing batteries
IM765464 | 0581DE | 1571_S_SK-IKYAD-BHARIA_0581DE | Hi temp/clear after check Ac's | Faulty System | Hi Temp | A/Cs | 324498 | SK-IKYAD-BHARIA | C1_0581DE_PH9 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/Faulty A/C (site working on one A/C only).
IM765469 | 3454DE | 1061_D_GH-MAHLT-MENOF_3454DE | ET Share / GN problem / Stolen batteries | Faulty System | batt | Batteries | 324838 | GH-MAHLT-MENOF | C2_3454DE_PH13 | Batteries | Item(s) stolen/Stolen Batteries
IM765469 | 3454DE | 1061_D_GH-MAHLT-MENOF_3454DE | ET Share / GN problem / Stolen batteries | Faulty System | GN | Generator | 324838 | GH-MAHLT-MENOF | C2_3454DE_PH13 | ATS / Engine | Item(s) stolen/stolen batteries
IM765469 | 3454DE | 1061_D_GH-MAHLT-MENOF_3454DE | ET Share / GN problem / Stolen batteries | Faulty System | GN | Generator | 324838 | GH-MAHLT-MENOF | C2_3454DE_PH13 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM765483 | 3110DE | 1681_D_GH-SHUBRA-RIS_3110DE | Acccess VF / VF GN problem @ GH-SHUBRA-RIS_3110DE / weak batteries | Faulty System | GN | Generator | 324613 | GH-SHUBRA-RIS | C1_3110DE_PH12 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM765506 | 3126DE | 0121_S_DK-HAGYZEYA_3126DE | main power/Stolen batteries/handel SK-SAWALEH_3338DE,SK-TELRAK_0798DE,TAMEY-AMDID_0347D | Faulty System | batt | Batteries | 355992 | DK-HAGYZEYA | C6-3126DE-PH12 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM765531 | 0050DE | 0001_S_GH-SHABSHR-HAS_0050DE | Main power / batteries under check / connected PG | Faulty System | batt | Batteries | 304298 | GH-SHABSHR-HAS | C1_0050DE_PH1 | Batteries | Some parts are missing/cover
IM765543 | 3368DE | 0201_S_BH-ABO-SHIQAF_3368DE | Access VF / Main power / stolen batteries | Faulty System | batt | Batteries | 324904 | BH-ABO-SHIQAF | C1_3368DE_PH12 | Batteries | Item(s) stolen/There is no battery for site
IM765544 | 3590DE | 1631_S_BH-HADIN_3590DE | GN problem / stolen batteries / connected PG | Faulty System | batt | Batteries | 324439 | BH-HADIN | C2_3590DE_PH13 | Batteries | Item(s) stolen/There is no battery for site
IM765544 | 3590DE | 1631_S_BH-HADIN_3590DE | GN problem / stolen batteries / connected PG | Faulty System | GN | Generator | 324439 | BH-HADIN | C2_3590DE_PH13 | ATS / Engine | Components faulty/Check small generator operation (There is no battery for site)
IM765605 | 3151UP | 1561_S_BS-QIMAN-AROS_3151UP | Due to EC power cutoff , weak batteries , PG Connected | Faulty System | batt | Batteries | 355911 | 01_S_BS-QIMAN-AROS_3151UP | C2_3151UP_PH13 | Rectifiers | Alarms reporting to the OMC/Loop on the minor alarm in DDF (Port 6)
IM765605 | 3151UP | 1561_S_BS-QIMAN-AROS_3151UP | Due to EC power cutoff , weak batteries , PG Connected | Faulty System | batt | Batteries | 355911 | 01_S_BS-QIMAN-AROS_3151UP | C2_3151UP_PH13 | Rectifiers | Alarms reporting to the OMC/The power alarm is faulty (Always active on the rectifier and OMC)
IM765621 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | ATS / Engine | Components faulty/Gen battery was defected
IM765621 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | ATS / Engine | Components faulty/Gen battery was defected
IM765621 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/ATS Cables not organized
IM765621 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/ATS Cables not organized
IM765626 | 0673CA | 02654_S_0673CA_ASMA-FAHMY | down due to main power & weak batteries at 0673CA_ASMA-FAHMY (T) | Faulty System | batt | Batteries | 356212 | ASMA-FAHMY | C1_0673CA_PH8 | Batteries | Some parts are (missing / stolen)/missing batteries
IM765658 | 0038RE | 00210_C_0038RE_3P-SZ-RAS-ABU-DRAJ | DG Stopped , dead batteries , once team arrive and fix DG Site recovered | Faulty System | DG | Generator | 304375 | SZ-RAS-ABU-DRAJ | C3_0038RE_PH2 | ATS / Engine | Components faulty/missing battery
IM765658 | 0038RE | 00210_C_0038RE_3P-SZ-RAS-ABU-DRAJ | DG Stopped , dead batteries , once team arrive and fix DG Site recovered | Faulty System | DG | Generator | 304375 | SZ-RAS-ABU-DRAJ | C3_0038RE_PH2 | ATS / Engine | Wrong connection/welded cables
IM765658 | 0038RE | 00210_C_0038RE_3P-SZ-RAS-ABU-DRAJ | DG Stopped , dead batteries , once team arrive and fix DG Site recovered | Faulty System | DG | Generator | 304375 | SZ-RAS-ABU-DRAJ | C3_0038RE_PH2 | ATS / Engine | Wrong connection/wrong connection & jumper on the contactor
IM765658 | 0038RE | 00210_C_0038RE_3P-SZ-RAS-ABU-DRAJ | DG Stopped , dead batteries , once team arrive and fix DG Site recovered | Faulty System | DG | Generator | 304375 | SZ-RAS-ABU-DRAJ | C3_0038RE_PH2 | ATS / Engine | Wrong connection/cable not isolated
IM765658 | 0038RE | 00210_C_0038RE_3P-SZ-RAS-ABU-DRAJ | DG Stopped , dead batteries , once team arrive and fix DG Site recovered | Faulty System | DG | Generator | 304375 | SZ-RAS-ABU-DRAJ | C3_0038RE_PH2 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/cables not terminated
IM765658 | 0038RE | 00210_C_0038RE_3P-SZ-RAS-ABU-DRAJ | DG Stopped , dead batteries , once team arrive and fix DG Site recovered | Faulty System | DG | Generator | 304375 | SZ-RAS-ABU-DRAJ | C3_0038RE_PH2 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage
IM765668 | 3089UP | 2141_S_SG-GALAWEYA_3089UP | Main power disconnection ,batteries stolen , Power meter out of Charge , Escalated , our team in site to Connect PG and waiting Guard more than 45min , VF team solved power meter also , recovered . | Faulty System | batt | Batteries | 356371 | 01_S_SG-GALAWEYA_3089UP | C1_3089UP_PH13 | Batteries | Some parts are (missing / stolen)/site batteries were Stolen
IM765683 | 0427DE | 0061_D_SK-EZBA-SARYA_0427DE | GN problem/no battery/team on way | Faulty System | batt | Batteries | 345382 | SK-EZBA-SARYA | C2_0427DE_PH4 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM765683 | 0427DE | 0061_D_SK-EZBA-SARYA_0427DE | GN problem/no battery/team on way | Faulty System | GN | Generator | 345382 | SK-EZBA-SARYA | C2_0427DE_PH4 | ATS / Engine | Components faulty/Exhaust fan not working and another not exist
IM765693 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Share VF / Main power / Stolen batteries | Faulty System | batt | Batteries | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | Batteries | Item(s) stolen/Stolen
IM765715 | 0490SI | 03534_S_0490SI_IS-NASR | Outage power in area located site , dead batteries , once team arrive to connect PG power restored and site recovered | Faulty System | batt | Batteries | 356007 | 01_S_IS-NASR_0490SI | C2_0490SI_PH14 | Rectifiers | Alarms reporting to the OMC/Rectifier alarm , A/C & door not apear on CAP
IM765715 | 0490SI | 03534_S_0490SI_IS-NASR | Outage power in area located site , dead batteries , once team arrive to connect PG power restored and site recovered | Faulty System | batt | Batteries | 356007 | 01_S_IS-NASR_0490SI | C2_0490SI_PH14 | Batteries | Components faulty/Battery voltag reading drop to 46 volt after we disconnect th rectifier C.B (Check the batteries)
IM765728 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN problem/Stolen batteries/clear after check GN | Faulty System | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | ATS / Engine | Wrong connection/Welding cables
IM765728 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN problem/Stolen batteries/clear after check GN | Faulty System | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot
IM765742 | 3620DE | 0631_S_QL-BATIMDA_3620DE | access Guard/Guard switch MCB OFF finencial problem/Stolen batteries@QL-BATMIDA_3620DE | Faulty System | batt | Batteries | 356052 | QL-BATIMDA | C02_3620DE_PH13 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM765774 | 0734DE | 0441_D_MF-TANTA-HW1_0734DE | GN problem / solar theft case / stolen batteries / PG connected | Faulty System | batt | Batteries | 356142 | MF-TANTA-HW1 | C1_0734DE_PH9 | Rectifiers | Alarms reporting to the OMC/Site has fake power alarm
IM765774 | 0734DE | 0441_D_MF-TANTA-HW1_0734DE | GN problem / solar theft case / stolen batteries / PG connected | Faulty System | batt | Batteries | 356142 | MF-TANTA-HW1 | C1_0734DE_PH9 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM765774 | 0734DE | 0441_D_MF-TANTA-HW1_0734DE | GN problem / solar theft case / stolen batteries / PG connected | Faulty System | GN | Generator | 356142 | MF-TANTA-HW1 | C1_0734DE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has leakage
IM765780 | 0711DE | 0701_S_GH-GOMHORIYAH_0711DE | Access TE " access blocked " / H.T alarm / hanging BTS | Faulty System | H.T | A/Cs | 335126 | GH-GOMHORIYAH | C2_0711DE_PH09 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/Faulty
IM765780 | 0711DE | 0701_S_GH-GOMHORIYAH_0711DE | Access TE " access blocked " / H.T alarm / hanging BTS | Faulty System | H.T | A/Cs | 335126 | GH-GOMHORIYAH | C2_0711DE_PH09 | A/Cs Cooling / Free Cooling / Ventilation | Wrong connection/terminals in one slot
IM765788 | 0485DE | K_MF-BARAHIM_21106_1 | Main power /Batteries under investigation@BARAHIM_0485DE/clear after power back | Faulty System | batt | Batteries | 304303 | MF-BARAHIM | C5_0485DE_PH7 | Batteries | Some parts are missing/Battery without covers
IM765858 | 3798DE | 1471_S_SK-MNZL-MYMON_3798DE | power crises/Main power/Stolen batteries@MNZL-MYMON_3798DE/handel nodal sites AWLAD-MUSA,,Fadadna | Faulty System | batt | Batteries | 355763 | SK-MNZL-MYMON | C2-3798DE-PH14 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM765863 | 3823DE | 1121_G_SK-DAHTAMON_3823DE | power crises/Main power/Stolen batteries/handel nodal sites AWLAD-MUSA,,Fadadna | Faulty System | batt | Batteries | 303844 | SK-DAHTAMON | C1_3823DE_PH14 | Batteries | Item(s) stolen/No backup batteries.
IM765865 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to dynamo problem and site has weak backup batteries | Faulty System | backup | Batteries | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | Batteries | Item(s) stolen/One of batteries string was stolen
IM765865 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to dynamo problem and site has weak backup batteries | Faulty System | batt | Batteries | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | Batteries | Item(s) stolen/One of batteries string was stolen
IM765865 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to dynamo problem and site has weak backup batteries | Faulty System | Gen | Generator | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | ATS / Engine | Components faulty/Gen battery is defected
IM765865 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to dynamo problem and site has weak backup batteries | Faulty System | generator | Generator | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | ATS / Engine | Components faulty/Gen battery is defected
IM765865 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to dynamo problem and site has weak backup batteries | Faulty System | Gen | Generator | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Gen battery cables not isolated well
IM765865 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to dynamo problem and site has weak backup batteries | Faulty System | generator | Generator | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Gen battery cables not isolated well
IM765865 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to dynamo problem and site has weak backup batteries | Faulty System | Gen | Generator | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | ATS / Engine | Panorama pictures for each system/Open gland in Gen enclosure need insulation
IM765865 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to dynamo problem and site has weak backup batteries | Faulty System | generator | Generator | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | ATS / Engine | Panorama pictures for each system/Open gland in Gen enclosure need insulation
IM765865 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to dynamo problem and site has weak backup batteries | Faulty System | Gen | Generator | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM765865 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to dynamo problem and site has weak backup batteries | Faulty System | generator | Generator | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM765865 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to dynamo problem and site has weak backup batteries | Faulty System | Gen | Generator | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | ATS / Engine | Panorama pictures for each system/Last Gen hour meter at Auidt G ( 661 )
IM765865 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to dynamo problem and site has weak backup batteries | Faulty System | generator | Generator | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | ATS / Engine | Panorama pictures for each system/Last Gen hour meter at Auidt G ( 661 )
IM765870 | 3245CA | 01973_S_3245CA_10th-RSD-6 | EC power outage / weak batteries / cleared on PG till E power restored | Faulty System | batt | Batteries | 356443 | 10TH-RSD-6 | C4_3245CA_PH11 | Batteries | Some parts are (missing / stolen)/Battery string stolen
IM765873 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG Stoppage / weak batteries /radiator problem / cleared after power restored | Faulty System | batt | Batteries | 356434 | 01_G_SS-RAMADA-SEDR_0371SI | C4_0371SI_PH09 | Batteries | Some parts are (missing / stolen)/Battery string stolen
IM765873 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG Stoppage / weak batteries /radiator problem / cleared after power restored | Faulty System | DG | Generator | 356434 | 01_G_SS-RAMADA-SEDR_0371SI | C4_0371SI_PH09 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage
IM765873 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG Stoppage / weak batteries /radiator problem / cleared after power restored | Faulty System | DG | Generator | 356434 | 01_G_SS-RAMADA-SEDR_0371SI | C4_0371SI_PH09 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage
IM765873 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG Stoppage / weak batteries /radiator problem / cleared after power restored | Faulty System | DG | Generator | 356434 | 01_G_SS-RAMADA-SEDR_0371SI | C4_0371SI_PH09 | ATS / Engine | Components faulty/Generator battery defected
IM765873 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG Stoppage / weak batteries /radiator problem / cleared after power restored | Faulty System | DG | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure
IM765873 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG Stoppage / weak batteries /radiator problem / cleared after power restored | Faulty System | DG | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Wrong connection/generator battery as used in the site and not suitable in High temp
IM765923 | 3009AL | 03232_D_3009AL_MM-ALMN-APT2 | VF guard access problem/ GN problem/ weak batteries/ restored after solve GN problem | Faulty System | GN | Generator | 324992 | MM-ALMN-APT2 | C1_3009AL_PH19 | ATS / Engine | Components faulty/Burned generator need to be replaced.
IM765923 | 3009AL | 03232_D_3009AL_MM-ALMN-APT2 | VF guard access problem/ GN problem/ weak batteries/ restored after solve GN problem | Faulty System | GN | Generator | 324992 | MM-ALMN-APT2 | C1_3009AL_PH19 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Vodafone gen has leakage.
IM765938 | 0490SI | 03534_S_0490SI_IS-NASR | EC power outage /weak batteries / cleared after power restored | Faulty System | batt | Batteries | 356007 | 01_S_IS-NASR_0490SI | C2_0490SI_PH14 | Rectifiers | Alarms reporting to the OMC/Rectifier alarm , A/C & door not apear on CAP
IM765938 | 0490SI | 03534_S_0490SI_IS-NASR | EC power outage /weak batteries / cleared after power restored | Faulty System | batt | Batteries | 356007 | 01_S_IS-NASR_0490SI | C2_0490SI_PH14 | Batteries | Components faulty/Battery voltag reading drop to 46 volt after we disconnect th rectifier C.B (Check the batteries)
IM765970 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to Deliberately Switched Off & stolen batteries (T) | Faulty System | batt | Batteries | 314391 | REHAB-G17 | C1_3492CA_PH13 | Batteries | Some parts are missing/missing batteries
IM765987 | 3333DE | 0181_S_BH-OM-SABER_3333DE | Main power/week battery/clear after power back | Faulty System | batt | Batteries | 304089 | BH-OM-SABER_SSS0 | C1_3333DE_PH12 | Batteries | Item(s) stolen/There is no battery for site
IM765989 | 3299DE | 0541_S_KS-ZAAFRAN_3299DE | Main power / Weak batteries / VF Share / BDT @ 16/03/2019 Is: 1.00 | Faulty System | batt | Batteries | 355873 | KS-ZAAFRAN | C1_3299DE_PH12 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM766047 | 3126DE | 0121_S_DK-HAGYZEYA_3126DE | main power/Stolen batteries/handel SK-SAWALEH_3338DE,SK-TELRAK_0798DE,TAMEY-AMDID_0347D | Faulty System | batt | Batteries | 355992 | DK-HAGYZEYA | C6-3126DE-PH12 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM766078 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to DG Fuel Pump problem & stolen batteries (T) | Faulty System | batt | Batteries | 314391 | REHAB-G17 | C1_3492CA_PH13 | Batteries | Some parts are missing/missing batteries
IM766078 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to DG Fuel Pump problem & stolen batteries (T) | Faulty System | DG | Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | ATS / Engine | Wrong connection/wrong connection
IM766086 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG stoppage / weak batteries / cleared after power restored | Faulty System | batt | Batteries | 356434 | 01_G_SS-RAMADA-SEDR_0371SI | C4_0371SI_PH09 | Batteries | Some parts are (missing / stolen)/Battery string stolen
IM766086 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 356434 | 01_G_SS-RAMADA-SEDR_0371SI | C4_0371SI_PH09 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage
IM766086 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 356434 | 01_G_SS-RAMADA-SEDR_0371SI | C4_0371SI_PH09 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage
IM766086 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 356434 | 01_G_SS-RAMADA-SEDR_0371SI | C4_0371SI_PH09 | ATS / Engine | Components faulty/Generator battery defected
IM766086 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure
IM766086 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Wrong connection/generator battery as used in the site and not suitable in High temp
IM766091 | 0324UP | 1421_S_MN-BARTABAT_0324UP | Commercial power cut off and site has stolen backup batteries, recovered | Faulty System | backup | Batteries | 324919 | 01_S_MN-BARTABAT_0324UP | C1_0324UP_PH8 | Batteries | Item(s) stolen/Site batteries were stolen
IM766091 | 0324UP | 1421_S_MN-BARTABAT_0324UP | Commercial power cut off and site has stolen backup batteries, recovered | Faulty System | batt | Batteries | 324919 | 01_S_MN-BARTABAT_0324UP | C1_0324UP_PH8 | Batteries | Item(s) stolen/Site batteries were stolen
IM766155 | 0882DE | 1091_D_GH-MHLA-BHR-ST_0882DE | GN problem @ GH-MHLA-BHR-ST_0882DE / batteries under check | Faulty System | GN | Generator | 324934 | GH-MHLA-BHR-ST | C6_0882DE_PH09 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check, clean
IM766161 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problrm/stolen batteries/clear after check GN | Faulty System | batt | Batteries | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | Batteries | Some parts are missing/Battery cabinet need cleaning (from inside) and holes need sealing.
IM766161 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problrm/stolen batteries/clear after check GN | Faulty System | batt | Batteries | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | Batteries | Some parts are missing/Batteries poles need have missing covers.
IM766161 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problrm/stolen batteries/clear after check GN | Faulty System | GN | Generator | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | ATS / Engine | Components faulty/Generator has bad performance and need overall.
IM766161 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problrm/stolen batteries/clear after check GN | Faulty System | GN | Generator | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | ATS / Engine | Panorama pictures for each system/Overview.
IM766179 | 0882DE | 1091_D_GH-MHLA-BHR-ST_0882DE | GN problem @ GH-MHLA-BHR-ST_0882DE / batteries under check / connect PG / lock 2G | Faulty System | GN | Generator | 324934 | GH-MHLA-BHR-ST | C6_0882DE_PH09 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check, clean
IM766181 | 0914CA | 00138_L_0914CA_MAADI-TABARK | down due to DG LOP and stolen batt. (I) | Faulty System | batt | Batteries | 345257 | MAADI-TABARK | C1_0914CA_PH09 | Batteries | Some parts are missing/missing batteries
IM766186 | 0303AL | 0451_N_WARDIAN-EST_0303AL | High Temperature Problem / Problem Solved after solving A/Cs Problem and reset BTS | Faulty System | A/Cs | A/Cs | 355917 | Wardian East ODU | C1_0303AL_PH4 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/Battery cabinet A/C isn't working and its control board need check.
IM766186 | 0303AL | 0451_N_WARDIAN-EST_0303AL | High Temperature Problem / Problem Solved after solving A/Cs Problem and reset BTS | Faulty System | A/Cs | A/Cs | 355916 | N_WARDIAN-EST_0303AL | C1_0303AL_PH4 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/A/C1 isn't working and its CB tripped off.
IM766210 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG stoppage / weak batteries / cleared after power restored | Faulty System | batt | Batteries | 356434 | 01_G_SS-RAMADA-SEDR_0371SI | C4_0371SI_PH09 | Batteries | Some parts are (missing / stolen)/Battery string stolen
IM766210 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 356434 | 01_G_SS-RAMADA-SEDR_0371SI | C4_0371SI_PH09 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage
IM766210 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 356434 | 01_G_SS-RAMADA-SEDR_0371SI | C4_0371SI_PH09 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage
IM766210 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 356434 | 01_G_SS-RAMADA-SEDR_0371SI | C4_0371SI_PH09 | ATS / Engine | Components faulty/Generator battery defected
IM766210 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure
IM766210 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Wrong connection/generator battery as used in the site and not suitable in High temp
IM766211 | 0223UP | 0261_C_SG-DIER-NAYASSA_0223UP | Due to Generator problem due to LOP alarm, weak batteries , Recovered | Faulty System | Gen | Generator | 324451 | 01_G_SG-DIER-NAYASSA_0223UP | C1_0223UP_PH5 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Battery cables to be isolated well
IM766211 | 0223UP | 0261_C_SG-DIER-NAYASSA_0223UP | Due to Generator problem due to LOP alarm, weak batteries , Recovered | Faulty System | generator | Generator | 324451 | 01_G_SG-DIER-NAYASSA_0223UP | C1_0223UP_PH5 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Battery cables to be isolated well
IM766211 | 0223UP | 0261_C_SG-DIER-NAYASSA_0223UP | Due to Generator problem due to LOP alarm, weak batteries , Recovered | Faulty System | Gen | Generator | 324451 | 01_G_SG-DIER-NAYASSA_0223UP | C1_0223UP_PH5 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/ATS cables notorgnized and unused cable not isolated
IM766211 | 0223UP | 0261_C_SG-DIER-NAYASSA_0223UP | Due to Generator problem due to LOP alarm, weak batteries , Recovered | Faulty System | generator | Generator | 324451 | 01_G_SG-DIER-NAYASSA_0223UP | C1_0223UP_PH5 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/ATS cables notorgnized and unused cable not isolated
IM766211 | 0223UP | 0261_C_SG-DIER-NAYASSA_0223UP | Due to Generator problem due to LOP alarm, weak batteries , Recovered | Faulty System | Gen | Generator | 324451 | 01_G_SG-DIER-NAYASSA_0223UP | C1_0223UP_PH5 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Missing terminals inside ATS
IM766211 | 0223UP | 0261_C_SG-DIER-NAYASSA_0223UP | Due to Generator problem due to LOP alarm, weak batteries , Recovered | Faulty System | generator | Generator | 324451 | 01_G_SG-DIER-NAYASSA_0223UP | C1_0223UP_PH5 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Missing terminals inside ATS
IM766211 | 0223UP | 0261_C_SG-DIER-NAYASSA_0223UP | Due to Generator problem due to LOP alarm, weak batteries , Recovered | Faulty System | Gen | Generator | 324451 | 01_G_SG-DIER-NAYASSA_0223UP | C1_0223UP_PH5 | ATS / Engine | Item(s) stolen/Gen battery is missing
IM766211 | 0223UP | 0261_C_SG-DIER-NAYASSA_0223UP | Due to Generator problem due to LOP alarm, weak batteries , Recovered | Faulty System | generator | Generator | 324451 | 01_G_SG-DIER-NAYASSA_0223UP | C1_0223UP_PH5 | ATS / Engine | Item(s) stolen/Gen battery is missing
IM766211 | 0223UP | 0261_C_SG-DIER-NAYASSA_0223UP | Due to Generator problem due to LOP alarm, weak batteries , Recovered | Faulty System | Gen | Generator | 324451 | 01_G_SG-DIER-NAYASSA_0223UP | C1_0223UP_PH5 | ATS / Engine | Panorama pictures for each system/Panorama
IM766211 | 0223UP | 0261_C_SG-DIER-NAYASSA_0223UP | Due to Generator problem due to LOP alarm, weak batteries , Recovered | Faulty System | generator | Generator | 324451 | 01_G_SG-DIER-NAYASSA_0223UP | C1_0223UP_PH5 | ATS / Engine | Panorama pictures for each system/Panorama
IM766212 | 3778UP | 1291_S_AS-SABIL_3778UP_X | Main power disconnection and SCG isn't worked, Stolen batteries ,SCG did not work due to Fueling Problem , P.G connected | Faulty System | batt | Batteries | 356225 | 01_S_AS-SABIL_3778UP | C1_3778UP_PH15 | Batteries | Some parts are (missing / stolen)/Batteries were stolen
IM766228 | 3514DE | 1901_S_DK-KFR-GHENINA_3514DE | Main power @ DK-KFR-GHENINA_3514DE / weak batteries | Faulty System | batt | Batteries | 324923 | DK-KFR-GHENINA | C3_3514DE_PH13 | Batteries | Item(s) stolen/stolen Batteries
IM766229 | 3514DE | 1901_S_DK-KFR-GHENINA_3514DE | Main power @ DK-KFR-GHENINA_3514DE / weak batteries | Faulty System | batt | Batteries | 324923 | DK-KFR-GHENINA | C3_3514DE_PH13 | Batteries | Item(s) stolen/stolen Batteries
IM766241 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem and access VF problem & stolen batt. (I) | Faulty System | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | Batteries | Some parts are (missing / stolen)/missing battereis
IM766253 | 3455UP | 0921_S_QN-ELNUGOU_3455UP | Main power disconnection ,batteries are suspected to be weak , P.G connected | Faulty System | batt | Batteries | 355996 | 01_S_QN-ELNUGOU_3455UP | C1_3455UP_PH14 | Rectifiers | Alarms reporting to the OMC/Alarm was exists on rectifier control panel and appeared on the Omc to be cleared
IM766253 | 3455UP | 0921_S_QN-ELNUGOU_3455UP | Main power disconnection ,batteries are suspected to be weak , P.G connected | Faulty System | batt | Batteries | 355996 | 01_S_QN-ELNUGOU_3455UP | C1_3455UP_PH14 | Batteries | Some parts are (missing / stolen)/Missing batteries poles covers
IM766256 | 3812UP | 0631_E_SG-MNSHAH2_3812UP | Main power disconnection ,batteries are suspected to be weak, Autorecovered. | Faulty System | batt | Batteries | 355794 | 01_G_QN-MHAMID-QBLY_3807UP | C1_3807UP_PH15 | Rectifiers | Alarms reporting to the OMC/Rectifier minor alarm was looped at ddf
IM766270 | 3712DE | 0221_G_BH-QAMHA_3712DE | Main power problem @ BH-QAMHA_3712DE / SC GN problem | Faulty System | GN | Generator | 304258 | BH-QAMHA | C1_3712DE_PH14 | ATS / Engine | Components faulty/Small generator not working // Site has history generator status alarm
IM766273 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN problem/stolen battery@Mit Gaber/clear after GN working | Faulty System | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | ATS / Engine | Wrong connection/Welding cables
IM766273 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN problem/stolen battery@Mit Gaber/clear after GN working | Faulty System | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot
IM766281 | 3245CA | 01973_S_3245CA_10th-RSD-6 | EC power outage / weak batteries / cleared after power restored | Faulty System | batt | Batteries | 356443 | 10TH-RSD-6 | C4_3245CA_PH11 | Batteries | Some parts are (missing / stolen)/Battery string stolen
IM766330 | 4251DE | 03304_S_4251DE_QL-ABU-GHIT2 | main power/stolen batteries /clear after power back | Faulty System | batt | Batteries | 355722 | QL-ABU-GHIT2 | C1_4251DE_PH17 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM766373 | 3895DE | 0401_S_BH-KFR-ZYADA_3895DE | Share VF / VF GN problem / stolen batteries / then BTS problem / SM problem faulty / RP3 alarm | Faulty System | batt | Batteries | 324442 | BH-KFR-ZYADA | C1_3895DE_PH14 | Batteries | Item(s) stolen/There is no battery for site
IM766394 | 3319CA | 01131_S_3319CA_IMBABA-4 | down due to power failure and dead batteries (M) | Faulty System | batt | Batteries | 355486 | IMBABA-4 | C2_3319CA_PH12 | Rectifiers | Alarms reporting to the OMC/Rectifier alarms don't appear on the OMC
IM766394 | 3319CA | 01131_S_3319CA_IMBABA-4 | down due to power failure and dead batteries (M) | Faulty System | batt | Batteries | 355486 | IMBABA-4 | C2_3319CA_PH12 | Rectifiers | Alarms reporting to the OMC/Rectifier alarms don't appear on the OMC (battery fuse alarm)
IM766404 | 3489DE | 0461_S_DK-KFR-GHANNAM_3489DE | main power/stolen batteries /clear after power back | Faulty System | batt | Batteries | 325088 | DK-KFR-GHANNAM | C1-3489DE-PH13 | Batteries | Item(s) stolen/No backup batteries.
IM766406 | 0370UP | 1961_G_CAIRO-ASWAN-12_0370UP | Main power disconnection , stolen batteries , recovered | Faulty System | batt | Batteries | 304136 | 01_G_CAIRO-ASWAN-12_0370UP | C2_0370UP_PH8 | Batteries | Item(s) stolen/ Batteries were stolen
IM766425 | 0801DE | 0351_G_DK-BARHANTOSH_0801DE | main power/Stolen batteries @BARHANTOSH_0801DE/clear on P.G,cant carry full loads | Faulty System | batt | Batteries | 355760 | 01_G_IS-SALHIYA-RD_0433DE | C3_0433DE_PH4 | Rectifiers | Alarms reporting to the OMC/Site has old power alarm
IM766425 | 0801DE | 0351_G_DK-BARHANTOSH_0801DE | main power/Stolen batteries @BARHANTOSH_0801DE/clear on P.G,cant carry full loads | Faulty System | batt | Batteries | 355760 | 01_G_IS-SALHIYA-RD_0433DE | C3_0433DE_PH4 | Batteries | Some parts are (missing / stolen)/Battery string stolen
IM766425 | 0801DE | 0351_G_DK-BARHANTOSH_0801DE | main power/Stolen batteries @BARHANTOSH_0801DE/clear on P.G,cant carry full loads | Faulty System | batt | Batteries | 325114 | DK-BARHANTOSH | C1_0801DE_PH9 | Batteries | Item(s) stolen/No backup batteries.
IM766433 | 3090UP | 2131_S_SG-FAZARA_3090UP | Due to H.T alarm , recovered | Faulty System | H.T | A/Cs | 356038 | 01_S_SG-FAZARA_3090UP | C2_3090UP_PH13 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/2 A/c's not functioning
IM766434 | 3759UP | 0951_S_AT-AWLD-IBRHIM_3759UP | Commercial power cut off and site has weak backup batteries, recovered | Faulty System | backup | Batteries | 356232 | 01_S_AT-AWLD-IBRHIM_3759UP | C1_3759UP_PH15 | Batteries | Some parts are (missing / stolen)/site batteries were stolen
IM766434 | 3759UP | 0951_S_AT-AWLD-IBRHIM_3759UP | Commercial power cut off and site has weak backup batteries, recovered | Faulty System | batt | Batteries | 356232 | 01_S_AT-AWLD-IBRHIM_3759UP | C1_3759UP_PH15 | Batteries | Some parts are (missing / stolen)/site batteries were stolen
IM766460 | 3290DE | 1171_D_MF-QATTA_3290DE | GN problem/batteries under investigation/clear on P.G | Faulty System | GN | Generator | 355961 | MF-QATTA | C3_3290DE_PH12 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has leakage
IM766460 | 3290DE | 1171_D_MF-QATTA_3290DE | GN problem/batteries under investigation/clear on P.G | Faulty System | GN | Generator | 355961 | MF-QATTA | C3_3290DE_PH12 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals requried
IM766460 | 3290DE | 1171_D_MF-QATTA_3290DE | GN problem/batteries under investigation/clear on P.G | Faulty System | GN | Generator | 355961 | MF-QATTA | C3_3290DE_PH12 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Cable need to be terminated well
IM766462 | 0595DE | 0281_G_DK-NISHA_0595DE | Main power / weak batteries | Faulty System | batt | Batteries | 324924 | DK-NISHAA | C1_0595DE_PH9 | Batteries | Some parts are missing/cover
IM766467 | 3953DE | 0361_G_BH-MAARKA_3953DE | informed TT only @14:32//access ET/Main power/Stolen batteries | Faulty System | batt | Batteries | 304235 | BH-MAARKA | C1_3953DE_PH15 | Batteries | Components faulty/Faulty battery and cable disconnected
IM766487 | 3318UP | 01_S_SG-TAL-ELZOKI_3318UP | Commercial power cut off and site has stolen backup batteries | Faulty System | backup | Batteries | 324453 | 01_S_SG-TAL-ELZOKI_3318UP | C3_3318UP_PH14 | Batteries | Item(s) stolen/site batteries were stolen
IM766487 | 3318UP | 01_S_SG-TAL-ELZOKI_3318UP | Commercial power cut off and site has stolen backup batteries | Faulty System | batt | Batteries | 324453 | 01_S_SG-TAL-ELZOKI_3318UP | C3_3318UP_PH14 | Batteries | Item(s) stolen/site batteries were stolen
IM766487 | 3318UP | 01_S_SG-TAL-ELZOKI_3318UP | Commercial power cut off and site has stolen backup batteries | Faulty System | backup | Batteries | 356366 | 01_O_SG-RYAYNA-HAGR_3744UP | C1_3744UP_PH16 | Batteries | Some parts are (missing / stolen)/Site batteries were Stolen
IM766487 | 3318UP | 01_S_SG-TAL-ELZOKI_3318UP | Commercial power cut off and site has stolen backup batteries | Faulty System | batt | Batteries | 356366 | 01_O_SG-RYAYNA-HAGR_3744UP | C1_3744UP_PH16 | Batteries | Some parts are (missing / stolen)/Site batteries were Stolen
IM766502 | 0962CA | 02148_S_0962CA_OM-BAYOMI-STH | down due to main power & weak batteries | Faulty System | batt | Batteries | 345370 | OM-BAYOMI-STH | C1_0962CA_PH9 | Rectifiers | Alarms reporting to the OMC/Minor (high battery temp.) and major (faulty modules) alarms appear on the rectifier
IM766502 | 0962CA | 02148_S_0962CA_OM-BAYOMI-STH | down due to main power & weak batteries | Faulty System | batt | Batteries | 345370 | OM-BAYOMI-STH | C1_0962CA_PH9 | Batteries | Some parts are (missing / stolen)/Stolen batteries
IM766543 | 0882DE | 1091_D_GH-MHLA-BHR-ST_0882DE | GN problem @ GH-MHLA-BHR-ST_0882DE / batteries under check / connect PG / lock 2G | Faulty System | GN | Generator | 324934 | GH-MHLA-BHR-ST | C6_0882DE_PH09 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check, clean
IM766585 | 0517DE | 1541_G_QL-TUKH-TRAIN_0517DE | Main power/week battery/clear after power back | Faulty System | batt | Batteries | 303890 | QL-TUKH-TRAIN BSC | C1_0517DE_PH8 | Batteries | Item(s) stolen/stolen batteries
IM766608 | 0801DE | 0351_G_DK-BARHANTOSH_0801DE | Main power/stolen battery @ DK-BARHANTOSH/clear on P.G,can't carry full loads | Faulty System | batt | Batteries | 325114 | DK-BARHANTOSH | C1_0801DE_PH9 | Batteries | Item(s) stolen/No backup batteries.
IM766651 | 3438DE | 0411_S_DK-ABU-HUSEIN_3438DE | main power/Stolen batteries clear after power back | Faulty System | batt | Batteries | 325116 | DK-ABU-HUSEIN | C2-3438DE-PH13 | Batteries | Item(s) stolen/No backup batteries.
IM766676 | 3866DE | 2001_D_DK-SANBAKHT_3866DE | GN problem / stolen batteries | Faulty System | GN | Generator | 304185 | DK-SANBAKHT | C3_3866DE_PH14 | ATS / Engine | Components faulty/screen need repair
IM766676 | 3866DE | 2001_D_DK-SANBAKHT_3866DE | GN problem / stolen batteries | Faulty System | GN | Generator | 304185 | DK-SANBAKHT | C3_3866DE_PH14 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/protect by tray
IM766676 | 3866DE | 2001_D_DK-SANBAKHT_3866DE | GN problem / stolen batteries | Faulty System | GN | Generator | 304185 | DK-SANBAKHT | C3_3866DE_PH14 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/protect
IM766676 | 3866DE | 2001_D_DK-SANBAKHT_3866DE | GN problem / stolen batteries | Faulty System | GN | Generator | 304185 | DK-SANBAKHT | C3_3866DE_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check oil leakage
IM766685 | 0608UP | 1071_D_MN-BANI-ROH_0608UP | Generator stopped due to radiator problem and site has weak backup batteries Site has guard access problem at night | Faulty System | Gen | Generator | 356181 | 01_G_MN-BANI-ROH_0608UP | C1_0608UP_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage
IM766685 | 0608UP | 1071_D_MN-BANI-ROH_0608UP | Generator stopped due to radiator problem and site has weak backup batteries Site has guard access problem at night | Faulty System | generator | Generator | 356181 | 01_G_MN-BANI-ROH_0608UP | C1_0608UP_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage
IM766685 | 0608UP | 1071_D_MN-BANI-ROH_0608UP | Generator stopped due to radiator problem and site has weak backup batteries Site has guard access problem at night | Faulty System | Gen | Generator | 356181 | 01_G_MN-BANI-ROH_0608UP | C1_0608UP_PH9 | ATS / Engine | Components faulty/faulty battery
IM766685 | 0608UP | 1071_D_MN-BANI-ROH_0608UP | Generator stopped due to radiator problem and site has weak backup batteries Site has guard access problem at night | Faulty System | generator | Generator | 356181 | 01_G_MN-BANI-ROH_0608UP | C1_0608UP_PH9 | ATS / Engine | Components faulty/faulty battery
IM766685 | 0608UP | 1071_D_MN-BANI-ROH_0608UP | Generator stopped due to radiator problem and site has weak backup batteries Site has guard access problem at night | Faulty System | Gen | Generator | 356181 | 01_G_MN-BANI-ROH_0608UP | C1_0608UP_PH9 | ATS / Engine | Components faulty/need battery
IM766685 | 0608UP | 1071_D_MN-BANI-ROH_0608UP | Generator stopped due to radiator problem and site has weak backup batteries Site has guard access problem at night | Faulty System | generator | Generator | 356181 | 01_G_MN-BANI-ROH_0608UP | C1_0608UP_PH9 | ATS / Engine | Components faulty/need battery
IM766685 | 0608UP | 1071_D_MN-BANI-ROH_0608UP | Generator stopped due to radiator problem and site has weak backup batteries Site has guard access problem at night | Faulty System | Gen | Generator | 356181 | 01_G_MN-BANI-ROH_0608UP | C1_0608UP_PH9 | ATS / Engine | Wrong connection/remove wrong connection
IM766685 | 0608UP | 1071_D_MN-BANI-ROH_0608UP | Generator stopped due to radiator problem and site has weak backup batteries Site has guard access problem at night | Faulty System | generator | Generator | 356181 | 01_G_MN-BANI-ROH_0608UP | C1_0608UP_PH9 | ATS / Engine | Wrong connection/remove wrong connection
IM766699 | 0180AL | 1081_S_WARDIAN_0180AL | Site Down After HT Alarm / No Access Refer To Soc Team / On Air After Solving HT Alarm | Faulty System | HT | A/Cs | 324862 | S_WARDIAN_0180AL | C1_0180AL_PH3 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/a/C1 has faulty IDU and isn't working.
IM766765 | 0638UP | 0491_G_QN-MOSALA_0638UP | Rented generator problem , Stolen batteries ; recovered after solving the generator problem | Faulty System | batt | Batteries | 324745 | 01_G_QN-MOSALA_0638UP | C4_0638UP_PH9 | Batteries | Item(s) stolen/Batteries were stolen
IM766765 | 0638UP | 0491_G_QN-MOSALA_0638UP | Rented generator problem , Stolen batteries ; recovered after solving the generator problem | Faulty System | Gen | Generator | 324745 | 01_G_QN-MOSALA_0638UP | C4_0638UP_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage beside enclosure by Vodafone
IM766765 | 0638UP | 0491_G_QN-MOSALA_0638UP | Rented generator problem , Stolen batteries ; recovered after solving the generator problem | Faulty System | generator | Generator | 324745 | 01_G_QN-MOSALA_0638UP | C4_0638UP_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage beside enclosure by Vodafone
IM766848 | 3495DE | 0181_S_SK-MAHDIYA_3495DE | Main power/ stolen battery/connect PG | Faulty System | batt | Batteries | 304144 | SK-MAHDIYA | C3_3495DE_PH13 | Batteries | Item(s) stolen/No backup batteries.
IM766863 | 3151UP | 1561_S_BS-QIMAN-AROS_3151UP | Commercial power cut off and site has weak backup batteries, PG connected | Faulty System | backup | Batteries | 355911 | 01_S_BS-QIMAN-AROS_3151UP | C2_3151UP_PH13 | Rectifiers | Alarms reporting to the OMC/Loop on the minor alarm in DDF (Port 6)
IM766863 | 3151UP | 1561_S_BS-QIMAN-AROS_3151UP | Commercial power cut off and site has weak backup batteries, PG connected | Faulty System | batt | Batteries | 355911 | 01_S_BS-QIMAN-AROS_3151UP | C2_3151UP_PH13 | Rectifiers | Alarms reporting to the OMC/Loop on the minor alarm in DDF (Port 6)
IM766863 | 3151UP | 1561_S_BS-QIMAN-AROS_3151UP | Commercial power cut off and site has weak backup batteries, PG connected | Faulty System | backup | Batteries | 355911 | 01_S_BS-QIMAN-AROS_3151UP | C2_3151UP_PH13 | Rectifiers | Alarms reporting to the OMC/The power alarm is faulty (Always active on the rectifier and OMC)
IM766863 | 3151UP | 1561_S_BS-QIMAN-AROS_3151UP | Commercial power cut off and site has weak backup batteries, PG connected | Faulty System | batt | Batteries | 355911 | 01_S_BS-QIMAN-AROS_3151UP | C2_3151UP_PH13 | Rectifiers | Alarms reporting to the OMC/The power alarm is faulty (Always active on the rectifier and OMC)
IM766908 | 3275DE | 1151_S_QL-DEER-2_3275DE | main power @DEER-2_3275DE /weak battery/connect PG | Faulty System | batt | Batteries | 356318 | QL-DEER-2 | C1_3275DE_PH12 | Rectifiers | Alarms reporting to the OMC/Alarm cable disconnected (Alarms not appear at OMC)
IM766908 | 3275DE | 1151_S_QL-DEER-2_3275DE | main power @DEER-2_3275DE /weak battery/connect PG | Faulty System | batt | Batteries | 356318 | QL-DEER-2 | C1_3275DE_PH12 | Batteries | Components faulty/Faulty battaries
IM766924 | 3126DE | 0121_S_DK-HAGYZEYA_3126DE | main power/stolen batt/connect PG, | Faulty System | batt | Batteries | 355992 | DK-HAGYZEYA | C6-3126DE-PH12 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM766925 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Main power / VF Share / Stolen batteries | Faulty System | batt | Batteries | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | Batteries | Item(s) stolen/Stolen
IM766941 | 3445UP | 591_D_MN-TOKH_3445UP | Generator stopped due to LOP alarm and site has weak backup batteries | Faulty System | Gen | Generator | 356182 | 01_G_MN-TOKH_3445UP | C1_3445UP_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage
IM766941 | 3445UP | 591_D_MN-TOKH_3445UP | Generator stopped due to LOP alarm and site has weak backup batteries | Faulty System | generator | Generator | 356182 | 01_G_MN-TOKH_3445UP | C1_3445UP_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage
IM766941 | 3445UP | 591_D_MN-TOKH_3445UP | Generator stopped due to LOP alarm and site has weak backup batteries | Faulty System | Gen | Generator | 356182 | 01_G_MN-TOKH_3445UP | C1_3445UP_PH14 | ATS / Engine | Components faulty/need battery
IM766941 | 3445UP | 591_D_MN-TOKH_3445UP | Generator stopped due to LOP alarm and site has weak backup batteries | Faulty System | generator | Generator | 356182 | 01_G_MN-TOKH_3445UP | C1_3445UP_PH14 | ATS / Engine | Components faulty/need battery
IM766944 | 3275DE | 1151_S_QL-DEER-2_3275DE | main power @DEER-2_3275DE /weak battery/connect PG | Faulty System | batt | Batteries | 356318 | QL-DEER-2 | C1_3275DE_PH12 | Rectifiers | Alarms reporting to the OMC/Alarm cable disconnected (Alarms not appear at OMC)
IM766944 | 3275DE | 1151_S_QL-DEER-2_3275DE | main power @DEER-2_3275DE /weak battery/connect PG | Faulty System | batt | Batteries | 356318 | QL-DEER-2 | C1_3275DE_PH12 | Batteries | Components faulty/Faulty battaries
IM766963 | 3385DE | 0671_S_BH-GHAZALA-VLG_3385DE | Main power / Batteries need check | Faulty System | batt | Batteries | 355780 | BH-GHAZALA-VLG | C2_3385DE_PH13 | Rectifiers | Alarms reporting to the OMC/Site down due to power (Check alarms with OMC)
IM766978 | 0280DE | 0601_Q_BH-KOMHMADA-NTH_0280DE | GN problem @ BH-KOMHMADA-NTH_0280DE / Stolen batteries | Faulty System | batt | Batteries | 355878 | BH-KOMHMDA-NTH | C6_0280DE_PH3 | Batteries | Some parts are (missing / stolen)/Stolen
IM766978 | 0280DE | 0601_Q_BH-KOMHMADA-NTH_0280DE | GN problem @ BH-KOMHMADA-NTH_0280DE / Stolen batteries | Faulty System | GN | Generator | 355878 | BH-KOMHMDA-NTH | C6_0280DE_PH3 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Leakage
IM766978 | 0280DE | 0601_Q_BH-KOMHMADA-NTH_0280DE | GN problem @ BH-KOMHMADA-NTH_0280DE / Stolen batteries | Faulty System | GN | Generator | 355878 | BH-KOMHMDA-NTH | C6_0280DE_PH3 | ATS / Engine | Unit earth/Disconnected
IM767038 | 3272UP | 0791_G_QN-QENWYA-BHRY_3272UP | Main power disconnection , Weak batteries , P.G Connected | Faulty System | batt | Batteries | 355823 | 01_G_QN-QENWYA-BHRY_3272UP | C2_3272UP_PH14 | Batteries | Some parts are (missing / stolen)/Some of Batteries were stolen
IM767058 | 0430AL | 00658_D_0430AL_TAMIR-EXIT | Generator problem/engine overhauling/Weak batteries/Connected PG/solved/Site restored | Faulty System | Gen | Generator | 356072 | Tamir Exit | C2_0430AL_PH9 | ATS / Engine | Unit earth/Disconnect generator earth.
IM767058 | 0430AL | 00658_D_0430AL_TAMIR-EXIT | Generator problem/engine overhauling/Weak batteries/Connected PG/solved/Site restored | Faulty System | generator | Generator | 356072 | Tamir Exit | C2_0430AL_PH9 | ATS / Engine | Unit earth/Disconnect generator earth.
IM767058 | 0430AL | 00658_D_0430AL_TAMIR-EXIT | Generator problem/engine overhauling/Weak batteries/Connected PG/solved/Site restored | Faulty System | Gen | Generator | 356072 | Tamir Exit | C2_0430AL_PH9 | ATS / Engine | Components faulty/GCM Module need replacement.
IM767058 | 0430AL | 00658_D_0430AL_TAMIR-EXIT | Generator problem/engine overhauling/Weak batteries/Connected PG/solved/Site restored | Faulty System | generator | Generator | 356072 | Tamir Exit | C2_0430AL_PH9 | ATS / Engine | Components faulty/GCM Module need replacement.
IM767058 | 0430AL | 00658_D_0430AL_TAMIR-EXIT | Generator problem/engine overhauling/Weak batteries/Connected PG/solved/Site restored | Faulty System | Gen | Generator | 356072 | Tamir Exit | C2_0430AL_PH9 | ATS / Engine | Wrong connection/Generator has bad condition and need overall.
IM767058 | 0430AL | 00658_D_0430AL_TAMIR-EXIT | Generator problem/engine overhauling/Weak batteries/Connected PG/solved/Site restored | Faulty System | generator | Generator | 356072 | Tamir Exit | C2_0430AL_PH9 | ATS / Engine | Wrong connection/Generator has bad condition and need overall.
IM767070 | 0983DE | 1771_S_DK-MIT-ANTAR_0983DE | Main power / Stolen batteries | Faulty System | batt | Batteries | 324896 | DK-MIT-ANTAR | C8_0983DE_PH11 | Batteries | Item(s) stolen/stolen batteries
IM767078 | 3046UP | 0551_D_AT-BANI-FEEZ_3046UP | Generator stopped due to radiator problem and site has stolen backup batteries | Faulty System | backup | Batteries | 303971 | 01_G_AT-BANI-FEEZ_3046UP | C4_3046UP_PH13 | Batteries | Item(s) stolen/Site batteries were stolen
IM767078 | 3046UP | 0551_D_AT-BANI-FEEZ_3046UP | Generator stopped due to radiator problem and site has stolen backup batteries | Faulty System | batt | Batteries | 303971 | 01_G_AT-BANI-FEEZ_3046UP | C4_3046UP_PH13 | Batteries | Item(s) stolen/Site batteries were stolen
IM767078 | 3046UP | 0551_D_AT-BANI-FEEZ_3046UP | Generator stopped due to radiator problem and site has stolen backup batteries | Faulty System | Gen | Generator | 303971 | 01_G_AT-BANI-FEEZ_3046UP | C4_3046UP_PH13 | ATS / Engine | Components faulty/Site need new battery
IM767078 | 3046UP | 0551_D_AT-BANI-FEEZ_3046UP | Generator stopped due to radiator problem and site has stolen backup batteries | Faulty System | generator | Generator | 303971 | 01_G_AT-BANI-FEEZ_3046UP | C4_3046UP_PH13 | ATS / Engine | Components faulty/Site need new battery
IM767078 | 3046UP | 0551_D_AT-BANI-FEEZ_3046UP | Generator stopped due to radiator problem and site has stolen backup batteries | Faulty System | Gen | Generator | 303971 | 01_G_AT-BANI-FEEZ_3046UP | C4_3046UP_PH13 | ATS / Engine | Components faulty/Control panel button not working
IM767078 | 3046UP | 0551_D_AT-BANI-FEEZ_3046UP | Generator stopped due to radiator problem and site has stolen backup batteries | Faulty System | generator | Generator | 303971 | 01_G_AT-BANI-FEEZ_3046UP | C4_3046UP_PH13 | ATS / Engine | Components faulty/Control panel button not working
IM767078 | 3046UP | 0551_D_AT-BANI-FEEZ_3046UP | Generator stopped due to radiator problem and site has stolen backup batteries | Faulty System | Gen | Generator | 303971 | 01_G_AT-BANI-FEEZ_3046UP | C4_3046UP_PH13 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Power cables not protected and missing power gland
IM767078 | 3046UP | 0551_D_AT-BANI-FEEZ_3046UP | Generator stopped due to radiator problem and site has stolen backup batteries | Faulty System | generator | Generator | 303971 | 01_G_AT-BANI-FEEZ_3046UP | C4_3046UP_PH13 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Power cables not protected and missing power gland
IM767078 | 3046UP | 0551_D_AT-BANI-FEEZ_3046UP | Generator stopped due to radiator problem and site has stolen backup batteries | Faulty System | Gen | Generator | 303971 | 01_G_AT-BANI-FEEZ_3046UP | C4_3046UP_PH13 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/Power cable not organized
IM767078 | 3046UP | 0551_D_AT-BANI-FEEZ_3046UP | Generator stopped due to radiator problem and site has stolen backup batteries | Faulty System | generator | Generator | 303971 | 01_G_AT-BANI-FEEZ_3046UP | C4_3046UP_PH13 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/Power cable not organized
IM767078 | 3046UP | 0551_D_AT-BANI-FEEZ_3046UP | Generator stopped due to radiator problem and site has stolen backup batteries | Faulty System | Gen | Generator | 303971 | 01_G_AT-BANI-FEEZ_3046UP | C4_3046UP_PH13 | ATS / Engine | Panorama pictures for each system/Panorama
IM767078 | 3046UP | 0551_D_AT-BANI-FEEZ_3046UP | Generator stopped due to radiator problem and site has stolen backup batteries | Faulty System | generator | Generator | 303971 | 01_G_AT-BANI-FEEZ_3046UP | C4_3046UP_PH13 | ATS / Engine | Panorama pictures for each system/Panorama
IM767152 | 3089UP | 2141_S_SG-GALAWEYA_3089UP | Main power disconnection , Stolen batteries , P.G Connected | Faulty System | batt | Batteries | 356371 | 01_S_SG-GALAWEYA_3089UP | C1_3089UP_PH13 | Batteries | Some parts are (missing / stolen)/site batteries were Stolen
IM767195 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN prob@SK-MIT-GABIR_3833DE/stolen battery/tGNerator work | Faulty System | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | ATS / Engine | Wrong connection/Welding cables
IM767195 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN prob@SK-MIT-GABIR_3833DE/stolen battery/tGNerator work | Faulty System | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot
IM767197 | 0390UP | D_DAR-FOUAD_4712_S6_G | site cascade on site DAR-FOUAD and DAR-FOUAD down H.T and solved after fix A/C (MA) | Faulty System | A/C | A/Cs | 356338 | DAR-FOUAD | C3_0390UP_PH8 | A/Cs Cooling / Free Cooling / Ventilation | Some parts are (missing / stolen)/cover
IM767197 | 0390UP | D_DAR-FOUAD_4712_S6_G | site cascade on site DAR-FOUAD and DAR-FOUAD down H.T and solved after fix A/C (MA) | Faulty System | H.T | A/Cs | 356338 | DAR-FOUAD | C3_0390UP_PH8 | A/Cs Cooling / Free Cooling / Ventilation | Some parts are (missing / stolen)/cover
IM767202 | 3245CA | 01973_S_3245CA_10th-RSD-6 | EC power outage /weak batteries / cleared after power restored | Faulty System | batt | Batteries | 356443 | 10TH-RSD-6 | C4_3245CA_PH11 | Batteries | Some parts are (missing / stolen)/Battery string stolen
IM767238 | 0022SI | 03519_H_0022SI_IS-ABU-ATWA | EC power outage /stolen batteries / cleared after power restored | Faulty System | batt | Batteries | 325082 | 01_H_IS-ABU-ATWA_0022SI | C8_0022SI_PH1 | Batteries | Item(s) stolen/Battery string stolen
IM767246 | 0711DE | 0701_S_GH-GOMHORIYAH_0711DE | Access TE / H.T alarm / BTS hanged | Faulty System | H.T | A/Cs | 335126 | GH-GOMHORIYAH | C2_0711DE_PH09 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/Faulty
IM767246 | 0711DE | 0701_S_GH-GOMHORIYAH_0711DE | Access TE / H.T alarm / BTS hanged | Faulty System | H.T | A/Cs | 335126 | GH-GOMHORIYAH | C2_0711DE_PH09 | A/Cs Cooling / Free Cooling / Ventilation | Wrong connection/terminals in one slot
IM767302 | 3894CA | 02231_S_3894CA_REHAB-STAGE7 | down due to VF DG problem and stolen batteries and access VF problem (M) | Faulty System | batt | Batteries | 356204 | REHAB-STAGE7 | C1_3894CA_PH17 | Batteries | Some parts are (missing / stolen)/missing batteries
IM767330 | 3495DE | 0181_S_SK-MAHDIYA_3495DE | VF/main power/stolen battery/ PG (has problem will solved) | Faulty System | batt | Batteries | 304144 | SK-MAHDIYA | C3_3495DE_PH13 | Batteries | Item(s) stolen/No backup batteries.
IM767367 | 3495DE | 0181_S_SK-MAHDIYA_3495DE | access VF/VF PM need charge /Main power/Stolen batteries/clear after power back | Faulty System | batt | Batteries | 304144 | SK-MAHDIYA | C3_3495DE_PH13 | Batteries | Item(s) stolen/No backup batteries.
IM767381 | 0222RE | 03824_G_0222RE_RS-FLAMNCO-HTL | Site was down due to Gen Stoppage / stolen batteries / fuel theft case / cleared after refueled | Faulty System | Gen | Generator | 355690 | 01_G_RS-FLAMNCO-HTL_0222RE | C1_0222RE_PH09 | ATS / Engine | Components faulty/need battery
IM767506 | 0028RE | 03477_N_0028RE_SZ-SUEZ8 | EC power outage / weak batteries / access PG problem / cleared after power restored | Faulty System | batt | Batteries | 345369 | 01_N_SZ-SUEZ8_0028RE | C2_0028RE_PH1 | Batteries | Some parts are (missing / stolen)/Stolen battery string
IM767594 | 3955DE | 0731_S_SK-QRMT-SAHBRA_3955DE | Main power/stolen battery/clear after power back | Faulty System | batt | Batteries | 356230 | SK-QRMT-SAHBRA | C1_3955DE_PH15 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM767647 | 3628DE | 0811_S_GH-QSR-BAGHDAD_3628DE | Main power / stolen batteries / PG connected | Faulty System | batt | Batteries | 324836 | GH-QSR-BAGHDAD | C2_3628DE_PH13 | Batteries | Item(s) stolen/Stolen batteries
IM767648 | 0498RE | 03500_S_0498RE_SZ-SELIM-HAY | EC power outage / weak batteries / access PG problem / VF owner / cleared after power restored | Faulty System | batt | Batteries | 345366 | 01_S_SZ-SELIM-HAY_0498RE | C1_0498RE_PH17 | Batteries | Some parts are (missing / stolen)/Stolen battery
IM767754 | 3361DE | 0441_S_KS-HAMUL-EST_3361DE | Share VF / Main power / stolen batteries | Faulty System | batt | Batteries | 355874 | KS-HAMUL-EST | C1_3361DE_PH12 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM767787 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Share VF / main power / stolen batteries | Faulty System | batt | Batteries | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | Batteries | Item(s) stolen/Stolen
IM767789 | 0050DE | 0001_S_GH-SHABSHR-HAS_0050DE | Main power @ GH-SHABSHR-HAS_0050DE / batteries under check | Faulty System | batt | Batteries | 304298 | GH-SHABSHR-HAS | C1_0050DE_PH1 | Batteries | Some parts are missing/cover
IM767793 | 3368DE | 0201_S_BH-ABO-SHIQAF_3368DE | Access VF / Main power / stolen batteries | Faulty System | batt | Batteries | 324904 | BH-ABO-SHIQAF | C1_3368DE_PH12 | Batteries | Item(s) stolen/There is no battery for site
IM767825 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN problem/stolen battery/clear after check GN | Faulty System | batt | Batteries | 324500 | SK-AZZAZI | C1_4029DE_PH15 | Batteries | Item(s) stolen/No backup batteries.
IM767825 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN problem/stolen battery/clear after check GN | Faulty System | GN | Generator | 324500 | SK-AZZAZI | C1_4029DE_PH15 | ATS / Engine | Wrong connection/Some cables are disconnected and need adjust.
IM767825 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN problem/stolen battery/clear after check GN | Faulty System | GN | Generator | 324500 | SK-AZZAZI | C1_4029DE_PH15 | ATS / Engine | Panorama pictures for each system/Generator battery poles need cleaning, wax and covers.
IM767825 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN problem/stolen battery/clear after check GN | Faulty System | GN | Generator | 324500 | SK-AZZAZI | C1_4029DE_PH15 | ATS / Engine | Panorama pictures for each system/Overview.
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | batt | Batteries | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | Rectifiers | Alarms reporting to the OMC/Alarm on the rectifer module
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | batt | Batteries | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | Batteries | Cables termination/lugs (AC side), lugs (DC side)/Loose in battery power cable
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | DG | Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Water leakage
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | Gen | Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Water leakage
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | DG | Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Genset Oil leakage
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | Gen | Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Genset Oil leakage
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | DG | Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Water leakage from the water pump
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | Gen | Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Water leakage from the water pump
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | DG | Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | ATS / Engine | Unit earth/Stolen earth cables
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | Gen | Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | ATS / Engine | Unit earth/Stolen earth cables
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | DG | Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | ATS / Engine | Components faulty/Defected genset battery
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | Gen | Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | ATS / Engine | Components faulty/Defected genset battery
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | DG | Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | ATS / Engine | Components faulty/Broken radiator fan plade
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | Gen | Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | ATS / Engine | Components faulty/Broken radiator fan plade
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | DG | Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | ATS / Engine | Wrong connection/Wrong connection , jumper on the genset main contactor
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | Gen | Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | ATS / Engine | Wrong connection/Wrong connection , jumper on the genset main contactor
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | DG | Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | ATS / Engine | Wrong connection/Genset welded cables
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | Gen | Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | ATS / Engine | Wrong connection/Genset welded cables
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | DG | Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Bad genset contactor terminals
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | Gen | Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Bad genset contactor terminals
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | DG | Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Unused genset ATS cables
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | Gen | Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Unused genset ATS cables
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | DG | Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Genset alarm cables , not fixed well , not terminated
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | Gen | Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Genset alarm cables , not fixed well , not terminated
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | DG | Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Charging system cables bad terminals
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | Faulty System | Gen | Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Charging system cables bad terminals
IM767864 | 0050DE | 0001_S_GH-SHABSHR-HAS_0050DE | Main power / batteries under check | Faulty System | batt | Batteries | 304298 | GH-SHABSHR-HAS | C1_0050DE_PH1 | Batteries | Some parts are missing/cover
IM767875 | 3037DE | 0301_D_DK-BAGALAT_3037DE | Share ET / GN problem / stolen batteries | Faulty System | batt | Batteries | 345376 | DK-BAGALAT | C3_3037DE_PH11 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM767875 | 3037DE | 0301_D_DK-BAGALAT_3037DE | Share ET / GN problem / stolen batteries | Faulty System | GN | Generator | 345376 | DK-BAGALAT | C3_3037DE_PH11 | ATS / Engine | Components faulty/Control module has faulty buttons.
IM767875 | 3037DE | 0301_D_DK-BAGALAT_3037DE | Share ET / GN problem / stolen batteries | Faulty System | GN | Generator | 345376 | DK-BAGALAT | C3_3037DE_PH11 | ATS / Engine | Wrong connection/Cable has bad connections and need replacement.
IM767952 | 3394DE | 0011_S_B-SAFT-KHALED_3394DE | Share VF / Main power / weak batteries | Faulty System | batt | Batteries | 304033 | BH-SAFT-KHALED | C1_3394DE_PH13 | Batteries | Components faulty/Faulty battery
IM767969 | 0435UP | 02_G_SG-GAZAZRA_0435UP | Main power disconnection , stolen batteries , recovered when EC power come back | Faulty System | batt | Batteries | 325007 | 01_G_SG-GAZAZRA_0435UP | C1_0435UP_PH9 | Batteries | Item(s) stolen/site batteries were stolen
IM767969 | 0435UP | 02_G_SG-GAZAZRA_0435UP | Main power disconnection , stolen batteries , recovered when EC power come back | Faulty System | batt | Batteries | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | Batteries | Item(s) stolen/Batteries were stolen
IM767989 | 3778UP | 1291_S_AS-SABIL_3778UP_X | Main power disconnection , Stolen batteries , P.G connected | Faulty System | batt | Batteries | 356225 | 01_S_AS-SABIL_3778UP | C1_3778UP_PH15 | Batteries | Some parts are (missing / stolen)/Batteries were stolen
IM768000 | 0096SI | 01_G_SS-MR-BLUE-BAY_0096SI | DG stoppage / weak batteries / Radiator problem / spare requested / cleared after power restored | Faulty System | DG | Generator | 356415 | 01_G_SS-MR-BLUE-BAY_0096SI | C1_0096SI_PH2 | ATS / Engine | Unit earth/Genset unit earth cable not connected to main earth bar
IM768000 | 0096SI | 01_G_SS-MR-BLUE-BAY_0096SI | DG stoppage / weak batteries / Radiator problem / spare requested / cleared after power restored | Faulty System | DG | Generator | 356415 | 01_G_SS-MR-BLUE-BAY_0096SI | C1_0096SI_PH2 | ATS / Engine | Components faulty/Defected genset battery
IM768000 | 0096SI | 01_G_SS-MR-BLUE-BAY_0096SI | DG stoppage / weak batteries / Radiator problem / spare requested / cleared after power restored | Faulty System | DG | Generator | 356415 | 01_G_SS-MR-BLUE-BAY_0096SI | C1_0096SI_PH2 | ATS / Engine | Wrong connection/Wrong connection of the main ATS contactor , the coil fed by line power cable from the same contactor main contact
IM768000 | 0096SI | 01_G_SS-MR-BLUE-BAY_0096SI | DG stoppage / weak batteries / Radiator problem / spare requested / cleared after power restored | Faulty System | DG | Generator | 356415 | 01_G_SS-MR-BLUE-BAY_0096SI | C1_0096SI_PH2 | ATS / Engine | Wrong connection/Welded cables
IM768000 | 0096SI | 01_G_SS-MR-BLUE-BAY_0096SI | DG stoppage / weak batteries / Radiator problem / spare requested / cleared after power restored | Faulty System | DG | Generator | 356415 | 01_G_SS-MR-BLUE-BAY_0096SI | C1_0096SI_PH2 | ATS / Engine | Wrong connection/Plastic bags used as isolation in the genset ATS panels
IM768000 | 0096SI | 01_G_SS-MR-BLUE-BAY_0096SI | DG stoppage / weak batteries / Radiator problem / spare requested / cleared after power restored | Faulty System | DG | Generator | 356415 | 01_G_SS-MR-BLUE-BAY_0096SI | C1_0096SI_PH2 | ATS / Engine | Wrong connection/•Charge & dynamo cables welded bad status
IM768000 | 0096SI | 01_G_SS-MR-BLUE-BAY_0096SI | DG stoppage / weak batteries / Radiator problem / spare requested / cleared after power restored | Faulty System | DG | Generator | 356415 | 01_G_SS-MR-BLUE-BAY_0096SI | C1_0096SI_PH2 | ATS / Engine | Wrong connection/Deep cycle battery used as genset starter
IM768000 | 0096SI | 01_G_SS-MR-BLUE-BAY_0096SI | DG stoppage / weak batteries / Radiator problem / spare requested / cleared after power restored | Faulty System | DG | Generator | 356415 | 01_G_SS-MR-BLUE-BAY_0096SI | C1_0096SI_PH2 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Bad cables terminals
IM768000 | 0096SI | 01_G_SS-MR-BLUE-BAY_0096SI | DG stoppage / weak batteries / Radiator problem / spare requested / cleared after power restored | Faulty System | DG | Generator | 356415 | 01_G_SS-MR-BLUE-BAY_0096SI | C1_0096SI_PH2 | ATS / Engine | Oil level & quality/Genset oil bad status
IM768000 | 0096SI | 01_G_SS-MR-BLUE-BAY_0096SI | DG stoppage / weak batteries / Radiator problem / spare requested / cleared after power restored | Faulty System | DG | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure
IM768000 | 0096SI | 01_G_SS-MR-BLUE-BAY_0096SI | DG stoppage / weak batteries / Radiator problem / spare requested / cleared after power restored | Faulty System | DG | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Wrong connection/generator battery as used in the site and not suitable in High temp
IM768037 | 3740DE | 0521_S_KS-MNSHT-ABS_3740DE | Access TE / Main power / Stolen batteries | Faulty System | batt | Batteries | 324805 | KS-MNSHT-ABS | C1_3740DE_Ph14 | Batteries | Item(s) stolen/There is no battery for site
IM768038 | 3821DE | 1481_S_SK-HAJAJIYAH_3821DE | vf gn /stolen battery/VF checked gn | Faulty System | batt | Batteries | 303842 | SK-HAJAJIYAH | C2-3821DE-PH14 | Batteries | Item(s) stolen/BTS covers need fixation.
IM768038 | 3821DE | 1481_S_SK-HAJAJIYAH_3821DE | vf gn /stolen battery/VF checked gn | Faulty System | batt | Batteries | 303842 | SK-HAJAJIYAH | C2-3821DE-PH14 | Batteries | Item(s) stolen/No backup batteries.
IM768076 | 3712DE | 0221_G_BH-QAMHA_3712DE | Main power problem @ BH-QAMHA_3712DE / SC GN in continous mode / BDT @ 07/01/2019 Is: 3.00 | Faulty System | GN | Generator | 304258 | BH-QAMHA | C1_3712DE_PH14 | ATS / Engine | Components faulty/Small generator not working // Site has history generator status alarm
IM768128 | 3821DE | 1481_S_SK-HAJAJIYAH_3821DE | VF GEN PROB/stolen battery/connect PG | Faulty System | batt | Batteries | 303842 | SK-HAJAJIYAH | C2-3821DE-PH14 | Batteries | Item(s) stolen/BTS covers need fixation.
IM768128 | 3821DE | 1481_S_SK-HAJAJIYAH_3821DE | VF GEN PROB/stolen battery/connect PG | Faulty System | batt | Batteries | 303842 | SK-HAJAJIYAH | C2-3821DE-PH14 | Batteries | Item(s) stolen/No backup batteries.
IM768134 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to DG Oil sensor problem and weak batteries(M) | Faulty System | DG | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | ATS / Engine | Wrong connection/wrong connections
IM768134 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to DG Oil sensor problem and weak batteries(M) | Faulty System | DG | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/floating hoses
IM768134 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to DG Oil sensor problem and weak batteries(M) | Faulty System | DG | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/unprotected cable
IM768134 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to DG Oil sensor problem and weak batteries(M) | Faulty System | DG | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage
IM768137 | 3178UP | 01_D_AT-BAQUR_3178UP | Generator stopped due to fuel shortage and site has weak backup batteries | Faulty System | backup | Batteries | 324555 | 01_G_AT-BAQUR_3178UP | C2_3178UP_PH13 | Batteries | Components faulty/site batteries were defected and to be changed
IM768137 | 3178UP | 01_D_AT-BAQUR_3178UP | Generator stopped due to fuel shortage and site has weak backup batteries | Faulty System | batt | Batteries | 324555 | 01_G_AT-BAQUR_3178UP | C2_3178UP_PH13 | Batteries | Components faulty/site batteries were defected and to be changed
IM768137 | 3178UP | 01_D_AT-BAQUR_3178UP | Generator stopped due to fuel shortage and site has weak backup batteries | Faulty System | Gen | Generator | 324555 | 01_G_AT-BAQUR_3178UP | C2_3178UP_PH13 | ATS / Engine | Components faulty/Gen missing battery
IM768137 | 3178UP | 01_D_AT-BAQUR_3178UP | Generator stopped due to fuel shortage and site has weak backup batteries | Faulty System | generator | Generator | 324555 | 01_G_AT-BAQUR_3178UP | C2_3178UP_PH13 | ATS / Engine | Components faulty/Gen missing battery
IM768137 | 3178UP | 01_D_AT-BAQUR_3178UP | Generator stopped due to fuel shortage and site has weak backup batteries | Faulty System | Gen | Generator | 324555 | 01_G_AT-BAQUR_3178UP | C2_3178UP_PH13 | ATS / Engine | Wrong connection/Bad isolation for batteries cables
IM768137 | 3178UP | 01_D_AT-BAQUR_3178UP | Generator stopped due to fuel shortage and site has weak backup batteries | Faulty System | generator | Generator | 324555 | 01_G_AT-BAQUR_3178UP | C2_3178UP_PH13 | ATS / Engine | Wrong connection/Bad isolation for batteries cables
IM768185 | 3532DE | 0511_S_SK-NATORA_3532DE | VDF GEN problem/stolen battery/gen work | Faulty System | batt | Batteries | 356262 | SK-NATORA | C2_3532DE_PH13 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM768221 | 3953DE | 0361_G_BH-MAARKA_3953DE | main power/weak battery/clear after power back | Faulty System | batt | Batteries | 304235 | BH-MAARKA | C1_3953DE_PH15 | Batteries | Components faulty/Faulty battery and cable disconnected
IM768279 | 0581DE | 1571_S_SK-IKYAD-BHARIA_0581DE | main power/stolen batteries @SK-IKYAD-BHARIA_0581DE/clear on P.G | Faulty System | batt | Batteries | 324498 | SK-IKYAD-BHARIA | C1_0581DE_PH9 | Batteries | Item(s) stolen/No backup batteries.
IM768288 | 4021DE | 0181_S_BH-ABQAEEN_4021DE | Access VF / Main power / stolen batteries | Faulty System | batt | Batteries | 304224 | BH-ABQAEEN | C1_4021DE_PH15 | Batteries | Item(s) stolen/There is no battery for site
IM768337 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN problem/Stolen batteries @SK-MIT-GABIR_3833DE/clear on P.G | Faulty System | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | ATS / Engine | Wrong connection/Welding cables
IM768337 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN problem/Stolen batteries @SK-MIT-GABIR_3833DE/clear on P.G | Faulty System | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot
IM768357 | 3828DE | 0961_S_BH-GWAD-HUSNI_3828DE | Main power /stolen batteries | Faulty System | batt | Batteries | 356184 | BH-GWAD-HUSNI | C1_3828DE_PH14 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM768377 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Share VF / Main power / stolen batteries | Faulty System | batt | Batteries | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | Batteries | Item(s) stolen/Stolen
IM768390 | 0735DE | 0711_G_GH-TANTA-HW2_0735DE | Main power @ GH-TANTA-HW2_0735DE / stolen batteries | Faulty System | batt | Batteries | 324537 | GH-TANTA-HW2 | C1_0735DE_PH9 | Batteries | Item(s) stolen/There is no battery for site
IM768394 | 3455UP | 0921_S_QN-ELNUGOU_3455UP | Main power disconnection ,batteries are suspected to be weak , P.G connected | Faulty System | batt | Batteries | 355996 | 01_S_QN-ELNUGOU_3455UP | C1_3455UP_PH14 | Rectifiers | Alarms reporting to the OMC/Alarm was exists on rectifier control panel and appeared on the Omc to be cleared
IM768394 | 3455UP | 0921_S_QN-ELNUGOU_3455UP | Main power disconnection ,batteries are suspected to be weak , P.G connected | Faulty System | batt | Batteries | 355996 | 01_S_QN-ELNUGOU_3455UP | C1_3455UP_PH14 | Batteries | Some parts are (missing / stolen)/Missing batteries poles covers
IM768395 | 3259DE | 0291_S_BH-ANAAM_3259DE | Share VF/ Main power / stolen batteries | Faulty System | batt | Batteries | 324534 | BH-ANAAM | C1_3259DE_PH12 | Batteries | Item(s) stolen/There is no battery for site
IM768401 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to commercial cut and no backup and access problem (MA) | Faulty System | backup | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | Batteries | Some parts are (missing / stolen)/missing battereis
IM768440 | 3484DE | 0231_S_SK-MIT-BASHAR_3484DE | main power/stolen battery/power back | Faulty System | batt | Batteries | 356055 | SK-MIT-BASHAR | C2-3484DE-PH13 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM768468 | 3394DE | 0011_S_B-SAFT-KHALED_3394DE | Share VF / Main power / weak batteries | Faulty System | batt | Batteries | 304033 | BH-SAFT-KHALED | C1_3394DE_PH13 | Batteries | Components faulty/Faulty battery
IM768489 | 0975UP | 0381_S_BS-MASID-ABYAD_0975UP_X | Commercial power cut off and site has stolen backup batteries, PG connected | Faulty System | backup | Batteries | 356360 | 01_S_BS-MASID-ABYAD_0975UP | C1_0975UP_PH12 | Rectifiers | Alarms reporting to the OMC/Minor alarm doesn't appear on the OMC
IM768489 | 0975UP | 0381_S_BS-MASID-ABYAD_0975UP_X | Commercial power cut off and site has stolen backup batteries, PG connected | Faulty System | batt | Batteries | 356360 | 01_S_BS-MASID-ABYAD_0975UP | C1_0975UP_PH12 | Rectifiers | Alarms reporting to the OMC/Minor alarm doesn't appear on the OMC
IM768489 | 0975UP | 0381_S_BS-MASID-ABYAD_0975UP_X | Commercial power cut off and site has stolen backup batteries, PG connected | Faulty System | backup | Batteries | 356360 | 01_S_BS-MASID-ABYAD_0975UP | C1_0975UP_PH12 | Batteries | Some parts are (missing / stolen)/Batteries and cables are stolen
IM768489 | 0975UP | 0381_S_BS-MASID-ABYAD_0975UP_X | Commercial power cut off and site has stolen backup batteries, PG connected | Faulty System | batt | Batteries | 356360 | 01_S_BS-MASID-ABYAD_0975UP | C1_0975UP_PH12 | Batteries | Some parts are (missing / stolen)/Batteries and cables are stolen
IM768491 | 3414UP | 0401_S_BS-AHWA_3414UP_X | Commercial power cut off and site has weak backup batteries, PG connected | Faulty System | backup | Batteries | 356350 | 01_S_BS-AHWA_3414UP | C1_3414UP_PH14 | Rectifiers | Alarms reporting to the OMC/Loop on the major alarm in DDF
IM768491 | 3414UP | 0401_S_BS-AHWA_3414UP_X | Commercial power cut off and site has weak backup batteries, PG connected | Faulty System | batt | Batteries | 356350 | 01_S_BS-AHWA_3414UP | C1_3414UP_PH14 | Rectifiers | Alarms reporting to the OMC/Loop on the major alarm in DDF
IM768491 | 3414UP | 0401_S_BS-AHWA_3414UP_X | Commercial power cut off and site has weak backup batteries, PG connected | Faulty System | backup | Batteries | 356350 | 01_S_BS-AHWA_3414UP | C1_3414UP_PH14 | Batteries | Components faulty/Batteries are faulty and site is down after less than one hour of power disconnected
IM768491 | 3414UP | 0401_S_BS-AHWA_3414UP_X | Commercial power cut off and site has weak backup batteries, PG connected | Faulty System | batt | Batteries | 356350 | 01_S_BS-AHWA_3414UP | C1_3414UP_PH14 | Batteries | Components faulty/Batteries are faulty and site is down after less than one hour of power disconnected
IM768527 | 0485SI | 01_S_SS-MOUSA-COAST_0485SI | EC power outage / weak batteries / cleared after power restored | Faulty System | batt | Batteries | 356428 | 01_S_SS-MOUSA-COAST_0485SI | C1_0485SI_PH13 | Batteries | Components faulty/All battery string exploded & not work
IM768547 | 3924CA | U_S_3924CA_NC-YASMIN7 | down due to DG filter problem and stolen batteries @ 3924CA_NC-YASMIN7 | Faulty System | DG | Generator | 356200 | NC-YASMIN7@U_S_3924CA_NC-YASMIN7 | 3924CA | ATS / Engine | Unit earth/missing earth
IM768569 | 3779DE | 1021_S_GH-BASTAWISY_3779DE | Share VF / Main power / Stolen batteries | Faulty System | batt | Batteries | 355870 | GH-BASTAWISY | C1_3779DE_PH14 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM768603 | 3837DE | 0441_D_SK-BAKARISH_3837DE | access Guard/GN problem/Stolen batteries/clear after check GN | Faulty System | batt | Batteries | 345278 | SK-BAKARISH | C1-3837DE-PH14 | Batteries | Some parts are (missing / stolen)/NO backup batteries.
IM768603 | 3837DE | 0441_D_SK-BAKARISH_3837DE | access Guard/GN problem/Stolen batteries/clear after check GN | Faulty System | GN | Generator | 345278 | SK-BAKARISH | C1-3837DE-PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Cables and neutral bolts need proper terminals.
IM768694 | 3072DE | 291_Q_GH-AMIRA-MHALA_3072DE | New GN swap / connect PG | Faulty System | GN | Generator | 324606 | Gh_Amria_Mahala | C1_3072DE_PH11 | ATS / Engine | Components faulty/DG Disconnected
IM768694 | 3072DE | 291_Q_GH-AMIRA-MHALA_3072DE | New GN swap / connect PG | Faulty System | GN | Generator | 324606 | Gh_Amria_Mahala | C1_3072DE_PH11 | ATS / Engine | Components faulty/Disconnected Cables
IM768694 | 3072DE | 291_Q_GH-AMIRA-MHALA_3072DE | New GN swap / connect PG | Faulty System | GN | Generator | 324606 | Gh_Amria_Mahala | C1_3072DE_PH11 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Fix and protect
IM768694 | 3072DE | 291_Q_GH-AMIRA-MHALA_3072DE | New GN swap / connect PG | Faulty System | GN | Generator | 324606 | Gh_Amria_Mahala | C1_3072DE_PH11 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Check leakage // hole
IM768694 | 3072DE | 291_Q_GH-AMIRA-MHALA_3072DE | New GN swap / connect PG | Faulty System | GN | Generator | 324606 | Gh_Amria_Mahala | C1_3072DE_PH11 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM768746 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN problem/Stolen batteries@MIT-GABIR_3833DE/clear after check GN | Faulty System | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | ATS / Engine | Wrong connection/Welding cables
IM768746 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN problem/Stolen batteries@MIT-GABIR_3833DE/clear after check GN | Faulty System | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot
IM768815 | 0407AL | G_ALEX-WST_48193_S2_S | Main power problem/Stolen batteries/Power backed/Autorecovered | Faulty System | batt | Batteries | 355458 | ALEX-WST ( Replacement) | C6_0407AL_PH09 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM768847 | 4016CA | 02557_V_4016CA_BAHTIM4 | down due to power failure and weak batteries and auto restored (M) | Faulty System | batt | Batteries | 355762 | BAHTIM4 | C1_4016CA_PH17 | Batteries | Some parts are (missing / stolen)/Two batteries are stolen
IM768857 | 3438DE | 0411_S_DK-ABU-HUSEIN_3438DE | one cell only/main power/stolen battery/clear on pg but it cannot carry all loads | Faulty System | batt | Batteries | 325116 | DK-ABU-HUSEIN | C2-3438DE-PH13 | Batteries | Item(s) stolen/No backup batteries.
IM768866 | 0581DE | 1571_S_SK-IKYAD-BHARIA_0581DE | main power/stolen batteries @SK-IKYAD-BHARIA_0581DE/clear on P.G | Faulty System | batt | Batteries | 324498 | SK-IKYAD-BHARIA | C1_0581DE_PH9 | Batteries | Item(s) stolen/No backup batteries.
IM768873 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Access VF " access blocked " / VF GN problem / Stolen batteries | Faulty System | batt | Batteries | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | Batteries | Item(s) stolen/Stolen
IM768873 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Access VF " access blocked " / VF GN problem / Stolen batteries | Faulty System | GN | Generator | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | ATS / Engine | Item(s) stolen/missing battery
IM768873 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Access VF " access blocked " / VF GN problem / Stolen batteries | Faulty System | GN | Generator | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM768874 | 3531DE | 1341_D_SK-MIT-EZZ_3531DE | GN. Problem / stolen batteries / clear after checking GN. | Faulty System | batt | Batteries | 303843 | SK-MIT-EZZ | C1-3531DE-PH13 | Batteries | Item(s) stolen/No backup batteries.
IM768874 | 3531DE | 1341_D_SK-MIT-EZZ_3531DE | GN. Problem / stolen batteries / clear after checking GN. | Faulty System | GN | Generator | 303843 | SK-MIT-EZZ | C1-3531DE-PH13 | ATS / Engine | Wrong connection/Generator need proper water feeding and radiator need check.
IM768883 | 3067DE | 1301_D_DK-GAMMALIAH2_3067DE | GN problem / batteries under check | Faulty System | GN | Generator | 304172 | DK-GAMMALIYAH2 | C5_3067DE_PH12 | ATS / Engine | Wrong connection/Generator has bad radiator feeding.
IM768883 | 3067DE | 1301_D_DK-GAMMALIAH2_3067DE | GN problem / batteries under check | Faulty System | GN | Generator | 304172 | DK-GAMMALIYAH2 | C5_3067DE_PH12 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Neutral cables need proper fixation with neutral bar.
IM768883 | 3067DE | 1301_D_DK-GAMMALIAH2_3067DE | GN problem / batteries under check | Faulty System | GN | Generator | 304172 | DK-GAMMALIYAH2 | C5_3067DE_PH12 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Hole need cover.
IM768919 | 3720DE | 0651_D_MF-SK-KARADIS_3720DE | GN problem/stolen battery @-SK-KARADIS/ | Faulty System | batt | Batteries | 355737 | MF-SK-KARADIS | C2-3720DE-PH14 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM768919 | 3720DE | 0651_D_MF-SK-KARADIS_3720DE | GN problem/stolen battery @-SK-KARADIS/ | Faulty System | GN | Generator | 355737 | MF-SK-KARADIS | C2-3720DE-PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Cables have bad connections, proper terminals and proper installtion are rerquired.
IM768945 | 0476DE | 0111_N_DK-BESHLA_0476DE | Main power/ battery under invistegation/clear after power back | Faulty System | batt | Batteries | 356100 | DK-BESHLA | C3_0476DE_PH7 | Batteries | Some parts are (missing / stolen)/no batteries
IM768950 | 0055RE | 01_G_RS-MR44-16_0055RE | DG Stoppage / cleared on PG till Gen problem solved | Faulty System | DG | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure
IM768950 | 0055RE | 01_G_RS-MR44-16_0055RE | DG Stoppage / cleared on PG till Gen problem solved | Faulty System | Gen | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure
IM768950 | 0055RE | 01_G_RS-MR44-16_0055RE | DG Stoppage / cleared on PG till Gen problem solved | Faulty System | DG | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Wrong connection/generator battery as used in the site and not suitable in High temp
IM768950 | 0055RE | 01_G_RS-MR44-16_0055RE | DG Stoppage / cleared on PG till Gen problem solved | Faulty System | Gen | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Wrong connection/generator battery as used in the site and not suitable in High temp
IM768982 | 0324UP | 1421_S_MN-BARTABAT_0324UP | Commercial power cut off and site has stolen backup batteries | Faulty System | backup | Batteries | 324919 | 01_S_MN-BARTABAT_0324UP | C1_0324UP_PH8 | Batteries | Item(s) stolen/Site batteries were stolen
IM768982 | 0324UP | 1421_S_MN-BARTABAT_0324UP | Commercial power cut off and site has stolen backup batteries | Faulty System | batt | Batteries | 324919 | 01_S_MN-BARTABAT_0324UP | C1_0324UP_PH8 | Batteries | Item(s) stolen/Site batteries were stolen
IM769011 | 0605DE | 0041_S_DK-MAHMUDIYYA_0605DE | Main power @ DK-MAHMUDIYYA_0605DE / Stolen batteries | Faulty System | batt | Batteries | 304053 | DK-MAHMUDIYYA | C2_0605DE_PH9 | Batteries | Item(s) stolen/No backup batteries.
IM769016 | 0015RE | 00223_C_0015RE_SUKHNA-RD7 | DG stoppage / stolen batteries / dynamo problem / cleared after Gen restored | Faulty System | batt | Batteries | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | Batteries | Some parts are (missing / stolen)/Battery string stolen
IM769016 | 0015RE | 00223_C_0015RE_SUKHNA-RD7 | DG stoppage / stolen batteries / dynamo problem / cleared after Gen restored | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage
IM769016 | 0015RE | 00223_C_0015RE_SUKHNA-RD7 | DG stoppage / stolen batteries / dynamo problem / cleared after Gen restored | Faulty System | Gen | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage
IM769016 | 0015RE | 00223_C_0015RE_SUKHNA-RD7 | DG stoppage / stolen batteries / dynamo problem / cleared after Gen restored | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Unit earth/Earth cable disconnected
IM769016 | 0015RE | 00223_C_0015RE_SUKHNA-RD7 | DG stoppage / stolen batteries / dynamo problem / cleared after Gen restored | Faulty System | Gen | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Unit earth/Earth cable disconnected
IM769016 | 0015RE | 00223_C_0015RE_SUKHNA-RD7 | DG stoppage / stolen batteries / dynamo problem / cleared after Gen restored | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Components faulty/Generator indicator broken & not work
IM769016 | 0015RE | 00223_C_0015RE_SUKHNA-RD7 | DG stoppage / stolen batteries / dynamo problem / cleared after Gen restored | Faulty System | Gen | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Components faulty/Generator indicator broken & not work
IM769016 | 0015RE | 00223_C_0015RE_SUKHNA-RD7 | DG stoppage / stolen batteries / dynamo problem / cleared after Gen restored | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Components faulty/Ventilation fan not work
IM769016 | 0015RE | 00223_C_0015RE_SUKHNA-RD7 | DG stoppage / stolen batteries / dynamo problem / cleared after Gen restored | Faulty System | Gen | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Components faulty/Ventilation fan not work
IM769016 | 0015RE | 00223_C_0015RE_SUKHNA-RD7 | DG stoppage / stolen batteries / dynamo problem / cleared after Gen restored | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Power cable has no terminal
IM769016 | 0015RE | 00223_C_0015RE_SUKHNA-RD7 | DG stoppage / stolen batteries / dynamo problem / cleared after Gen restored | Faulty System | Gen | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Power cable has no terminal
IM769036 | 0195RE | 03617_S_0195RE_RS-PRTO-COMPND | EC power outage / weak batteries / Access PG problem /cleared after power restored | Faulty System | batt | Batteries | 355604 | 01_S_RS-PRTO-COMPND_0195RE | C1_0195RE_PH9 | Batteries | Components faulty/change battery
IM769053 | 3598CA | 01968_S_3598CA_10TH-RSD-16 | EC power outage / weak batteries / cleared after power restored | Faulty System | batt | Batteries | 356447 | 10TH-RSD-16 | C1_3598CA_PH14 | Batteries | Some parts are (missing / stolen)/Missing battery pole cover
IM769096 | 3065AL | 03902_S_3065AL_MHWR-DABA-17 | Guard access problem / GN problem / stolen batteries / restored after solved Gn problem | Faulty System | GN | Generator | 324550 | MHWR-DABA-17 | C1_3065AL_PH20 | ATS / Engine | Wrong connection/Wrong connection (Joint cables)
IM769096 | 3065AL | 03902_S_3065AL_MHWR-DABA-17 | Guard access problem / GN problem / stolen batteries / restored after solved Gn problem | Faulty System | GN | Generator | 324550 | MHWR-DABA-17 | C1_3065AL_PH20 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/Cables needs organization
IM769123 | 3126DE | 0121_S_DK-HAGYZEYA_3126DE | Access ET. / Main Power / Stolen batteries / Clear on PG | Faulty System | batt | Batteries | 355992 | DK-HAGYZEYA | C6-3126DE-PH12 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM769137 | 3971DE | 0511_S_GH-ABU-GENDI_3971DE | ET Share / Main power / Stolen batteries | Faulty System | batt | Batteries | 324794 | GH-ABU-GENDI | C1_3971DE_PH15 | Batteries | Item(s) stolen/stolen batteries
IM769139 | 3344DE | 0681_S_BH-ELNEGILY_3344DE | VF Share / Main power / Stolen batteries | Faulty System | batt | Batteries | 304214 | BH-ELNEGILY | C3_3344DE_PH12 | Batteries | Item(s) stolen/There is no battery for site
IM769161 | 0329UP | 0791_S_MN-EBSHAK_0329UP | Commercial power cut off and site has weak backup batteries, PG connected | Faulty System | backup | Batteries | 325023 | 01_S_MN-EBSHAK_0329UP | C1_0329UP_PH8 | Batteries | Item(s) stolen/stolen Battery
IM769161 | 0329UP | 0791_S_MN-EBSHAK_0329UP | Commercial power cut off and site has weak backup batteries, PG connected | Faulty System | batt | Batteries | 325023 | 01_S_MN-EBSHAK_0329UP | C1_0329UP_PH8 | Batteries | Item(s) stolen/stolen Battery
IM769189 | 0080UP | L_E_AS-WST_0080UP | Swap Rectifier AP# 357553 | Faulty System | rect | Rectifier | 345348 | 01_S_AS-WST_0080UP | C3_0080UP_PH3 | DC Boxes | Unit earth/ddf earth cable is missing
IM769189 | 0080UP | L_E_AS-WST_0080UP | Swap Rectifier AP# 357553 | Faulty System | rect | Rectifier | 345348 | 01_S_AS-WST_0080UP | C3_0080UP_PH3 | DC Boxes | Unit earth/ddf earth cable is missing earth
IM769240 | 3394DE | 0011_S_B-SAFT-KHALED_3394DE | VF Share / Main power / Weak batteries | Faulty System | batt | Batteries | 304033 | BH-SAFT-KHALED | C1_3394DE_PH13 | Batteries | Components faulty/Faulty battery
IM769271 | 3776UP | 02_D_SG-HARJA-QARAN_3776UP | Generator problem , weak batteries , guard access problem ,recovered. | Faulty System | batt | Batteries | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | Rectifiers | Alarms reporting to the OMC/Rectifier minor alarm was looped at ddf
IM769271 | 3776UP | 02_D_SG-HARJA-QARAN_3776UP | Generator problem , weak batteries , guard access problem ,recovered. | Faulty System | batt | Batteries | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | Batteries | Components faulty/Batteries were faulty ( exploded )
IM769271 | 3776UP | 02_D_SG-HARJA-QARAN_3776UP | Generator problem , weak batteries , guard access problem ,recovered. | Faulty System | Gen | Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage from etisalat Gen
IM769271 | 3776UP | 02_D_SG-HARJA-QARAN_3776UP | Generator problem , weak batteries , guard access problem ,recovered. | Faulty System | generator | Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage from etisalat Gen
IM769271 | 3776UP | 02_D_SG-HARJA-QARAN_3776UP | Generator problem , weak batteries , guard access problem ,recovered. | Faulty System | Gen | Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | ATS / Engine | Unit earth/Gen enclosure earth cable is not connected
IM769271 | 3776UP | 02_D_SG-HARJA-QARAN_3776UP | Generator problem , weak batteries , guard access problem ,recovered. | Faulty System | generator | Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | ATS / Engine | Unit earth/Gen enclosure earth cable is not connected
IM769271 | 3776UP | 02_D_SG-HARJA-QARAN_3776UP | Generator problem , weak batteries , guard access problem ,recovered. | Faulty System | Gen | Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | ATS / Engine | Components faulty/ radiator is defected and connected with extranl water source
IM769271 | 3776UP | 02_D_SG-HARJA-QARAN_3776UP | Generator problem , weak batteries , guard access problem ,recovered. | Faulty System | generator | Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | ATS / Engine | Components faulty/ radiator is defected and connected with extranl water source
IM769271 | 3776UP | 02_D_SG-HARJA-QARAN_3776UP | Generator problem , weak batteries , guard access problem ,recovered. | Faulty System | Gen | Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | ATS / Engine | Components faulty/Gen battey is defected and need new one
IM769271 | 3776UP | 02_D_SG-HARJA-QARAN_3776UP | Generator problem , weak batteries , guard access problem ,recovered. | Faulty System | generator | Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | ATS / Engine | Components faulty/Gen battey is defected and need new one
IM769271 | 3776UP | 02_D_SG-HARJA-QARAN_3776UP | Generator problem , weak batteries , guard access problem ,recovered. | Faulty System | Gen | Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | ATS / Engine | Components faulty/ATS pressing keys and Knob were defected
IM769271 | 3776UP | 02_D_SG-HARJA-QARAN_3776UP | Generator problem , weak batteries , guard access problem ,recovered. | Faulty System | generator | Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | ATS / Engine | Components faulty/ATS pressing keys and Knob were defected
IM769271 | 3776UP | 02_D_SG-HARJA-QARAN_3776UP | Generator problem , weak batteries , guard access problem ,recovered. | Faulty System | Gen | Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | ATS / Engine | Wrong connection/Two cables inserted in one slot and not teminated can cause bad connections
IM769271 | 3776UP | 02_D_SG-HARJA-QARAN_3776UP | Generator problem , weak batteries , guard access problem ,recovered. | Faulty System | generator | Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | ATS / Engine | Wrong connection/Two cables inserted in one slot and not teminated can cause bad connections
IM769287 | 0015RE | 00223_C_0015RE_SUKHNA-RD7 | DG stoppage / stolen batteries / dynamo problem / cleared after power restored | Faulty System | batt | Batteries | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | Batteries | Some parts are (missing / stolen)/Battery string stolen
IM769287 | 0015RE | 00223_C_0015RE_SUKHNA-RD7 | DG stoppage / stolen batteries / dynamo problem / cleared after power restored | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage
IM769287 | 0015RE | 00223_C_0015RE_SUKHNA-RD7 | DG stoppage / stolen batteries / dynamo problem / cleared after power restored | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Unit earth/Earth cable disconnected
IM769287 | 0015RE | 00223_C_0015RE_SUKHNA-RD7 | DG stoppage / stolen batteries / dynamo problem / cleared after power restored | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Components faulty/Generator indicator broken & not work
IM769287 | 0015RE | 00223_C_0015RE_SUKHNA-RD7 | DG stoppage / stolen batteries / dynamo problem / cleared after power restored | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Components faulty/Ventilation fan not work
IM769287 | 0015RE | 00223_C_0015RE_SUKHNA-RD7 | DG stoppage / stolen batteries / dynamo problem / cleared after power restored | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Power cable has no terminal
IM769296 | 0013RE | 03428_Q_0013RE_SZ-HW33-9 | DG stoppage / weak batteries / Radiator problem / cleared after power restored | Faulty System | DG | Generator | 345446 | 01_W_SZ-HW33-9_0013RE | C1_0013RE_PH1 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Genest unclean & oil leakage
IM769296 | 0013RE | 03428_Q_0013RE_SZ-HW33-9 | DG stoppage / weak batteries / Radiator problem / cleared after power restored | Faulty System | DG | Generator | 345446 | 01_W_SZ-HW33-9_0013RE | C1_0013RE_PH1 | ATS / Engine | Unit earth/Loose in earth cable
IM769296 | 0013RE | 03428_Q_0013RE_SZ-HW33-9 | DG stoppage / weak batteries / Radiator problem / cleared after power restored | Faulty System | DG | Generator | 345446 | 01_W_SZ-HW33-9_0013RE | C1_0013RE_PH1 | ATS / Engine | Components faulty/Genset radiator low water level
IM769296 | 0013RE | 03428_Q_0013RE_SZ-HW33-9 | DG stoppage / weak batteries / Radiator problem / cleared after power restored | Faulty System | DG | Generator | 345446 | 01_W_SZ-HW33-9_0013RE | C1_0013RE_PH1 | ATS / Engine | Components faulty/Genset radiator low water level & missing green water
IM769296 | 0013RE | 03428_Q_0013RE_SZ-HW33-9 | DG stoppage / weak batteries / Radiator problem / cleared after power restored | Faulty System | DG | Generator | 345446 | 01_W_SZ-HW33-9_0013RE | C1_0013RE_PH1 | ATS / Engine | Components faulty/Hour meter gauage not work
IM769296 | 0013RE | 03428_Q_0013RE_SZ-HW33-9 | DG stoppage / weak batteries / Radiator problem / cleared after power restored | Faulty System | DG | Generator | 345446 | 01_W_SZ-HW33-9_0013RE | C1_0013RE_PH1 | ATS / Engine | Wrong connection/ATS welded cables & bad connection
IM769296 | 0013RE | 03428_Q_0013RE_SZ-HW33-9 | DG stoppage / weak batteries / Radiator problem / cleared after power restored | Faulty System | DG | Generator | 345446 | 01_W_SZ-HW33-9_0013RE | C1_0013RE_PH1 | ATS / Engine | Wrong connection/Non standard (From Orange ) DC/DC converter used & bad terminals
IM769296 | 0013RE | 03428_Q_0013RE_SZ-HW33-9 | DG stoppage / weak batteries / Radiator problem / cleared after power restored | Faulty System | DG | Generator | 345446 | 01_W_SZ-HW33-9_0013RE | C1_0013RE_PH1 | ATS / Engine | Wrong connection/Misisng fuel tank indoor light & power cable should be dismantled
IM769296 | 0013RE | 03428_Q_0013RE_SZ-HW33-9 | DG stoppage / weak batteries / Radiator problem / cleared after power restored | Faulty System | DG | Generator | 345446 | 01_W_SZ-HW33-9_0013RE | C1_0013RE_PH1 | ATS / Engine | Wrong connection/Stolen power from the site
IM769296 | 0013RE | 03428_Q_0013RE_SZ-HW33-9 | DG stoppage / weak batteries / Radiator problem / cleared after power restored | Faulty System | DG | Generator | 345446 | 01_W_SZ-HW33-9_0013RE | C1_0013RE_PH1 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Remain power cable
IM769316 | 0498RE | 03500_S_0498RE_SZ-SELIM-HAY | EC power outage / Sharing VF / weak batteries / access PG problem / cleared after power restored | Faulty System | batt | Batteries | 345366 | 01_S_SZ-SELIM-HAY_0498RE | C1_0498RE_PH17 | Batteries | Some parts are (missing / stolen)/Stolen battery
IM769334 | 0657CA | 01766_S_0657CA_BAGDAD-ST | down due to power failure and dead batteries | Faulty System | batt | Batteries | 345255 | BAGDAD-ST | C7_0657CA_PH8 | Batteries | Some parts are missing/missing batteries/ stolen
IM769381 | 3445UP | 591_D_MN-TOKH_3445UP | Generator stopped due to LOP alarm and site has weak backup batteries Site has guard access problem | Faulty System | Gen | Generator | 356182 | 01_G_MN-TOKH_3445UP | C1_3445UP_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage
IM769381 | 3445UP | 591_D_MN-TOKH_3445UP | Generator stopped due to LOP alarm and site has weak backup batteries Site has guard access problem | Faulty System | generator | Generator | 356182 | 01_G_MN-TOKH_3445UP | C1_3445UP_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage
IM769381 | 3445UP | 591_D_MN-TOKH_3445UP | Generator stopped due to LOP alarm and site has weak backup batteries Site has guard access problem | Faulty System | Gen | Generator | 356182 | 01_G_MN-TOKH_3445UP | C1_3445UP_PH14 | ATS / Engine | Components faulty/need battery
IM769381 | 3445UP | 591_D_MN-TOKH_3445UP | Generator stopped due to LOP alarm and site has weak backup batteries Site has guard access problem | Faulty System | generator | Generator | 356182 | 01_G_MN-TOKH_3445UP | C1_3445UP_PH14 | ATS / Engine | Components faulty/need battery
IM769390 | 0013RE | 03428_Q_0013RE_SZ-HW33-9 | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 345446 | 01_W_SZ-HW33-9_0013RE | C1_0013RE_PH1 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Genest unclean & oil leakage
IM769390 | 0013RE | 03428_Q_0013RE_SZ-HW33-9 | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 345446 | 01_W_SZ-HW33-9_0013RE | C1_0013RE_PH1 | ATS / Engine | Unit earth/Loose in earth cable
IM769390 | 0013RE | 03428_Q_0013RE_SZ-HW33-9 | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 345446 | 01_W_SZ-HW33-9_0013RE | C1_0013RE_PH1 | ATS / Engine | Components faulty/Genset radiator low water level
IM769390 | 0013RE | 03428_Q_0013RE_SZ-HW33-9 | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 345446 | 01_W_SZ-HW33-9_0013RE | C1_0013RE_PH1 | ATS / Engine | Components faulty/Genset radiator low water level & missing green water
IM769390 | 0013RE | 03428_Q_0013RE_SZ-HW33-9 | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 345446 | 01_W_SZ-HW33-9_0013RE | C1_0013RE_PH1 | ATS / Engine | Components faulty/Hour meter gauage not work
IM769390 | 0013RE | 03428_Q_0013RE_SZ-HW33-9 | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 345446 | 01_W_SZ-HW33-9_0013RE | C1_0013RE_PH1 | ATS / Engine | Wrong connection/ATS welded cables & bad connection
IM769390 | 0013RE | 03428_Q_0013RE_SZ-HW33-9 | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 345446 | 01_W_SZ-HW33-9_0013RE | C1_0013RE_PH1 | ATS / Engine | Wrong connection/Non standard (From Orange ) DC/DC converter used & bad terminals
IM769390 | 0013RE | 03428_Q_0013RE_SZ-HW33-9 | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 345446 | 01_W_SZ-HW33-9_0013RE | C1_0013RE_PH1 | ATS / Engine | Wrong connection/Misisng fuel tank indoor light & power cable should be dismantled
IM769390 | 0013RE | 03428_Q_0013RE_SZ-HW33-9 | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 345446 | 01_W_SZ-HW33-9_0013RE | C1_0013RE_PH1 | ATS / Engine | Wrong connection/Stolen power from the site
IM769390 | 0013RE | 03428_Q_0013RE_SZ-HW33-9 | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 345446 | 01_W_SZ-HW33-9_0013RE | C1_0013RE_PH1 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Remain power cable
IM769433 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem and stolen batteries and VF access problem . | Faulty System | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | Batteries | Some parts are (missing / stolen)/missing battereis
IM769459 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to generator problem (filter air) and stolen batteries | Faulty System | batt | Batteries | 314391 | REHAB-G17 | C1_3492CA_PH13 | Batteries | Some parts are missing/missing batteries
IM769459 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to generator problem (filter air) and stolen batteries | Faulty System | Gen | Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | ATS / Engine | Wrong connection/wrong connection
IM769459 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to generator problem (filter air) and stolen batteries | Faulty System | generator | Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | ATS / Engine | Wrong connection/wrong connection
IM769494 | 3185DE | 0171_D_MF-SANGALF_3185DE | GN Problem/ Stolen batteries / Clear after check GN | Faulty System | batt | Batteries | 345324 | MF-SANGALF | C2-3185DE-PH12 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM769500 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to generator problem air filter and stolen batteries | Faulty System | batt | Batteries | 314391 | REHAB-G17 | C1_3492CA_PH13 | Batteries | Some parts are missing/missing batteries
IM769500 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to generator problem air filter and stolen batteries | Faulty System | Gen | Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | ATS / Engine | Wrong connection/wrong connection
IM769500 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to generator problem air filter and stolen batteries | Faulty System | generator | Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | ATS / Engine | Wrong connection/wrong connection
IM769526 | 3290DE | 1171_D_MF-QATTA_3290DE | GEN failure/batteries under investigtion | Faulty System | Gen | Generator | 355961 | MF-QATTA | C3_3290DE_PH12 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has leakage
IM769526 | 3290DE | 1171_D_MF-QATTA_3290DE | GEN failure/batteries under investigtion | Faulty System | Gen | Generator | 355961 | MF-QATTA | C3_3290DE_PH12 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals requried
IM769526 | 3290DE | 1171_D_MF-QATTA_3290DE | GEN failure/batteries under investigtion | Faulty System | Gen | Generator | 355961 | MF-QATTA | C3_3290DE_PH12 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Cable need to be terminated well
IM769549 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to generator problem (filter air) and stolen batteries | Faulty System | batt | Batteries | 314391 | REHAB-G17 | C1_3492CA_PH13 | Batteries | Some parts are missing/missing batteries
IM769549 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to generator problem (filter air) and stolen batteries | Faulty System | Gen | Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | ATS / Engine | Wrong connection/wrong connection
IM769549 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to generator problem (filter air) and stolen batteries | Faulty System | generator | Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | ATS / Engine | Wrong connection/wrong connection
IM769578 | 3096DE | 02891_G_3096DE_OBOUR-DST6 | down due to DG problem and no battery install | Faulty System | DG | Generator | 345263 | OBOUR-DST6 | C1_3096DE_PH12 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage
IM769622 | 3807UP | 0631_D_QN-MHAMID-QBLY_3807UP | Generator problem , batteries are suspected to be weak ,Guard night access problem , solved , Recovered after solvig the generator problem . | Faulty System | batt | Batteries | 355794 | 01_G_QN-MHAMID-QBLY_3807UP | C1_3807UP_PH15 | Rectifiers | Alarms reporting to the OMC/Rectifier minor alarm was looped at ddf
IM769622 | 3807UP | 0631_D_QN-MHAMID-QBLY_3807UP | Generator problem , batteries are suspected to be weak ,Guard night access problem , solved , Recovered after solvig the generator problem . | Faulty System | Gen | Generator | 355794 | 01_G_QN-MHAMID-QBLY_3807UP | C1_3807UP_PH15 | ATS / Engine | Unit earth/Earth bar is missing
IM769622 | 3807UP | 0631_D_QN-MHAMID-QBLY_3807UP | Generator problem , batteries are suspected to be weak ,Guard night access problem , solved , Recovered after solvig the generator problem . | Faulty System | generator | Generator | 355794 | 01_G_QN-MHAMID-QBLY_3807UP | C1_3807UP_PH15 | ATS / Engine | Unit earth/Earth bar is missing
IM769622 | 3807UP | 0631_D_QN-MHAMID-QBLY_3807UP | Generator problem , batteries are suspected to be weak ,Guard night access problem , solved , Recovered after solvig the generator problem . | Faulty System | Gen | Generator | 355794 | 01_G_QN-MHAMID-QBLY_3807UP | C1_3807UP_PH15 | ATS / Engine | Components faulty/Gen enclosure Screen press keys were defected
IM769622 | 3807UP | 0631_D_QN-MHAMID-QBLY_3807UP | Generator problem , batteries are suspected to be weak ,Guard night access problem , solved , Recovered after solvig the generator problem . | Faulty System | generator | Generator | 355794 | 01_G_QN-MHAMID-QBLY_3807UP | C1_3807UP_PH15 | ATS / Engine | Components faulty/Gen enclosure Screen press keys were defected
IM769622 | 3807UP | 0631_D_QN-MHAMID-QBLY_3807UP | Generator problem , batteries are suspected to be weak ,Guard night access problem , solved , Recovered after solvig the generator problem . | Faulty System | Gen | Generator | 355794 | 01_G_QN-MHAMID-QBLY_3807UP | C1_3807UP_PH15 | ATS / Engine | Filters condition oil/fuel/air/Air Filter cover is not fixed
IM769622 | 3807UP | 0631_D_QN-MHAMID-QBLY_3807UP | Generator problem , batteries are suspected to be weak ,Guard night access problem , solved , Recovered after solvig the generator problem . | Faulty System | generator | Generator | 355794 | 01_G_QN-MHAMID-QBLY_3807UP | C1_3807UP_PH15 | ATS / Engine | Filters condition oil/fuel/air/Air Filter cover is not fixed
IM769634 | 4011CA | 02353_V_4011CA_MOSTORD-RD2 | down due to main power cut off and stolen batt. (I) | Faulty System | batt | Batteries | 355905 | MOSTORD-RD2 | C1_4011CA_PH17 | Batteries | Some parts are (missing / stolen)/Batteries are stolen
IM769656 | 0709DE | 0181_D_GH-MIDO-PARK_0709DE | Access Owner / GN problem | Faulty System | GN | Generator | 355834 | GH-MIDO-PARK | C3_0709DE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check and clean
IM769656 | 0709DE | 0181_D_GH-MIDO-PARK_0709DE | Access Owner / GN problem | Faulty System | GN | Generator | 355834 | GH-MIDO-PARK | C3_0709DE_PH9 | ATS / Engine | Unit earth/not earthed
IM769656 | 0709DE | 0181_D_GH-MIDO-PARK_0709DE | Access Owner / GN problem | Faulty System | GN | Generator | 355834 | GH-MIDO-PARK | C3_0709DE_PH9 | ATS / Engine | Components faulty/faulty radiator
IM769656 | 0709DE | 0181_D_GH-MIDO-PARK_0709DE | Access Owner / GN problem | Faulty System | GN | Generator | 355834 | GH-MIDO-PARK | C3_0709DE_PH9 | ATS / Engine | Components faulty/faulty
IM769656 | 0709DE | 0181_D_GH-MIDO-PARK_0709DE | Access Owner / GN problem | Faulty System | GN | Generator | 355834 | GH-MIDO-PARK | C3_0709DE_PH9 | ATS / Engine | Components below/over rate (excluding main power feeder if not hot)/high rate
IM769689 | 3953DE | 0361_G_BH-MAARKA_3953DE | Access ET. / Main Power / Weak batteries / Clear on PG | Faulty System | batt | Batteries | 304235 | BH-MAARKA | C1_3953DE_PH15 | Batteries | Components faulty/Faulty battery and cable disconnected
IM769690 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN peoblem/Stolen batteries/ | Faulty System | batt | Batteries | 324500 | SK-AZZAZI | C1_4029DE_PH15 | Batteries | Item(s) stolen/No backup batteries.
IM769690 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN peoblem/Stolen batteries/ | Faulty System | GN | Generator | 324500 | SK-AZZAZI | C1_4029DE_PH15 | ATS / Engine | Wrong connection/Some cables are disconnected and need adjust.
IM769690 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN peoblem/Stolen batteries/ | Faulty System | GN | Generator | 324500 | SK-AZZAZI | C1_4029DE_PH15 | ATS / Engine | Panorama pictures for each system/Generator battery poles need cleaning, wax and covers.
IM769690 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN peoblem/Stolen batteries/ | Faulty System | GN | Generator | 324500 | SK-AZZAZI | C1_4029DE_PH15 | ATS / Engine | Panorama pictures for each system/Overview.
IM769696 | 3775DE | 0471_D_DK-DABBOS-VLG_3775DE | GN problem / batteries under check | Faulty System | GN | Generator | 325073 | DK-DABBOS-VLG | C1_3775DE_PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/bad terminals
IM769696 | 3775DE | 0471_D_DK-DABBOS-VLG_3775DE | GN problem / batteries under check | Faulty System | GN | Generator | 325073 | DK-DABBOS-VLG | C1_3775DE_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM769701 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to DG Dynamo problem and batt. stolen (I) | Faulty System | batt | Batteries | 314391 | REHAB-G17 | C1_3492CA_PH13 | Batteries | Some parts are missing/missing batteries
IM769701 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to DG Dynamo problem and batt. stolen (I) | Faulty System | DG | Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | ATS / Engine | Wrong connection/wrong connection
IM769724 | 0102RE | 00086_S_0102RE_SZ-STLLADEMARE | EC power outage / weak batteries / access PG problem/ Hotel / cleared after power restored | Faulty System | batt | Batteries | 324988 | SZ-STLLADEMARE | C3_0102RE_PH3 | Batteries | Item(s) stolen/Battery string stolen
IM769738 | 3844DE | 1841_S_BH-SAHALI_3844DE | Access Guard " 1786 " / H.T | Faulty System | H.T | A/Cs | 356089 | BH-SAHALI | C1_3844DE_PH14 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/A/C has no proper cooling (Working only as a fan)
IM769738 | 3844DE | 1841_S_BH-SAHALI_3844DE | Access Guard " 1786 " / H.T | Faulty System | H.T | A/Cs | 356089 | BH-SAHALI | C1_3844DE_PH14 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/A/C has no proper cooling (Working only as a fan) // Burned cables
IM769738 | 3844DE | 1841_S_BH-SAHALI_3844DE | Access Guard " 1786 " / H.T | Faulty System | H.T | A/Cs | 356089 | BH-SAHALI | C1_3844DE_PH14 | A/Cs Cooling / Free Cooling / Ventilation | Wrong connection/Cancelling the control board and replacing it by temperature sensor
IM769738 | 3844DE | 1841_S_BH-SAHALI_3844DE | Access Guard " 1786 " / H.T | Faulty System | H.T | A/Cs | 356089 | BH-SAHALI | C1_3844DE_PH14 | A/Cs Cooling / Free Cooling / Ventilation | Cables termination/lugs (AC side), lugs (DC side)/Cables at 1 slot
IM769738 | 3844DE | 1841_S_BH-SAHALI_3844DE | Access Guard " 1786 " / H.T | Faulty System | H.T | A/Cs | 356089 | BH-SAHALI | C1_3844DE_PH14 | A/Cs Cooling / Free Cooling / Ventilation | Cables termination/lugs (AC side), lugs (DC side)/Cable need to be terminated well
IM769747 | 0411RE | 03870_S_0411RE_RS-BRAYKA-BAY | PM Generator / stolen batteries | Faulty System | batt | Batteries | 356418 | 01_S_RS-BRAYKA-BAY_0411RE | C1_0411RE_PH15 | Batteries | Some parts are (missing / stolen)/Batteries were stolen
IM769747 | 0411RE | 03870_S_0411RE_RS-BRAYKA-BAY | PM Generator / stolen batteries | Faulty System | Gen | Generator | 356418 | 01_S_RS-BRAYKA-BAY_0411RE | C1_0411RE_PH15 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Open gland in Gen enclosure need insulation
IM769747 | 0411RE | 03870_S_0411RE_RS-BRAYKA-BAY | PM Generator / stolen batteries | Faulty System | generator | Generator | 356418 | 01_S_RS-BRAYKA-BAY_0411RE | C1_0411RE_PH15 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Open gland in Gen enclosure need insulation
IM769747 | 0411RE | 03870_S_0411RE_RS-BRAYKA-BAY | PM Generator / stolen batteries | Faulty System | Gen | Generator | 356418 | 01_S_RS-BRAYKA-BAY_0411RE | C1_0411RE_PH15 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Two cables inserted in one slot and not teminated can cause bad connections
IM769747 | 0411RE | 03870_S_0411RE_RS-BRAYKA-BAY | PM Generator / stolen batteries | Faulty System | generator | Generator | 356418 | 01_S_RS-BRAYKA-BAY_0411RE | C1_0411RE_PH15 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Two cables inserted in one slot and not teminated can cause bad connections
IM769876 | 0498RE | 03500_S_0498RE_SZ-SELIM-HAY | EC power outage / Sharing VF / weak batteries / access PG problem / cleared after power restored | Faulty System | batt | Batteries | 345366 | 01_S_SZ-SELIM-HAY_0498RE | C1_0498RE_PH17 | Batteries | Some parts are (missing / stolen)/Stolen battery
IM769892 | 3272UP | 0791_G_QN-QENWYA-BHRY_3272UP | Main power disconnection ,batteries are suspected to be weak , recovered when EC power come back | Faulty System | batt | Batteries | 355823 | 01_G_QN-QENWYA-BHRY_3272UP | C2_3272UP_PH14 | Batteries | Some parts are (missing / stolen)/Some of Batteries were stolen
IM769920 | 3628DE | 0811_S_GH-QSR-BAGHDAD_3628DE | Main power / stolen batteries | Faulty System | batt | Batteries | 324836 | GH-QSR-BAGHDAD | C2_3628DE_PH13 | Batteries | Item(s) stolen/Stolen batteries
IM769927 | 0248UP | 0061_H_SG-MINSHAH-NTH_0248UP | Main power disconnection, batteries are suspected to be weak, Standby Generator was not worked due to fuel pump problem, recovere d when EC power come back | Faulty System | batt | Batteries | 356519 | S_SG-MINSHAH-NTH_0248UP | C1_0248UP_PH06 | Batteries | Some parts are (missing / stolen)/Batteries string were stolen
IM769927 | 0248UP | 0061_H_SG-MINSHAH-NTH_0248UP | Main power disconnection, batteries are suspected to be weak, Standby Generator was not worked due to fuel pump problem, recovere d when EC power come back | Faulty System | Gen | Generator | 356519 | S_SG-MINSHAH-NTH_0248UP | C1_0248UP_PH06 | ATS / Engine | Wrong connection/neutral cable inside ATS panel was Burnt
IM769927 | 0248UP | 0061_H_SG-MINSHAH-NTH_0248UP | Main power disconnection, batteries are suspected to be weak, Standby Generator was not worked due to fuel pump problem, recovere d when EC power come back | Faulty System | generator | Generator | 356519 | S_SG-MINSHAH-NTH_0248UP | C1_0248UP_PH06 | ATS / Engine | Wrong connection/neutral cable inside ATS panel was Burnt
IM769927 | 0248UP | 0061_H_SG-MINSHAH-NTH_0248UP | Main power disconnection, batteries are suspected to be weak, Standby Generator was not worked due to fuel pump problem, recovere d when EC power come back | Faulty System | Gen | Generator | 356519 | S_SG-MINSHAH-NTH_0248UP | C1_0248UP_PH06 | ATS / Engine | Alarms on equipment (excluding ADM)/Gen has alarm
IM769927 | 0248UP | 0061_H_SG-MINSHAH-NTH_0248UP | Main power disconnection, batteries are suspected to be weak, Standby Generator was not worked due to fuel pump problem, recovere d when EC power come back | Faulty System | generator | Generator | 356519 | S_SG-MINSHAH-NTH_0248UP | C1_0248UP_PH06 | ATS / Engine | Alarms on equipment (excluding ADM)/Gen has alarm
IM769927 | 0248UP | 0061_H_SG-MINSHAH-NTH_0248UP | Main power disconnection, batteries are suspected to be weak, Standby Generator was not worked due to fuel pump problem, recovere d when EC power come back | Faulty System | Gen | Generator | 356519 | S_SG-MINSHAH-NTH_0248UP | C1_0248UP_PH06 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Bad teminated can cause bad connections
IM769927 | 0248UP | 0061_H_SG-MINSHAH-NTH_0248UP | Main power disconnection, batteries are suspected to be weak, Standby Generator was not worked due to fuel pump problem, recovere d when EC power come back | Faulty System | generator | Generator | 356519 | S_SG-MINSHAH-NTH_0248UP | C1_0248UP_PH06 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Bad teminated can cause bad connections
IM769927 | 0248UP | 0061_H_SG-MINSHAH-NTH_0248UP | Main power disconnection, batteries are suspected to be weak, Standby Generator was not worked due to fuel pump problem, recovere d when EC power come back | Faulty System | Gen | Generator | 356519 | S_SG-MINSHAH-NTH_0248UP | C1_0248UP_PH06 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Two cables inserted in one slot and bad teminated can cause bad connections
IM769927 | 0248UP | 0061_H_SG-MINSHAH-NTH_0248UP | Main power disconnection, batteries are suspected to be weak, Standby Generator was not worked due to fuel pump problem, recovere d when EC power come back | Faulty System | generator | Generator | 356519 | S_SG-MINSHAH-NTH_0248UP | C1_0248UP_PH06 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Two cables inserted in one slot and bad teminated can cause bad connections
IM769948 | 0028RE | 03477_N_0028RE_SZ-SUEZ8 | EC power outage / weak batteries / access PG problem / cleared after power restored | Faulty System | batt | Batteries | 345369 | 01_N_SZ-SUEZ8_0028RE | C2_0028RE_PH1 | Batteries | Some parts are (missing / stolen)/Stolen battery string
IM769954 | 3385DE | 0671_S_BH-GHAZALA-VLG_3385DE | Suspected main power / batteries under check | Faulty System | batt | Batteries | 355780 | BH-GHAZALA-VLG | C2_3385DE_PH13 | Rectifiers | Alarms reporting to the OMC/Site down due to power (Check alarms with OMC)
IM769974 | 0102RE | 00086_S_0102RE_SZ-STLLADEMARE | EC power outage / weak batteries / access PG problem/ Hotel / cleared after power restored | Faulty System | batt | Batteries | 324988 | SZ-STLLADEMARE | C3_0102RE_PH3 | Batteries | Item(s) stolen/Battery string stolen
IM769983 | 3394DE | 0011_S_B-SAFT-KHALED_3394DE | Share VF / Main power / weak batteries | Faulty System | batt | Batteries | 304033 | BH-SAFT-KHALED | C1_3394DE_PH13 | Batteries | Components faulty/Faulty battery
IM769985 | 3333DE | 0181_S_BH-OM-SABER_3333DE | Access VF. / Main Power / Stolen batteries / Clear after power back | Faulty System | batt | Batteries | 304089 | BH-OM-SABER_SSS0 | C1_3333DE_PH12 | Batteries | Item(s) stolen/There is no battery for site
IM770053 | 0476DE | 0111_N_DK-BESHLA_0476DE | Main power/ batteries dismentle/clear after power back | Faulty System | batt | Batteries | 356100 | DK-BESHLA | C3_0476DE_PH7 | Batteries | Some parts are (missing / stolen)/no batteries
IM770072 | 0443SI | 0481_G_SS-RING-RD2_0443SI | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 355554 | 01_G_SS-RING-RD2_0443SI | C1_0443SI_PH12 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage
IM770072 | 0443SI | 0481_G_SS-RING-RD2_0443SI | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 355554 | 01_G_SS-RING-RD2_0443SI | C1_0443SI_PH12 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage
IM770072 | 0443SI | 0481_G_SS-RING-RD2_0443SI | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 355554 | 01_G_SS-RING-RD2_0443SI | C1_0443SI_PH12 | ATS / Engine | Unit earth/earth cable not connected
IM770072 | 0443SI | 0481_G_SS-RING-RD2_0443SI | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 355554 | 01_G_SS-RING-RD2_0443SI | C1_0443SI_PH12 | ATS / Engine | Unit earth/earth bar not connected to main earth bar
IM770072 | 0443SI | 0481_G_SS-RING-RD2_0443SI | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 355554 | 01_G_SS-RING-RD2_0443SI | C1_0443SI_PH12 | ATS / Engine | Wrong connection/welded cable
IM770072 | 0443SI | 0481_G_SS-RING-RD2_0443SI | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 355554 | 01_G_SS-RING-RD2_0443SI | C1_0443SI_PH12 | ATS / Engine | Wrong connection/welded neutral cable
IM770072 | 0443SI | 0481_G_SS-RING-RD2_0443SI | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 355554 | 01_G_SS-RING-RD2_0443SI | C1_0443SI_PH12 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/cable not terminated
IM770072 | 0443SI | 0481_G_SS-RING-RD2_0443SI | DG stoppage / weak batteries / cleared after power restored | Faulty System | DG | Generator | 355554 | 01_G_SS-RING-RD2_0443SI | C1_0443SI_PH12 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/cables not terminated
IM770148 | 0498RE | 03500_S_0498RE_SZ-SELIM-HAY | EC power outage / Sharing VF / weak batteries / access PG problem / cleared after power restored | Faulty System | batt | Batteries | 345366 | 01_S_SZ-SELIM-HAY_0498RE | C1_0498RE_PH17 | Batteries | Some parts are (missing / stolen)/Stolen battery
IM770198 | 0613DE | 00167_D_0613DE_SANDORINI-CLUB | GN. Problem /batteries UNDER INVESTIGATION / clear after check GEN | Faulty System | Gen | Generator | 303981 | Sandorini Country Club | C1_0613DE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check and clean
IM770198 | 0613DE | 00167_D_0613DE_SANDORINI-CLUB | GN. Problem /batteries UNDER INVESTIGATION / clear after check GEN | Faulty System | GN | Generator | 303981 | Sandorini Country Club | C1_0613DE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check and clean
IM770220 | 0540UP | 0071_G_AS-ENT_0540UP_X | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | batt | Batteries | 345343 | 01_G_AS-ENT_0540UP | C3_0540UP_PH9 | Rectifiers | Alarms reporting to the OMC/Rectifer alarm not appeared on the omc ( Minor & major rectifier alarm looped at ddf )
IM770220 | 0540UP | 0071_G_AS-ENT_0540UP_X | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | batt | Batteries | 345343 | 01_G_AS-ENT_0540UP | C3_0540UP_PH9 | Batteries | Some parts are (missing / stolen)/One Batteries string was stolen
IM770220 | 0540UP | 0071_G_AS-ENT_0540UP_X | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | Gen | Generator | 345343 | 01_G_AS-ENT_0540UP | C3_0540UP_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure
IM770220 | 0540UP | 0071_G_AS-ENT_0540UP_X | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | Faulty System | generator | Generator | 345343 | 01_G_AS-ENT_0540UP | C3_0540UP_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure
IM770244 | 0405RE | 03878_S_0405RE_RS-MRSA-NAKARI | ET DG Stoppage / stolen batteries / cleared after GEN restored | Faulty System | batt | Batteries | 356420 | 01_S_RS-MRSA-NAKARI_0405RE | C1_0405RE_PH15 | Batteries | Some parts are (missing / stolen)/Batteries were stolen
IM770291 | 3494DE | 1101_D_GH-ATWA-QIBLYA_3494DE | GN problem / Stolen batteries | Faulty System | GN | Generator | 345242 | GH-ATWA-QIBLYA | C4_3494DE_PH13 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminal requried
IM770291 | 3494DE | 1101_D_GH-ATWA-QIBLYA_3494DE | GN problem / Stolen batteries | Faulty System | GN | Generator | 345242 | GH-ATWA-QIBLYA | C4_3494DE_PH13 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Cable need to be terminated well
IM770291 | 3494DE | 1101_D_GH-ATWA-QIBLYA_3494DE | GN problem / Stolen batteries | Faulty System | GN | Generator | 345242 | GH-ATWA-QIBLYA | C4_3494DE_PH13 | ATS / Engine | Filters condition oil/fuel/air/Missing protective cover
IM770311 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem and access VF problem and stolen batt. (I) | Faulty System | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | Batteries | Some parts are (missing / stolen)/missing battereis
IM770335 | 0485SI | 01_S_SS-MOUSA-COAST_0485SI | Outage power in area located site , dead batteries Once power restored , site recovered | Faulty System | batt | Batteries | 356428 | 01_S_SS-MOUSA-COAST_0485SI | C1_0485SI_PH13 | Batteries | Components faulty/All battery string exploded & not work
IM770340 | 3892DE | 0171_S_BH-ZWIT-HUMOR_3892DE | Main power / Stolen batteries | Faulty System | batt | Batteries | 324905 | BH-ZWIT-HUMOR | C1_3892DE_PH14 | Batteries | Item(s) stolen/There is no battery for site
IM770341 | 0576DE | 1611_G_BH-WAFAIYYA_0576DE | Main power / Stolen batteries | Faulty System | batt | Batteries | 324440 | BH-WAFAIYYA | C2_0576DE_PH9 | Batteries | Item(s) stolen/There is no battery for site
IM770352 | 3844DE | 1841_S_BH-SAHALI_3844DE | H.T alarm / BTS hanged | Faulty System | H.T | A/Cs | 356089 | BH-SAHALI | C1_3844DE_PH14 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/A/C has no proper cooling (Working only as a fan)
IM770352 | 3844DE | 1841_S_BH-SAHALI_3844DE | H.T alarm / BTS hanged | Faulty System | H.T | A/Cs | 356089 | BH-SAHALI | C1_3844DE_PH14 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/A/C has no proper cooling (Working only as a fan) // Burned cables
IM770352 | 3844DE | 1841_S_BH-SAHALI_3844DE | H.T alarm / BTS hanged | Faulty System | H.T | A/Cs | 356089 | BH-SAHALI | C1_3844DE_PH14 | A/Cs Cooling / Free Cooling / Ventilation | Wrong connection/Cancelling the control board and replacing it by temperature sensor
IM770352 | 3844DE | 1841_S_BH-SAHALI_3844DE | H.T alarm / BTS hanged | Faulty System | H.T | A/Cs | 356089 | BH-SAHALI | C1_3844DE_PH14 | A/Cs Cooling / Free Cooling / Ventilation | Cables termination/lugs (AC side), lugs (DC side)/Cables at 1 slot
IM770352 | 3844DE | 1841_S_BH-SAHALI_3844DE | H.T alarm / BTS hanged | Faulty System | H.T | A/Cs | 356089 | BH-SAHALI | C1_3844DE_PH14 | A/Cs Cooling / Free Cooling / Ventilation | Cables termination/lugs (AC side), lugs (DC side)/Cable need to be terminated well
IM770353 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Due to Generator problem , weak batteries, Recovered | Faulty System | Gen | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | ATS / Engine | Components faulty/Gen battery was defected
IM770353 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Due to Generator problem , weak batteries, Recovered | Faulty System | generator | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | ATS / Engine | Components faulty/Gen battery was defected
IM770353 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Due to Generator problem , weak batteries, Recovered | Faulty System | Gen | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/ATS Cables not organized
IM770353 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Due to Generator problem , weak batteries, Recovered | Faulty System | generator | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/ATS Cables not organized
IM770365 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to DG oil sensor problem & stolen batteries (T) | Faulty System | batt | Batteries | 314391 | REHAB-G17 | C1_3492CA_PH13 | Batteries | Some parts are missing/missing batteries
IM770365 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to DG oil sensor problem & stolen batteries (T) | Faulty System | DG | Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | ATS / Engine | Wrong connection/wrong connection
IM770375 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Wrong connection/external cable to the guard connected from gen and not protected
IM770375 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Wrong connection/external cable to the guard connected from gen and not protected
IM770375 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Wrong connection/One Contactor turned on by setting wood inside it
IM770375 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Wrong connection/One Contactor turned on by setting wood inside it
IM770375 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cables not protected in tube
IM770375 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cables not protected in tube
IM770375 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cables not protected
IM770375 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cables not protected
IM770375 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Item(s) stolen/Gen battery is missing
IM770375 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Item(s) stolen/Gen battery is missing
IM770375 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/ Fuel leakage inside Gen
IM770375 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/ Fuel leakage inside Gen
IM770375 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage inside Gen
IM770375 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage inside Gen
IM770375 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage beisde Gen enclosure area need cleaning
IM770375 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage beisde Gen enclosure area need cleaning
IM770375 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Panorama pictures for each system/Open gland in Gen enclosure need insulation
IM770375 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Panorama pictures for each system/Open gland in Gen enclosure need insulation
IM770375 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM770375 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM770375 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Panorama pictures for each system/Last Gen hour meter at Audit G ( 31148 )
IM770375 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Panorama pictures for each system/Last Gen hour meter at Audit G ( 31148 )
IM770392 | 0800CA | 01942_S_0800CA_RAMADAN-FCT | Outage power in factory located site access factory weekend / weak batteries /Nog. informed Once power restored site recovered | Faulty System | batt | Batteries | 356352 | RAMADAN-FCT | C1_0800CA_PH9 | Rectifiers | Alarms reporting to the OMC/Power alarm not report the OMC due to loop on DDF
IM770392 | 0800CA | 01942_S_0800CA_RAMADAN-FCT | Outage power in factory located site access factory weekend / weak batteries /Nog. informed Once power restored site recovered | Faulty System | batt | Batteries | 356352 | RAMADAN-FCT | C1_0800CA_PH9 | Rectifiers | Alarms reporting to the OMC/Rectifier minor alarm not report the OMC due to loop on DDF
IM770405 | 0476DE | 0111_N_DK-BESHLA_0476DE | main power/batteries not installed /clear after power back | Faulty System | batt | Batteries | 356100 | DK-BESHLA | C3_0476DE_PH7 | Batteries | Some parts are (missing / stolen)/no batteries
IM770463 | 3454DE | 1061_D_GH-MAHLT-MENOF_3454DE | share ET / GN problem / stolen batteries | Faulty System | batt | Batteries | 324838 | GH-MAHLT-MENOF | C2_3454DE_PH13 | Batteries | Item(s) stolen/Stolen Batteries
IM770463 | 3454DE | 1061_D_GH-MAHLT-MENOF_3454DE | share ET / GN problem / stolen batteries | Faulty System | GN | Generator | 324838 | GH-MAHLT-MENOF | C2_3454DE_PH13 | ATS / Engine | Item(s) stolen/stolen batteries
IM770463 | 3454DE | 1061_D_GH-MAHLT-MENOF_3454DE | share ET / GN problem / stolen batteries | Faulty System | GN | Generator | 324838 | GH-MAHLT-MENOF | C2_3454DE_PH13 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM770534 | 0485SI | 01_S_SS-MOUSA-COAST_0485SI | Outage power in area located site , dead batteries Once power restored , site recovered | Faulty System | batt | Batteries | 356428 | 01_S_SS-MOUSA-COAST_0485SI | C1_0485SI_PH13 | Batteries | Components faulty/All battery string exploded & not work
IM770542 | 3778UP | 1291_S_AS-SABIL_3778UP_X | Main power disconnection , stolen batteries , SCG defected , P.G Connected . | Faulty System | batt | Batteries | 356225 | 01_S_AS-SABIL_3778UP | C1_3778UP_PH15 | Batteries | Some parts are (missing / stolen)/Batteries were stolen
IM770548 | 0899UP | 00352_S_0899UP_6OCT-ZAYED-1ST | down due to main power cut off and stolen batt. (I) | Faulty System | batt | Batteries | 356343 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Batteries | Some parts are (missing / stolen)/stolen batteries
IM770576 | 0405RE | 03878_S_0405RE_RS-MRSA-NAKARI | ET DG Stopped , stolen batteries , caused site Down once ET team fix DG Site recovered | Faulty System | batt | Batteries | 356420 | 01_S_RS-MRSA-NAKARI_0405RE | C1_0405RE_PH15 | Batteries | Some parts are (missing / stolen)/Batteries were stolen
IM770578 | 3916DE | 1191_S_BH-BAYDA-2_3916DE | Access guard / Main power / weak batteries | Faulty System | batt | Batteries | 355465 | BH-BAYDA-2 | C1_3916DE_PH14 | Batteries | Components faulty/faulty
IM770579 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/stolen battery/clear after check GN | Faulty System | batt | Batteries | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | Batteries | Some parts are missing/Battery cabinet need cleaning (from inside) and holes need sealing.
IM770579 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/stolen battery/clear after check GN | Faulty System | batt | Batteries | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | Batteries | Some parts are missing/Batteries poles need have missing covers.
IM770579 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/stolen battery/clear after check GN | Faulty System | GN | Generator | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | ATS / Engine | Components faulty/Generator has bad performance and need overall.
IM770579 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/stolen battery/clear after check GN | Faulty System | GN | Generator | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | ATS / Engine | Panorama pictures for each system/Overview.
IM770593 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | VF GN / VF night access /stolen battery/clear after | Faulty System | batt | Batteries | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | Batteries | Item(s) stolen/There is no battery for site
IM770593 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | VF GN / VF night access /stolen battery/clear after | Faulty System | GN | Generator | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cable has damaged protective isolation
IM770597 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem & access VF problem & stolen batt. (I) | Faulty System | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | Batteries | Some parts are (missing / stolen)/missing battereis
IM770612 | 3368DE | 0201_S_BH-ABO-SHIQAF_3368DE | Access VF / Main power / stolen batteries | Faulty System | batt | Batteries | 324904 | BH-ABO-SHIQAF | C1_3368DE_PH12 | Batteries | Item(s) stolen/There is no battery for site
IM770640 | 0595DE | 0281_G_DK-NISHA_0595DE | Main power / weak batteries | Faulty System | batt | Batteries | 324924 | DK-NISHAA | C1_0595DE_PH9 | Batteries | Some parts are missing/cover
IM770661 | 3495DE | 0181_S_SK-MAHDIYA_3495DE | Main Power / Stolen batteries / Clear after power back | Faulty System | batt | Batteries | 304144 | SK-MAHDIYA | C3_3495DE_PH13 | Batteries | Item(s) stolen/No backup batteries.
IM770665 | 0476DE | 0111_N_DK-BESHLA_0476DE | Main power/batteries were dismanteled/ | Faulty System | batt | Batteries | 356100 | DK-BESHLA | C3_0476DE_PH7 | Batteries | Some parts are (missing / stolen)/no batteries
IM770668 | 0364RE | U_S_0364RE_SZ-MALLAHA | Outage power in area located site , dead batteries , access PG Once power restored , site recovered | Faulty System | batt | Batteries | 356046 | SZ-MALLAHA | 0364RE | Batteries | Some parts are (missing / stolen)/Missing battery pole cover
IM770676 | 0485DE | K_MF-BARAHIM_21106_1 | Main power /6074150/batteries under investigation@MF-BARAHIM_0485DE// | Faulty System | batt | Batteries | 304303 | MF-BARAHIM | C5_0485DE_PH7 | Batteries | Some parts are missing/Battery without covers
IM770679 | 0587DE | 0221_S_DK-KFR-KURDI_0587DE | Share VF / main power / stolen batteries | Faulty System | batt | Batteries | 324791 | DK-KFR-KURDI | C9_0587DE_PH09 | Batteries | Item(s) stolen/No backup batteries.
IM770710 | 3403UP | 01_G_LU-QBLY-QAMOLA_3403UP | Main power disconnection ,batteries are suspected to be weak , P.G connected | Faulty System | batt | Batteries | 356289 | 01_G_LU-QBLY-QAMOLA_3403UP | C2_3403UP_PH14 | Batteries | Components faulty/Backup batteries voltage drop too fast
IM770758 | 3394DE | 0011_S_B-SAFT-KHALED_3394DE | VF Share / Main power / Weak batteries | Faulty System | batt | Batteries | 304033 | BH-SAFT-KHALED | C1_3394DE_PH13 | Batteries | Components faulty/Faulty battery
IM770869 | 3089UP | 2141_S_SG-GALAWEYA_3089UP | Main power disconnection , stolen batteries , recovered when EC power come back | Faulty System | batt | Batteries | 356371 | 01_S_SG-GALAWEYA_3089UP | C1_3089UP_PH13 | Batteries | Some parts are (missing / stolen)/site batteries were Stolen
IM770885 | 0029SI | 01_G_SZ-HALIJAL-OYUN_0029SI | DG Stopped due alternator problem , dead batteries once team arrive and install PG Sites Recovered | Faulty System | batt | Batteries | 325124 | 01_G_SZ-HALIJAL-OYUN_0029SI | C2_0029SI_PH2 | Batteries | Item(s) stolen/Stolen battery string
IM770885 | 0029SI | 01_G_SZ-HALIJAL-OYUN_0029SI | DG Stopped due alternator problem , dead batteries once team arrive and install PG Sites Recovered | Faulty System | batt | Batteries | 325124 | 01_G_SZ-HALIJAL-OYUN_0029SI | C2_0029SI_PH2 | Batteries | Item(s) stolen/C.B's connected to the stolen battery string should be switched off
IM770885 | 0029SI | 01_G_SZ-HALIJAL-OYUN_0029SI | DG Stopped due alternator problem , dead batteries once team arrive and install PG Sites Recovered | Faulty System | DG | Generator | 325124 | 01_G_SZ-HALIJAL-OYUN_0029SI | C2_0029SI_PH2 | ATS / Engine | Components faulty/Genset indicator notwork , voltage & temp
IM770885 | 0029SI | 01_G_SZ-HALIJAL-OYUN_0029SI | DG Stopped due alternator problem , dead batteries once team arrive and install PG Sites Recovered | Faulty System | DG | Generator | 325124 | 01_G_SZ-HALIJAL-OYUN_0029SI | C2_0029SI_PH2 | ATS / Engine | Components faulty/Burnet main contactor
IM770885 | 0029SI | 01_G_SZ-HALIJAL-OYUN_0029SI | DG Stopped due alternator problem , dead batteries once team arrive and install PG Sites Recovered | Faulty System | DG | Generator | 325124 | 01_G_SZ-HALIJAL-OYUN_0029SI | C2_0029SI_PH2 | ATS / Engine | Components faulty/Burnet ATS panel
IM770885 | 0029SI | 01_G_SZ-HALIJAL-OYUN_0029SI | DG Stopped due alternator problem , dead batteries once team arrive and install PG Sites Recovered | Faulty System | DG | Generator | 325124 | 01_G_SZ-HALIJAL-OYUN_0029SI | C2_0029SI_PH2 | ATS / Engine | Wrong connection/Jumper on the main contactor
IM770885 | 0029SI | 01_G_SZ-HALIJAL-OYUN_0029SI | DG Stopped due alternator problem , dead batteries once team arrive and install PG Sites Recovered | Faulty System | DG | Generator | 325124 | 01_G_SZ-HALIJAL-OYUN_0029SI | C2_0029SI_PH2 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Bad terminals of main contactor
IM770885 | 0029SI | 01_G_SZ-HALIJAL-OYUN_0029SI | DG Stopped due alternator problem , dead batteries once team arrive and install PG Sites Recovered | Faulty System | DG | Generator | 325124 | 01_G_SZ-HALIJAL-OYUN_0029SI | C2_0029SI_PH2 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Disconnected ATS cable
IM770885 | 0029SI | 01_G_SZ-HALIJAL-OYUN_0029SI | DG Stopped due alternator problem , dead batteries once team arrive and install PG Sites Recovered | Faulty System | DG | Generator | 325124 | 01_G_SZ-HALIJAL-OYUN_0029SI | C2_0029SI_PH2 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Hole in the genset container
IM770885 | 0029SI | 01_G_SZ-HALIJAL-OYUN_0029SI | DG Stopped due alternator problem , dead batteries once team arrive and install PG Sites Recovered | Faulty System | DG | Generator | 325124 | 01_G_SZ-HALIJAL-OYUN_0029SI | C2_0029SI_PH2 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Genset oil leakage
IM770885 | 0029SI | 01_G_SZ-HALIJAL-OYUN_0029SI | DG Stopped due alternator problem , dead batteries once team arrive and install PG Sites Recovered | Faulty System | DG | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure
IM770885 | 0029SI | 01_G_SZ-HALIJAL-OYUN_0029SI | DG Stopped due alternator problem , dead batteries once team arrive and install PG Sites Recovered | Faulty System | DG | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Wrong connection/generator battery as used in the site and not suitable in High temp
IM770894 | 3634DE | 1481_D_MF-DAMLIG_3634DE | Main power /batteries under investigation// Clear after power back | Faulty System | batt | Batteries | 303849 | MF-DAMLIG | C1-3634DE-PH13 | Batteries | Components faulty/Faulty battery
IM771001 | 3943DE | 0921_S_SK-AKRASH_3943DE | Access ET. / ET. GN. Problem / stolen batteries @ 0921_S_SK-AKRASH_3943DE / Clear after checking GN. | Faulty System | batt | Batteries | 303886 | SK-AKRASH | C1_3943DE_PH15 | Batteries | Item(s) stolen/No backup batteries.
IM771019 | 3867DE | 2101_S_GH-NAWYA_3867DE | Main power / weak batteries | Faulty System | batt | Batteries | 324418 | GH-NAWYA | C1_3867DE_PH14 | Batteries | Item(s) stolen/stolen
IM771047 | 0578DE | 0801_G_SK-QSASIN-AZHR_0578DE | main power/stolen Batteries @QSASIN-AZHR_0578DE/clear after power back | Faulty System | batt | Batteries | 335150 | PS-KHADIGA | C2_3413DE_PH13 | Batteries | Item(s) stolen/missing batteries
IM771070 | 0605DE | 0041_S_DK-MAHMUDIYYA_0605DE | Main power @DK-MAHMUDIYYA_0605DE / stolen batteries | Faulty System | batt | Batteries | 304053 | DK-MAHMUDIYYA | C2_0605DE_PH9 | Batteries | Item(s) stolen/No backup batteries.
IM771115 | 0405RE | 03878_S_0405RE_RS-MRSA-NAKARI | ET DG Stopped , stolen batteries recovered once VDF DG fixed | Faulty System | batt | Batteries | 356420 | 01_S_RS-MRSA-NAKARI_0405RE | C1_0405RE_PH15 | Batteries | Some parts are (missing / stolen)/Batteries were stolen
IM771123 | 0242CA | 01963_S_0242CA_10TH-RSD2 | Outage power in factory located site , access PG , weak Backup Recovered once power restored | Faulty System | backup | Batteries | 356353 | 10TH-RSD2 | C4_0242CA_PH2 | Batteries | Some parts are (missing / stolen)/Battery string stolen
IM771131 | 3429UP | 0901_D_QN-BELAD-ELMAL_3429UP | Due to PM generator with AP# C358757 , weak batteries , Recovered . | Faulty System | Gen | Generator | 356495 | 01_G_QN-BELAD-ELMAL_3429UP | C1_3429UP_PH14 | ATS / Engine | Unit earth/Gen enclosure earth cable is missing
IM771131 | 3429UP | 0901_D_QN-BELAD-ELMAL_3429UP | Due to PM generator with AP# C358757 , weak batteries , Recovered . | Faulty System | generator | Generator | 356495 | 01_G_QN-BELAD-ELMAL_3429UP | C1_3429UP_PH14 | ATS / Engine | Unit earth/Gen enclosure earth cable is missing
IM771131 | 3429UP | 0901_D_QN-BELAD-ELMAL_3429UP | Due to PM generator with AP# C358757 , weak batteries , Recovered . | Faulty System | Gen | Generator | 356495 | 01_G_QN-BELAD-ELMAL_3429UP | C1_3429UP_PH14 | ATS / Engine | Components faulty/fuel level sensor not working and faulty (checked with zte team and it is not working )
IM771131 | 3429UP | 0901_D_QN-BELAD-ELMAL_3429UP | Due to PM generator with AP# C358757 , weak batteries , Recovered . | Faulty System | generator | Generator | 356495 | 01_G_QN-BELAD-ELMAL_3429UP | C1_3429UP_PH14 | ATS / Engine | Components faulty/fuel level sensor not working and faulty (checked with zte team and it is not working )
IM771131 | 3429UP | 0901_D_QN-BELAD-ELMAL_3429UP | Due to PM generator with AP# C358757 , weak batteries , Recovered . | Faulty System | Gen | Generator | 356495 | 01_G_QN-BELAD-ELMAL_3429UP | C1_3429UP_PH14 | ATS / Engine | Components faulty/Gen enclosure battery is faulty
IM771131 | 3429UP | 0901_D_QN-BELAD-ELMAL_3429UP | Due to PM generator with AP# C358757 , weak batteries , Recovered . | Faulty System | generator | Generator | 356495 | 01_G_QN-BELAD-ELMAL_3429UP | C1_3429UP_PH14 | ATS / Engine | Components faulty/Gen enclosure battery is faulty
IM771131 | 3429UP | 0901_D_QN-BELAD-ELMAL_3429UP | Due to PM generator with AP# C358757 , weak batteries , Recovered . | Faulty System | Gen | Generator | 356495 | 01_G_QN-BELAD-ELMAL_3429UP | C1_3429UP_PH14 | ATS / Engine | Components faulty/ATS pressing keys were faulty and screen glass was broken
IM771131 | 3429UP | 0901_D_QN-BELAD-ELMAL_3429UP | Due to PM generator with AP# C358757 , weak batteries , Recovered . | Faulty System | generator | Generator | 356495 | 01_G_QN-BELAD-ELMAL_3429UP | C1_3429UP_PH14 | ATS / Engine | Components faulty/ATS pressing keys were faulty and screen glass was broken
IM771153 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | Access VF Guard/VF GN problem/Stolen batteries/clear on P.G | Faulty System | batt | Batteries | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | Batteries | Item(s) stolen/There is no battery for site
IM771153 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | Access VF Guard/VF GN problem/Stolen batteries/clear on P.G | Faulty System | GN | Generator | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cable has damaged protective isolation
IM771160 | 3594DE | 1241_S_BH-TAYRIYA_3594DE | main power/stolen Batteries /clear after power back | Faulty System | batt | Batteries | 325119 | BH-TAYRIYA | C1-3594DE-PH13 | Batteries | Item(s) stolen/There is no battery for site
IM771199 | 4021DE | 0181_S_BH-ABQAEEN_4021DE | Access VF / Main power / stolen batteries | Faulty System | batt | Batteries | 304224 | BH-ABQAEEN | C1_4021DE_PH15 | Batteries | Item(s) stolen/There is no battery for site
IM771216 | 4021DE | 0181_S_BH-ABQAEEN_4021DE | Access VF / Main power / stolen batteries | Faulty System | batt | Batteries | 304224 | BH-ABQAEEN | C1_4021DE_PH15 | Batteries | Item(s) stolen/There is no battery for site
IM771218 | 3368DE | 0201_S_BH-ABO-SHIQAF_3368DE | Access VF / Main power / stolen batteries | Faulty System | batt | Batteries | 324904 | BH-ABO-SHIQAF | C1_3368DE_PH12 | Batteries | Item(s) stolen/There is no battery for site
IM771275 | 3953DE | 0361_G_BH-MAARKA_3953DE | access ET/Main power/weak batteries clear on P.G | Faulty System | batt | Batteries | 304235 | BH-MAARKA | C1_3953DE_PH15 | Batteries | Components faulty/Faulty battery and cable disconnected
IM771305 | 0070SI | 01_S_SS-SAINT-CATRN_0070SI | Power outage site has weak batteries and access PG problem recovered once power restored | Faulty System | batt | Batteries | 356151 | 01_S_SS-SAINT-CATRN_0070SI | C2_0070SI_PH2 | Rectifiers | Alarms reporting to the OMC/rectifier major alarm appears
IM771319 | 3199UP | 0641_S_AT-GANADLAH_3199UP | Due to EC power cutoff , stolen batteries , Recovered | Faulty System | batt | Batteries | 303847 | 01_S_AT-GANADLAH_3199UP | C2_3199UP_PH13 | Batteries | Item(s) stolen/site Batteries were Stolen
IM771395 | 0405RE | 03878_S_0405RE_RS-MRSA-NAKARI | ET DG Stopped , New site without Backup recovered once VDF DG fixed | Faulty System | backup | Batteries | 356420 | 01_S_RS-MRSA-NAKARI_0405RE | C1_0405RE_PH15 | Batteries | Some parts are (missing / stolen)/Batteries were stolen
IM771418 | 3628DE | 0811_S_GH-QSR-BAGHDAD_3628DE | Main power / stolen batteries | Faulty System | batt | Batteries | 324836 | GH-QSR-BAGHDAD | C2_3628DE_PH13 | Batteries | Item(s) stolen/Stolen batteries
IM771434 | 0459SI | 01_G_SS-RIVIERA_0459SI | DG Stopped , weak batteries caused site Down once DG Fix site recovered | Faulty System | DG | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure
IM771434 | 0459SI | 01_G_SS-RIVIERA_0459SI | DG Stopped , weak batteries caused site Down once DG Fix site recovered | Faulty System | DG | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Wrong connection/generator battery as used in the site and not suitable in High temp
IM771444 | 0452AL | 2001_S_MIAMI-SBWY-RD2_0452AL | Main Power Problem / Weak Batteries / Auto Recovered | Faulty System | batt | Batteries | 303998 | S_MIAMI-SBWY-RD2_0452AL | C1_0452AL_PH9 | Batteries | Item(s) stolen/No backup batteries.
IM771455 | 3548DE | 1391_S_GH-SANADID_3548DE | main power problem /Stolen batteries/handel shatanouf west,,batanoun,birkit esab north ,denshway/clear on P.F | Faulty System | batt | Batteries | 325091 | GH-SANADID | C2_3548DE_PH16 | Batteries | Item(s) stolen/No battery for site
IM771521 | 3534DE | 1641_D_SK-SANGAHA_3534DE | main power/weak batteries /clear on P.G | Faulty System | batt | Batteries | 335160 | SK-SANGAHA | C1-3534DE-PH13 | Batteries | Components faulty/batteries are ballooned and have cracked.
IM771521 | 3534DE | 1641_D_SK-SANGAHA_3534DE | main power/weak batteries /clear on P.G | Faulty System | batt | Batteries | 335160 | SK-SANGAHA | C1-3534DE-PH13 | Batteries | Some parts are missing/batteries poles need cover.
IM771629 | 3037DE | 0301_D_DK-BAGALAT_3037DE | GN problem / Stolen batteries | Faulty System | batt | Batteries | 345376 | DK-BAGALAT | C3_3037DE_PH11 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM771629 | 3037DE | 0301_D_DK-BAGALAT_3037DE | GN problem / Stolen batteries | Faulty System | GN | Generator | 345376 | DK-BAGALAT | C3_3037DE_PH11 | ATS / Engine | Components faulty/Control module has faulty buttons.
IM771629 | 3037DE | 0301_D_DK-BAGALAT_3037DE | GN problem / Stolen batteries | Faulty System | GN | Generator | 345376 | DK-BAGALAT | C3_3037DE_PH11 | ATS / Engine | Wrong connection/Cable has bad connections and need replacement.
IM771631 | 3949DE | 0721_S_SK-ABO-ARABY_3949DE | access ET/ET owner/Guard switch MCB OFF/stolen batteries | Faulty System | batt | Batteries | 355738 | SK-ABO-ARABY | C01_3949DE_PH15 | Batteries | Components faulty/Batteries can't carry site.
IM771654 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | VF Share / Main power / Stolen batteries | Faulty System | batt | Batteries | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | Batteries | Item(s) stolen/Stolen
IM771675 | 0605DE | 0041_S_DK-MAHMUDIYYA_0605DE | Main power @DK-MAHMUDIYYA_0605DE / stolen batteries | Faulty System | batt | Batteries | 304053 | DK-MAHMUDIYYA | C2_0605DE_PH9 | Batteries | Item(s) stolen/No backup batteries.
IM771676 | 3400DE | 0731_S_GH-GHAZL-MAHLA_3400DE | Share VF / Main power / stolen batteries | Faulty System | batt | Batteries | 325111 | GH-GHAZL-MAHLA | C1_3400DE_PH12 | Batteries | Item(s) stolen/Stolen Batteries
IM771697 | 3577UP | 2261_E_SG-NAZLET-ALI_3577UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 304210 | 01_S_SG-NAZLET-ALI_3577UP | C1_3577UP_PH14 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Power cable not protected and missing power gland
IM771697 | 3577UP | 2261_E_SG-NAZLET-ALI_3577UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 304210 | 01_S_SG-NAZLET-ALI_3577UP | C1_3577UP_PH14 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Power cable not protected and missing power gland
IM771697 | 3577UP | 2261_E_SG-NAZLET-ALI_3577UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 304210 | 01_S_SG-NAZLET-ALI_3577UP | C1_3577UP_PH14 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Battery cable not isolated
IM771697 | 3577UP | 2261_E_SG-NAZLET-ALI_3577UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 304210 | 01_S_SG-NAZLET-ALI_3577UP | C1_3577UP_PH14 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Battery cable not isolated
IM771697 | 3577UP | 2261_E_SG-NAZLET-ALI_3577UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 304210 | 01_S_SG-NAZLET-ALI_3577UP | C1_3577UP_PH14 | ATS / Engine | Item(s) stolen/Gen Missing battery
IM771697 | 3577UP | 2261_E_SG-NAZLET-ALI_3577UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 304210 | 01_S_SG-NAZLET-ALI_3577UP | C1_3577UP_PH14 | ATS / Engine | Item(s) stolen/Gen Missing battery
IM771697 | 3577UP | 2261_E_SG-NAZLET-ALI_3577UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 304210 | 01_S_SG-NAZLET-ALI_3577UP | C1_3577UP_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage around gen
IM771697 | 3577UP | 2261_E_SG-NAZLET-ALI_3577UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 304210 | 01_S_SG-NAZLET-ALI_3577UP | C1_3577UP_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage around gen
IM771697 | 3577UP | 2261_E_SG-NAZLET-ALI_3577UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 304210 | 01_S_SG-NAZLET-ALI_3577UP | C1_3577UP_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage from gen
IM771697 | 3577UP | 2261_E_SG-NAZLET-ALI_3577UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 304210 | 01_S_SG-NAZLET-ALI_3577UP | C1_3577UP_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage from gen
IM771697 | 3577UP | 2261_E_SG-NAZLET-ALI_3577UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 304210 | 01_S_SG-NAZLET-ALI_3577UP | C1_3577UP_PH14 | ATS / Engine | Panorama pictures for each system/Panorama
IM771697 | 3577UP | 2261_E_SG-NAZLET-ALI_3577UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 304210 | 01_S_SG-NAZLET-ALI_3577UP | C1_3577UP_PH14 | ATS / Engine | Panorama pictures for each system/Panorama
IM771717 | 0490SI | 03534_S_0490SI_IS-NASR | Power outage site has weak batteries and access PG problem recovered once power restored | Faulty System | batt | Batteries | 356007 | 01_S_IS-NASR_0490SI | C2_0490SI_PH14 | Rectifiers | Alarms reporting to the OMC/Rectifier alarm , A/C & door not apear on CAP
IM771717 | 0490SI | 03534_S_0490SI_IS-NASR | Power outage site has weak batteries and access PG problem recovered once power restored | Faulty System | batt | Batteries | 356007 | 01_S_IS-NASR_0490SI | C2_0490SI_PH14 | Batteries | Components faulty/Battery voltag reading drop to 46 volt after we disconnect th rectifier C.B (Check the batteries)
IM771738 | 3664DE | 1741_E_GH-KFR-HASHAD_3664DE | GN problem / weak batteries | Faulty System | batt | Batteries | 355453 | N_MILK-COMPANY_0251AL | C2_0251AL_PH3 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM771755 | 3684UP | 0471_G_SG-KOUM-ELARAB_3684UP | Due to EC power cutoff, weak batteries , Recovered | Faulty System | batt | Batteries | 324483 | 01_G_SG-KOUM-ELARAB_3684UP | C1_3684UP_PH15 | Batteries | Item(s) stolen/site batteries were Stolen
IM771842 | 0975UP | 0381_S_BS-MASID-ABYAD_0975UP_X | Due to EC power cutoff , Stolen batteries , Recovered | Faulty System | batt | Batteries | 356360 | 01_S_BS-MASID-ABYAD_0975UP | C1_0975UP_PH12 | Rectifiers | Alarms reporting to the OMC/Minor alarm doesn't appear on the OMC
IM771842 | 0975UP | 0381_S_BS-MASID-ABYAD_0975UP_X | Due to EC power cutoff , Stolen batteries , Recovered | Faulty System | batt | Batteries | 356360 | 01_S_BS-MASID-ABYAD_0975UP | C1_0975UP_PH12 | Batteries | Some parts are (missing / stolen)/Batteries and cables are stolen
IM771844 | 0587DE | 0221_S_DK-KFR-KURDI_0587DE | share VF / Main power / stolen batteries | Faulty System | batt | Batteries | 324791 | DK-KFR-KURDI | C9_0587DE_PH09 | Batteries | Item(s) stolen/No backup batteries.
IM771849 | 3784DE | 0661_S_KS-DAQLIT_3784DE | share VF / Main power / weak batteries | Faulty System | batt | Batteries | 335221 | KS-DAQLIT | C3_3784DE_PH14 | Batteries | Components faulty/Faulty battery (battearies are ballooned)
IM771895 | 3259DE | 0291_S_BH-ANAAM_3259DE | share VF / Main power / stolen batteries | Faulty System | batt | Batteries | 324534 | BH-ANAAM | C1_3259DE_PH12 | Batteries | Item(s) stolen/There is no battery for site
IM771896 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries , recovered | Faulty System | batt | Batteries | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | Batteries | Some parts are (missing / stolen)/Battery string stolen
IM771896 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries , recovered | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage
IM771896 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries , recovered | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Unit earth/Earth cable disconnected
IM771896 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries , recovered | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Components faulty/Generator indicator broken & not work
IM771896 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries , recovered | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Components faulty/Ventilation fan not work
IM771896 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries , recovered | Faulty System | DG | Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Power cable has no terminal
IM771897 | 0906DE | 691_S_KS-ANTRA-BAIDA_0906DE | main power / weak batteries | Faulty System | batt | Batteries | 324828 | LU-GZRT-BAIRAT | C1_4211UP_PH19 | Batteries | Item(s) stolen/Batteries were stolen
IM771902 | 0305UP | 01_S_AT-DEIR-MEHARA_0305UP | Due to EC power cutoff , weak batteries , PG Connected | Faulty System | batt | Batteries | 335158 | 01_S_AT-DEIR-MEHARA_0305UP | C1_0305UP_PH8 | Batteries | Components faulty/Fire panel was switched off
IM771976 | 0498RE | 03500_S_0498RE_SZ-SELIM-HAY | VFE power outage , dead batteries , recovered once power restored | Faulty System | batt | Batteries | 345366 | 01_S_SZ-SELIM-HAY_0498RE | C1_0498RE_PH17 | Batteries | Some parts are (missing / stolen)/Stolen battery
IM771992 | 3411UP | 0171_S_BS-DABAANA_3411UP_X | Due to EC power cutoff , weak batteries , PG Connected | Faulty System | batt | Batteries | 356314 | 01_S_BS-DABAANA_3411UP | C1_3411UP_PH14 | Rectifiers | Alarms reporting to the OMC/Loop on the minor alarm in DDF
IM772046 | 0673DE | 0871_H_MF-SEDOD_0673DE | Power/battery under investigation/connect P.G | Faulty System | batt | Batteries | 304302 | MF-SEDOD | C1_0673DE_PH9 | Batteries | Some parts are missing/Battery racks are placed directly under A/C IDU
IM772110 | 3830DE | 1311_S_BH-MHLT-KYL_3830DE | share VF / Main power / stolen batteries / PG handle another sites ( BH-KOM-DAFSHO_3803DE & BH-BARSIQ_3342DE ) | Faulty System | batt | Batteries | 356185 | BH-MHLT-KYL | C1_3830DE_PH14 | Batteries | Some parts are (missing / stolen)/No battery for site
IM772115 | 0127DE | 0061_H_GH-MRO4-QUTUR_0127DE | Main power @ GH-MRO4-QUTUR_0127DE / stolen batteries / PG connected | Faulty System | batt | Batteries | 304205 | 9_S_GH-MR04-QUTUR_0127DE_SS00 | C4_0127DE_PH2 | Batteries | Item(s) stolen/stolen batteries
IM772119 | 3394DE | 0011_S_B-SAFT-KHALED_3394DE | share VF / Main power / weak batteries | Faulty System | batt | Batteries | 304033 | BH-SAFT-KHALED | C1_3394DE_PH13 | Batteries | Components faulty/Faulty battery
IM772197 | 3431DE | 0001_D_DM-NEW-DUMYAT6_3431DE | ET GN problem / batteries under check / connect PG | Faulty System | batt | Batteries | 335138 | DM-NEW-DUMYAT6 | C1_3431DE_PH13 | Batteries | Some parts are missing/covers
IM772197 | 3431DE | 0001_D_DM-NEW-DUMYAT6_3431DE | ET GN problem / batteries under check / connect PG | Faulty System | GN | Generator | 335138 | DM-NEW-DUMYAT6 | C1_3431DE_PH13 | ATS / Engine | Components faulty/check genset
IM772197 | 3431DE | 0001_D_DM-NEW-DUMYAT6_3431DE | ET GN problem / batteries under check / connect PG | Faulty System | GN | Generator | 335138 | DM-NEW-DUMYAT6 | C1_3431DE_PH13 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM772205 | 0305UP | 01_S_AT-DEIR-MEHARA_0305UP | Due to EC power cutoff , weak batteries, PG Connected | Faulty System | batt | Batteries | 335158 | 01_S_AT-DEIR-MEHARA_0305UP | C1_0305UP_PH8 | Batteries | Components faulty/Fire panel was switched off
IM772253 | 0037SI | 01_H_SS-LIBEIRIQ_0037SI | DG Stopped , weak batteries caused site Down once DG Fix site recovered | Faulty System | DG | Generator | 304349 | 01_H_SS-LIBEIRIQ_0037SI | C1_0037SI_PH2 | ATS / Engine | Components faulty/Burnet ATS terminals
IM772253 | 0037SI | 01_H_SS-LIBEIRIQ_0037SI | DG Stopped , weak batteries caused site Down once DG Fix site recovered | Faulty System | DG | Generator | 304349 | 01_H_SS-LIBEIRIQ_0037SI | C1_0037SI_PH2 | ATS / Engine | Components faulty/Defected genset battery
IM772253 | 0037SI | 01_H_SS-LIBEIRIQ_0037SI | DG Stopped , weak batteries caused site Down once DG Fix site recovered | Faulty System | DG | Generator | 304349 | 01_H_SS-LIBEIRIQ_0037SI | C1_0037SI_PH2 | ATS / Engine | Components faulty/Broken control panel screen
IM772253 | 0037SI | 01_H_SS-LIBEIRIQ_0037SI | DG Stopped , weak batteries caused site Down once DG Fix site recovered | Faulty System | DG | Generator | 304349 | 01_H_SS-LIBEIRIQ_0037SI | C1_0037SI_PH2 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Bad fixation of fuel hose
IM772253 | 0037SI | 01_H_SS-LIBEIRIQ_0037SI | DG Stopped , weak batteries caused site Down once DG Fix site recovered | Faulty System | DG | Generator | 304349 | 01_H_SS-LIBEIRIQ_0037SI | C1_0037SI_PH2 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Bad termination of ATS panel
IM772253 | 0037SI | 01_H_SS-LIBEIRIQ_0037SI | DG Stopped , weak batteries caused site Down once DG Fix site recovered | Faulty System | DG | Generator | 304349 | 01_H_SS-LIBEIRIQ_0037SI | C1_0037SI_PH2 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Bad termination of charging system
IM772253 | 0037SI | 01_H_SS-LIBEIRIQ_0037SI | DG Stopped , weak batteries caused site Down once DG Fix site recovered | Faulty System | DG | Generator | 304349 | 01_H_SS-LIBEIRIQ_0037SI | C1_0037SI_PH2 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Genset oil & fuel leakage
IM772253 | 0037SI | 01_H_SS-LIBEIRIQ_0037SI | DG Stopped , weak batteries caused site Down once DG Fix site recovered | Faulty System | DG | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure
IM772253 | 0037SI | 01_H_SS-LIBEIRIQ_0037SI | DG Stopped , weak batteries caused site Down once DG Fix site recovered | Faulty System | DG | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Wrong connection/generator battery as used in the site and not suitable in High temp
IM772272 | 0498RE | 03500_S_0498RE_SZ-SELIM-HAY | VFE power outage , dead batteries , recovered once power restored | Faulty System | batt | Batteries | 345366 | 01_S_SZ-SELIM-HAY_0498RE | C1_0498RE_PH17 | Batteries | Some parts are (missing / stolen)/Stolen battery
IM772279 | 0278CA | 02185_N_0278CA_ABBOUD | down due to power probelm @ 0278CA_ABBOUD and battery weak | Faulty System | batt | Batteries | 304055 | ABBOUD | C1_0278CA_PH3 | Batteries | Item(s) stolen/Batteries and cables are stolen
IM772288 | 3499UP | 1871_S_AS-GAFAR-SADK_3499UP_X | Main Power Disconenction,Stolen Batteries, Autorecovered. | Faulty System | batt | Batteries | 356189 | 01_S_AS-GAFAR-SADK_3499UP | C1_3499UP_PH14 | Batteries | Some parts are (missing / stolen)/Site Batteries were stolen
IM772313 | 3181DE | 03323_D_3181DE_QL-QALIUB-RLWY | GN problem/battery under invistigation/clear after check GN | Faulty System | batt | Batteries | 303916 | QL_QALIUB_RLWY _3181DE_SSS0 | C1_3181DE_PH12 | Batteries | Item(s) stolen/stolen batteries
IM772313 | 3181DE | 03323_D_3181DE_QL-QALIUB-RLWY | GN problem/battery under invistigation/clear after check GN | Faulty System | GN | Generator | 303916 | QL_QALIUB_RLWY _3181DE_SSS0 | C1_3181DE_PH12 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/arrange
IM772336 | 0734DE | 0441_D_MF-TANTA-HW1_0734DE | GN problem / Stolen batteries | Faulty System | batt | Batteries | 356142 | MF-TANTA-HW1 | C1_0734DE_PH9 | Rectifiers | Alarms reporting to the OMC/Site has fake power alarm
IM772336 | 0734DE | 0441_D_MF-TANTA-HW1_0734DE | GN problem / Stolen batteries | Faulty System | batt | Batteries | 356142 | MF-TANTA-HW1 | C1_0734DE_PH9 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM772336 | 0734DE | 0441_D_MF-TANTA-HW1_0734DE | GN problem / Stolen batteries | Faulty System | GN | Generator | 356142 | MF-TANTA-HW1 | C1_0734DE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has leakage
IM772352 | 3275DE | 1151_S_QL-DEER-2_3275DE | Main power/weak battery@ QL-DEER-2_3275DE/clear after power back | Faulty System | batt | Batteries | 356318 | QL-DEER-2 | C1_3275DE_PH12 | Rectifiers | Alarms reporting to the OMC/Alarm cable disconnected (Alarms not appear at OMC)
IM772352 | 3275DE | 1151_S_QL-DEER-2_3275DE | Main power/weak battery@ QL-DEER-2_3275DE/clear after power back | Faulty System | batt | Batteries | 356318 | QL-DEER-2 | C1_3275DE_PH12 | Batteries | Components faulty/Faulty battaries
IM772363 | 3555CA | 00042_L_3555CA_SAMA-TOWER | down due to DG problem and no backup (MA) | Faulty System | backup | Batteries | 345256 | SAMA-TOWER | C2_3555CA_PH13 | Batteries | Some parts are missing/missing batteries
IM772363 | 3555CA | 00042_L_3555CA_SAMA-TOWER | down due to DG problem and no backup (MA) | Faulty System | DG | Generator | 345256 | SAMA-TOWER | C2_3555CA_PH13 | ATS / Engine | Wrong connection/welded cables
IM772363 | 3555CA | 00042_L_3555CA_SAMA-TOWER | down due to DG problem and no backup (MA) | Faulty System | DG | Generator | 345256 | SAMA-TOWER | C2_3555CA_PH13 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage
IM772476 | 0581DE | 1571_S_SK-IKYAD-BHARIA_0581DE | Main power/stolen battery@SK-IKYAD-BHARIA_0581DE/clear on P.G | Faulty System | batt | Batteries | 324498 | SK-IKYAD-BHARIA | C1_0581DE_PH9 | Batteries | Item(s) stolen/No backup batteries.
IM772479 | 3489DE | 0461_S_DK-KFR-GHANNAM_3489DE | Main power/stolen battery/clear after power back | Faulty System | batt | Batteries | 325088 | DK-KFR-GHANNAM | C1-3489DE-PH13 | Batteries | Item(s) stolen/No backup batteries.
IM772492 | 3499UP | 1871_S_AS-GAFAR-SADK_3499UP_X | Main Power Disconnection, weak batteries, PG Connected. | Faulty System | batt | Batteries | 356189 | 01_S_AS-GAFAR-SADK_3499UP | C1_3499UP_PH14 | Batteries | Some parts are (missing / stolen)/Site Batteries were stolen
IM772520 | 3895DE | 0401_S_BH-KFR-ZYADA_3895DE | Share VF / VG GN problem / stolen batteries | Faulty System | batt | Batteries | 324442 | BH-KFR-ZYADA | C1_3895DE_PH14 | Batteries | Item(s) stolen/There is no battery for site
IM772531 | 0156UP | 01_J_GIZA-LUXOR-25_0156UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 335205 | 01_C_GIZA-LUXOR-25_0156UP | C1_0156UP_PH3 | ATS / Engine | Components faulty/Gen enclosure battery was faulty
IM772531 | 0156UP | 01_J_GIZA-LUXOR-25_0156UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 335205 | 01_C_GIZA-LUXOR-25_0156UP | C1_0156UP_PH3 | ATS / Engine | Components faulty/Gen enclosure battery was faulty
IM772531 | 0156UP | 01_J_GIZA-LUXOR-25_0156UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 335205 | 01_C_GIZA-LUXOR-25_0156UP | C1_0156UP_PH3 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/ATS cables need organization
IM772531 | 0156UP | 01_J_GIZA-LUXOR-25_0156UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 335205 | 01_C_GIZA-LUXOR-25_0156UP | C1_0156UP_PH3 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/ATS cables need organization
IM772531 | 0156UP | 01_J_GIZA-LUXOR-25_0156UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 335205 | 01_C_GIZA-LUXOR-25_0156UP | C1_0156UP_PH3 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Loose neutral cable
IM772531 | 0156UP | 01_J_GIZA-LUXOR-25_0156UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 335205 | 01_C_GIZA-LUXOR-25_0156UP | C1_0156UP_PH3 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Loose neutral cable
IM772531 | 0156UP | 01_J_GIZA-LUXOR-25_0156UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 335205 | 01_C_GIZA-LUXOR-25_0156UP | C1_0156UP_PH3 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Two cables inserted in one slot and not teminated can cause bad connections
IM772531 | 0156UP | 01_J_GIZA-LUXOR-25_0156UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 335205 | 01_C_GIZA-LUXOR-25_0156UP | C1_0156UP_PH3 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Two cables inserted in one slot and not teminated can cause bad connections
IM772531 | 0156UP | 01_J_GIZA-LUXOR-25_0156UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 335205 | 01_C_GIZA-LUXOR-25_0156UP | C1_0156UP_PH3 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage inside Gen enclosure
IM772531 | 0156UP | 01_J_GIZA-LUXOR-25_0156UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 335205 | 01_C_GIZA-LUXOR-25_0156UP | C1_0156UP_PH3 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage inside Gen enclosure
IM772531 | 0156UP | 01_J_GIZA-LUXOR-25_0156UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 335205 | 01_C_GIZA-LUXOR-25_0156UP | C1_0156UP_PH3 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage
IM772531 | 0156UP | 01_J_GIZA-LUXOR-25_0156UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 335205 | 01_C_GIZA-LUXOR-25_0156UP | C1_0156UP_PH3 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage
IM772531 | 0156UP | 01_J_GIZA-LUXOR-25_0156UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 335205 | 01_C_GIZA-LUXOR-25_0156UP | C1_0156UP_PH3 | ATS / Engine | Panorama pictures for each system/Last gen hour meter at Audit G ( 6762 )
IM772531 | 0156UP | 01_J_GIZA-LUXOR-25_0156UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 335205 | 01_C_GIZA-LUXOR-25_0156UP | C1_0156UP_PH3 | ATS / Engine | Panorama pictures for each system/Last gen hour meter at Audit G ( 6762 )
IM772531 | 0156UP | 01_J_GIZA-LUXOR-25_0156UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 335205 | 01_C_GIZA-LUXOR-25_0156UP | C1_0156UP_PH3 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM772531 | 0156UP | 01_J_GIZA-LUXOR-25_0156UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 335205 | 01_C_GIZA-LUXOR-25_0156UP | C1_0156UP_PH3 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM772531 | 0156UP | 01_J_GIZA-LUXOR-25_0156UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure
IM772531 | 0156UP | 01_J_GIZA-LUXOR-25_0156UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure
IM772531 | 0156UP | 01_J_GIZA-LUXOR-25_0156UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Wrong connection/generator battery as used in the site and not suitable in High temp
IM772531 | 0156UP | 01_J_GIZA-LUXOR-25_0156UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Wrong connection/generator battery as used in the site and not suitable in High temp
IM772563 | 3628DE | 0811_S_GH-QSR-BAGHDAD_3628DE | main power / stolen batteries / PG connected | Faulty System | batt | Batteries | 324836 | GH-QSR-BAGHDAD | C2_3628DE_PH13 | Batteries | Item(s) stolen/Stolen batteries
IM772564 | 3124UP | 1761_S_AS-SILWA-BHRY_3124UP_X | Main Power Disconnection, Stolen Batteries, Autorecovered. | Faulty System | batt | Batteries | 355937 | 01_S_AS-SILWA-BHRY_3124UP | C1_3124UP_PH13 | Rectifiers | Alarms reporting to the OMC/Rectifer minor alarm is not appeared on the omc and looped
IM772575 | 3394DE | 0011_S_B-SAFT-KHALED_3394DE | Share VF / main power / weak batteries / PG connected | Faulty System | batt | Batteries | 304033 | BH-SAFT-KHALED | C1_3394DE_PH13 | Batteries | Components faulty/Faulty battery
IM772605 | 0391RE | 03496_S_0391RE_SZ-AAMER | Power outage site has weak batteries and access PG problem recovered once power restored | Faulty System | batt | Batteries | 356056 | 01_S_SZ-AAMER_0391RE | C1_0391RE_PH15 | Rectifiers | Alarms reporting to the OMC/Rectifier major alarm not report the OMC & Cable looped in DDF
IM772619 | 0238RE | 03882_S_0238RE_RS-RSRT-GHALEB | Power outage site has weak batteries and access PG problem recovered once power restored | Faulty System | batt | Batteries | 355503 | 01_S_RS-RSRT-GHALEB_0238RE | C2_0238RE_PH9 | Rectifiers | Alarms reporting to the OMC/Rectifer alarm not appeared on the omc ( looped at ddf rack alarm not connected at ddf )
IM772619 | 0238RE | 03882_S_0238RE_RS-RSRT-GHALEB | Power outage site has weak batteries and access PG problem recovered once power restored | Faulty System | batt | Batteries | 355503 | 01_S_RS-RSRT-GHALEB_0238RE | C2_0238RE_PH9 | Rectifiers | Alarms reporting to the OMC/Rectifer alarm not appeared on the omc ( looped at ddf rack alarm not connected at ddf )
IM772619 | 0238RE | 03882_S_0238RE_RS-RSRT-GHALEB | Power outage site has weak batteries and access PG problem recovered once power restored | Faulty System | batt | Batteries | 355503 | 01_S_RS-RSRT-GHALEB_0238RE | C2_0238RE_PH9 | Batteries | Components faulty/Batteries were faulty ( explosion )
IM772623 | 0638UP | 0491_G_QN-MOSALA_0638UP | Genertaor problem, stolen Batteries, solved. | Faulty System | batt | Batteries | 324745 | 01_G_QN-MOSALA_0638UP | C4_0638UP_PH9 | Batteries | Item(s) stolen/Batteries were stolen
IM772623 | 0638UP | 0491_G_QN-MOSALA_0638UP | Genertaor problem, stolen Batteries, solved. | Faulty System | Gen | Generator | 324745 | 01_G_QN-MOSALA_0638UP | C4_0638UP_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage beside enclosure by Vodafone
IM772653 | 3076DE | 0321_S_DK-MIT-ASEM_3076DE | Share VF / Main power / stolen batteries | Faulty System | batt | Batteries | 324790 | DK_Mit_Asem | C1_3076DE_PH11 | Batteries | Item(s) stolen/No backup batteries.
IM772658 | 0576DE | 1611_G_BH-WAFAIYYA_0576DE | Main power / stolen batteries | Faulty System | batt | Batteries | 324440 | BH-WAFAIYYA | C2_0576DE_PH9 | Batteries | Item(s) stolen/There is no battery for site
IM772660 | 3344DE | 0681_S_BH-ELNEGILY_3344DE | Access VF / Main power /VF Guard switched off MCB / stolen batteries | Faulty System | batt | Batteries | 304214 | BH-ELNEGILY | C3_3344DE_PH12 | Batteries | Item(s) stolen/There is no battery for site
IM772690 | 0305UP | 01_S_AT-DEIR-MEHARA_0305UP | Due to EC power cutoff , weak batteries , PG Connected | Faulty System | batt | Batteries | 335158 | 01_S_AT-DEIR-MEHARA_0305UP | C1_0305UP_PH8 | Batteries | Components faulty/Fire panel was switched off
IM772692 | 3873UP | 671_S_LU-TIBA-CITY-2_3873UP | Generator problem, weak Batteries, solved. | Faulty System | batt | Batteries | 324438 | LU-TIBA-CITY-2 | C1_3873UP_PH15 | Batteries | Item(s) stolen/Batteries were stolen
IM772692 | 3873UP | 671_S_LU-TIBA-CITY-2_3873UP | Generator problem, weak Batteries, solved. | Faulty System | batt | Batteries | 324438 | LU-TIBA-CITY-2 | C1_3873UP_PH15 | Batteries | Item(s) stolen/Batteries were stolen ( missing )
IM772692 | 3873UP | 671_S_LU-TIBA-CITY-2_3873UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 324438 | LU-TIBA-CITY-2 | C1_3873UP_PH15 | ATS / Engine | Wrong connection/Main cables were welded inside ATS panel
IM772692 | 3873UP | 671_S_LU-TIBA-CITY-2_3873UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 324438 | LU-TIBA-CITY-2 | C1_3873UP_PH15 | ATS / Engine | Wrong connection/Main cables were welded inside ATS panel
IM772692 | 3873UP | 671_S_LU-TIBA-CITY-2_3873UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 324438 | LU-TIBA-CITY-2 | C1_3873UP_PH15 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM wrong penetration/Wrong penetration for power cables
IM772692 | 3873UP | 671_S_LU-TIBA-CITY-2_3873UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 324438 | LU-TIBA-CITY-2 | C1_3873UP_PH15 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM wrong penetration/Wrong penetration for power cables
IM772692 | 3873UP | 671_S_LU-TIBA-CITY-2_3873UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 324438 | LU-TIBA-CITY-2 | C1_3873UP_PH15 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Two cables inserted in one slot can cause bad connections
IM772692 | 3873UP | 671_S_LU-TIBA-CITY-2_3873UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 324438 | LU-TIBA-CITY-2 | C1_3873UP_PH15 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Two cables inserted in one slot can cause bad connections
IM772692 | 3873UP | 671_S_LU-TIBA-CITY-2_3873UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 324438 | LU-TIBA-CITY-2 | C1_3873UP_PH15 | ATS / Engine | Item(s) stolen/Gen Battery is missing
IM772692 | 3873UP | 671_S_LU-TIBA-CITY-2_3873UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 324438 | LU-TIBA-CITY-2 | C1_3873UP_PH15 | ATS / Engine | Item(s) stolen/Gen Battery is missing
IM772692 | 3873UP | 671_S_LU-TIBA-CITY-2_3873UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 324438 | LU-TIBA-CITY-2 | C1_3873UP_PH15 | ATS / Engine | Panorama pictures for each system/Last Gen hour meter at hour meter at Audit G ( 5751 )
IM772692 | 3873UP | 671_S_LU-TIBA-CITY-2_3873UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 324438 | LU-TIBA-CITY-2 | C1_3873UP_PH15 | ATS / Engine | Panorama pictures for each system/Last Gen hour meter at hour meter at Audit G ( 5751 )
IM772692 | 3873UP | 671_S_LU-TIBA-CITY-2_3873UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 324438 | LU-TIBA-CITY-2 | C1_3873UP_PH15 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM772692 | 3873UP | 671_S_LU-TIBA-CITY-2_3873UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 324438 | LU-TIBA-CITY-2 | C1_3873UP_PH15 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM772780 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | batt | Batteries | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | Batteries | Item(s) stolen/Batteries were stolen
IM772780 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Wrong connection/external cable to the guard connected from gen and not protected
IM772780 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Wrong connection/external cable to the guard connected from gen and not protected
IM772780 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Wrong connection/One Contactor turned on by setting wood inside it
IM772780 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Wrong connection/One Contactor turned on by setting wood inside it
IM772780 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cables not protected in tube
IM772780 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cables not protected in tube
IM772780 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cables not protected
IM772780 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cables not protected
IM772780 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Item(s) stolen/Gen battery is missing
IM772780 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Item(s) stolen/Gen battery is missing
IM772780 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/ Fuel leakage inside Gen
IM772780 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/ Fuel leakage inside Gen
IM772780 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage inside Gen
IM772780 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage inside Gen
IM772780 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage beisde Gen enclosure area need cleaning
IM772780 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage beisde Gen enclosure area need cleaning
IM772780 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Panorama pictures for each system/Open gland in Gen enclosure need insulation
IM772780 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Panorama pictures for each system/Open gland in Gen enclosure need insulation
IM772780 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM772780 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM772780 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Panorama pictures for each system/Last Gen hour meter at Audit G ( 31148 )
IM772780 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Panorama pictures for each system/Last Gen hour meter at Audit G ( 31148 )
IM772813 | 0736CA | 02118_D_0736CA_PETROL-PIPELINS | down due to DG filter problem and stolen batteries | Faulty System | batt | Batteries | 356154 | PETROL-PIPELINS | C2_0736CA_PH9 | Batteries | Some parts are (missing / stolen)/Batteries and cables are stolen
IM772813 | 0736CA | 02118_D_0736CA_PETROL-PIPELINS | down due to DG filter problem and stolen batteries | Faulty System | DG | Generator | 356154 | PETROL-PIPELINS | C2_0736CA_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Signs of oil and fuel leakage arround the genset
IM772813 | 0736CA | 02118_D_0736CA_PETROL-PIPELINS | down due to DG filter problem and stolen batteries | Faulty System | DG | Generator | 356154 | PETROL-PIPELINS | C2_0736CA_PH9 | ATS / Engine | Unit earth/Stolen earth connections of the ATS panel
IM772813 | 0736CA | 02118_D_0736CA_PETROL-PIPELINS | down due to DG filter problem and stolen batteries | Faulty System | DG | Generator | 356154 | PETROL-PIPELINS | C2_0736CA_PH9 | ATS / Engine | Components faulty/White exhaust of the engine
IM772813 | 0736CA | 02118_D_0736CA_PETROL-PIPELINS | down due to DG filter problem and stolen batteries | Faulty System | DG | Generator | 356154 | PETROL-PIPELINS | C2_0736CA_PH9 | ATS / Engine | Wrong connection/Wrong connections of cables connected to the ATS trans.
IM772813 | 0736CA | 02118_D_0736CA_PETROL-PIPELINS | down due to DG filter problem and stolen batteries | Faulty System | DG | Generator | 356154 | PETROL-PIPELINS | C2_0736CA_PH9 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Missing terminals of power cables connected to the ATS contactors
IM772869 | 0421DE | 0721_H_MF-MANSH-SOLTN_0421DE | Main power/battery under investigation/clear after power back | Faulty System | batt | Batteries | 304300 | MF-MANSH-SOLTN | C1_0421DE_PH4 | Batteries | Some parts are missing/Battery racks are placed directly under A/C IDU
IM772910 | 3548DE | 1391_S_GH-SANADID_3548DE | Main power/stolen battery/clear on P.G | Faulty System | batt | Batteries | 325091 | GH-SANADID | C2_3548DE_PH16 | Batteries | Item(s) stolen/No battery for site
IM772960 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN problem/stolen battery/clear after check GN | Faulty System | batt | Batteries | 324500 | SK-AZZAZI | C1_4029DE_PH15 | Batteries | Item(s) stolen/No backup batteries.
IM772960 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN problem/stolen battery/clear after check GN | Faulty System | GN | Generator | 324500 | SK-AZZAZI | C1_4029DE_PH15 | ATS / Engine | Wrong connection/Some cables are disconnected and need adjust.
IM772960 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN problem/stolen battery/clear after check GN | Faulty System | GN | Generator | 324500 | SK-AZZAZI | C1_4029DE_PH15 | ATS / Engine | Panorama pictures for each system/Generator battery poles need cleaning, wax and covers.
IM772960 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN problem/stolen battery/clear after check GN | Faulty System | GN | Generator | 324500 | SK-AZZAZI | C1_4029DE_PH15 | ATS / Engine | Panorama pictures for each system/Overview.
IM772962 | 3037DE | 0301_D_DK-BAGALAT_3037DE | ET Share / GN stopped / Stolen batteries | Faulty System | batt | Batteries | 345376 | DK-BAGALAT | C3_3037DE_PH11 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM772962 | 3037DE | 0301_D_DK-BAGALAT_3037DE | ET Share / GN stopped / Stolen batteries | Faulty System | GN | Generator | 345376 | DK-BAGALAT | C3_3037DE_PH11 | ATS / Engine | Components faulty/Control module has faulty buttons.
IM772962 | 3037DE | 0301_D_DK-BAGALAT_3037DE | ET Share / GN stopped / Stolen batteries | Faulty System | GN | Generator | 345376 | DK-BAGALAT | C3_3037DE_PH11 | ATS / Engine | Wrong connection/Cable has bad connections and need replacement.
IM772997 | 3955DE | 0731_S_SK-QRMT-SAHBRA_3955DE | access ET/ET GN problem/Stolen batteries | Faulty System | batt | Batteries | 356230 | SK-QRMT-SAHBRA | C1_3955DE_PH15 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM773002 | 0615AL | 1381_S_NZHA-TERMINAL_0615AL | Down Due To Main Power Cutoff / Weak Batteries / On Air After Main Power Auto Recovered | Faulty System | batt | Batteries | 356028 | MF-TELYA | C4_0674DE_PH09 | Rectifiers | Alarms reporting to the OMC/Site down due to power during visite (Check alarms with OMC with capture)
IM773004 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/stolen battery/clear after check GN | Faulty System | batt | Batteries | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | Batteries | Some parts are missing/Battery cabinet need cleaning (from inside) and holes need sealing.
IM773004 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/stolen battery/clear after check GN | Faulty System | batt | Batteries | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | Batteries | Some parts are missing/Batteries poles need have missing covers.
IM773004 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/stolen battery/clear after check GN | Faulty System | GN | Generator | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | ATS / Engine | Components faulty/Generator has bad performance and need overall.
IM773004 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/stolen battery/clear after check GN | Faulty System | GN | Generator | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | ATS / Engine | Panorama pictures for each system/Overview.
IM773030 | 0070SI | 01_S_SS-SAINT-CATRN_0070SI | Power outage site has weak batteries and access PG problem recovered once power restored | Faulty System | batt | Batteries | 356151 | 01_S_SS-SAINT-CATRN_0070SI | C2_0070SI_PH2 | Rectifiers | Alarms reporting to the OMC/rectifier major alarm appears
IM773054 | 0509SI | U_S_0509SI_IS-NEW-MAHSAMA | Power outage , site has weak batteries must replace with another new team moved with PG , before arrive site recovered once power restored | Faulty System | batt | Batteries | 356269 | 01_S_IS-NEW-MAHSAMA_0509SI | C1_0509SI_PH15 | Batteries | Some parts are (missing / stolen)/Battery string stolen
IM773103 | 0983DE | 1771_S_DK-MIT-ANTAR_0983DE | H.T alarm / BTS hanging | Faulty System | H.T | A/Cs | 324896 | DK-MIT-ANTAR | C8_0983DE_PH11 | A/Cs Cooling / Free Cooling / Ventilation | Components faulty/faulty , need to rest it control each time to work
IM773105 | 0498CA | 01846_S_0498CA_GHAMRA | down due to power failure and weak batteries and auto restored(M) | Faulty System | batt | Batteries | 324428 | GHAMRA | C2_0498CA_PH4 | Batteries | Some parts are missing/Missing hoods of batteries
IM773125 | 3594DE | 1241_S_BH-TAYRIYA_3594DE | main power/Stolen batteries/clear on PG | Faulty System | batt | Batteries | 325119 | BH-TAYRIYA | C1-3594DE-PH13 | Batteries | Item(s) stolen/There is no battery for site
IM773198 | 0070UP | 01_J_QN-HAMMADI-NTH_0070UP | Generator problem, weak Batteries, TV station access problem | Faulty System | Gen | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure
IM773198 | 0070UP | 01_J_QN-HAMMADI-NTH_0070UP | Generator problem, weak Batteries, TV station access problem | Faulty System | generator | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure
IM773198 | 0070UP | 01_J_QN-HAMMADI-NTH_0070UP | Generator problem, weak Batteries, TV station access problem | Faulty System | Gen | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Wrong connection/generator battery as used in the site and not suitable in High temp
IM773198 | 0070UP | 01_J_QN-HAMMADI-NTH_0070UP | Generator problem, weak Batteries, TV station access problem | Faulty System | generator | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Wrong connection/generator battery as used in the site and not suitable in High temp
IM773204 | 0456UP | 02_S_QN-TOWAYRAT_0456UP | Main power disconnection ,batteries are suspected to be weak , P.G connected | Faulty System | batt | Batteries | 356277 | 01_S_QN-TOWAYRAT_0456UP | C1_0456UP_PH9 | Rectifiers | Alarms reporting to the OMC/Alarm was exists on rectifier control panel and appeared on the Omc to
IM773335 | 3368DE | 0201_S_BH-ABO-SHIQAF_3368DE | Access VF / Main power / stolen batteries / PG handle anther sites ( BH-ABO-REESH_3064DE & BH-SHUBRA-NUNA_0048DE ) | Faulty System | batt | Batteries | 324904 | BH-ABO-SHIQAF | C1_3368DE_PH12 | Batteries | Item(s) stolen/There is no battery for site
IM773351 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Main power / stolen batteries | Faulty System | batt | Batteries | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | Batteries | Item(s) stolen/Stolen
IM773442 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem and battery stolen and PG access | Faulty System | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | Batteries | Some parts are (missing / stolen)/missing battereis
IM773470 | 3110DE | 1681_D_GH-SHUBRA-RIS_3110DE | Share VF / VF GN problem @ GH-SHUBRA-RIS_3110DE / weak batteries | Faulty System | GN | Generator | 324613 | GH-SHUBRA-RIS | C1_3110DE_PH12 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM773472 | 0350DE | 1271_Q_BH-BADR_0350DE | access guard/GN problem/batteries under investigation@BH-BADR_0350DE | Faulty System | GN | Generator | 304087 | BH-BADR | C3_0350DE_PH4 | ATS / Engine | Components below rate (excluding main power feeder if not hot)/Generator voltage is high
IM773472 | 0350DE | 1271_Q_BH-BADR_0350DE | access guard/GN problem/batteries under investigation@BH-BADR_0350DE | Faulty System | GN | Generator | 304087 | BH-BADR | C3_0350DE_PH4 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/Disconnected cables
IM773472 | 0350DE | 1271_Q_BH-BADR_0350DE | access guard/GN problem/batteries under investigation@BH-BADR_0350DE | Faulty System | GN | Generator | 304087 | BH-BADR | C3_0350DE_PH4 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM wrong penetration/CB need fixation
IM773472 | 0350DE | 1271_Q_BH-BADR_0350DE | access guard/GN problem/batteries under investigation@BH-BADR_0350DE | Faulty System | GN | Generator | 304087 | BH-BADR | C3_0350DE_PH4 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals requried
IM773472 | 0350DE | 1271_Q_BH-BADR_0350DE | access guard/GN problem/batteries under investigation@BH-BADR_0350DE | Faulty System | GN | Generator | 304087 | BH-BADR | C3_0350DE_PH4 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Burned terminal // Terminals at 1 slot
IM773522 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to DG problem and battery stolen and PG accessed | Faulty System | batt | Batteries | 314391 | REHAB-G17 | C1_3492CA_PH13 | Batteries | Some parts are missing/missing batteries
IM773522 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to DG problem and battery stolen and PG accessed | Faulty System | DG | Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | ATS / Engine | Wrong connection/wrong connection
IM773561 | 0993UP | 0041_S_AT-ELOUNA_0993UP | Due to EC power cutoff , Weak batteries , PG Connected | Faulty System | batt | Batteries | 355474 | 01_S_AT-ELOUNA_0993UP | C1_0993UP_PH12 | Rectifiers | Alarms reporting to the OMC/Power alarm not appeared on the omc
IM773630 | 3575DE | 1701_S_BH-NKHLA-BHRYA_3575DE | Main power / batteries under check | Faulty System | batt | Batteries | 356088 | BH-NKHLA-BHRYA | C1_3575DE_PH13 | Batteries | Components faulty/Battery CBs off
IM773769 | 3290DE | 1171_D_MF-QATTA_3290DE | acess Guard/GN problem /Good batteries/clear after check GN | Faulty System | GN | Generator | 355961 | MF-QATTA | C3_3290DE_PH12 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has leakage
IM773769 | 3290DE | 1171_D_MF-QATTA_3290DE | acess Guard/GN problem /Good batteries/clear after check GN | Faulty System | GN | Generator | 355961 | MF-QATTA | C3_3290DE_PH12 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminals requried
IM773769 | 3290DE | 1171_D_MF-QATTA_3290DE | acess Guard/GN problem /Good batteries/clear after check GN | Faulty System | GN | Generator | 355961 | MF-QATTA | C3_3290DE_PH12 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Cable need to be terminated well
IM773787 | 0633AL | B_ALEX-WST-1_1_33866_G | gen problem / stolen batteries / solved . | Faulty System | batt | Batteries | 355459 | ALEX-WST-1 | C1_0633AL_PH13 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM773787 | 0633AL | B_ALEX-WST-1_1_33866_G | gen problem / stolen batteries / solved . | Faulty System | Gen | Generator | 355459 | ALEX-WST-1 | C1_0633AL_PH13 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator and its area has a lot of leakage.
IM773799 | 3436UP | 1071_S_MN-MYANA-WAQF_3436UP | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 324959 | 01_S_MN-MYANA-WAQF_3436UP | C2_3436UP_PH14 | ATS / Engine | Wrong connection/Gen working without control and protection
IM773799 | 3436UP | 1071_S_MN-MYANA-WAQF_3436UP | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 324959 | 01_S_MN-MYANA-WAQF_3436UP | C2_3436UP_PH14 | ATS / Engine | Wrong connection/Gen working without control and protection
IM773799 | 3436UP | 1071_S_MN-MYANA-WAQF_3436UP | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 324959 | 01_S_MN-MYANA-WAQF_3436UP | C2_3436UP_PH14 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Battery cables not isolated
IM773799 | 3436UP | 1071_S_MN-MYANA-WAQF_3436UP | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 324959 | 01_S_MN-MYANA-WAQF_3436UP | C2_3436UP_PH14 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Battery cables not isolated
IM773799 | 3436UP | 1071_S_MN-MYANA-WAQF_3436UP | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 324959 | 01_S_MN-MYANA-WAQF_3436UP | C2_3436UP_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage around Gen set from ET
IM773799 | 3436UP | 1071_S_MN-MYANA-WAQF_3436UP | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 324959 | 01_S_MN-MYANA-WAQF_3436UP | C2_3436UP_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage around Gen set from ET
IM773799 | 3436UP | 1071_S_MN-MYANA-WAQF_3436UP | Due to Generator problem , weak batteries , Recovered | Faulty System | Gen | Generator | 324959 | 01_S_MN-MYANA-WAQF_3436UP | C2_3436UP_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage from oil filler cap
IM773799 | 3436UP | 1071_S_MN-MYANA-WAQF_3436UP | Due to Generator problem , weak batteries , Recovered | Faulty System | generator | Generator | 324959 | 01_S_MN-MYANA-WAQF_3436UP | C2_3436UP_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage from oil filler cap
IM773831 | 0673DE | 0871_H_MF-SEDOD_0673DE | main power/Batteries under investigation/clear after connect P.G | Faulty System | batt | Batteries | 304302 | MF-SEDOD | C1_0673DE_PH9 | Batteries | Some parts are missing/Battery racks are placed directly under A/C IDU
IM773855 | 4021DE | 0181_S_BH-ABQAEEN_4021DE | Access VF / Main power / stolen batteries / PG handle anther sites ( BH-ABO-REESH_3064DE & BH-SHUBRA-NUNA_0048DE ) | Faulty System | batt | Batteries | 304224 | BH-ABQAEEN | C1_4021DE_PH15 | Batteries | Item(s) stolen/There is no battery for site
IM773880 | 3628DE | 0811_S_GH-QSR-BAGHDAD_3628DE | BTS problem / Down after AP 358492 / O&M disconnected / then Main power / Stolen batteries / PG connected | Faulty System | batt | Batteries | 324836 | GH-QSR-BAGHDAD | C2_3628DE_PH13 | Batteries | Item(s) stolen/Stolen batteries
IM773912 | 3955DE | 0731_S_SK-QRMT-SAHBRA_3955DE | Access ET. / ET. GN. Problem / stolen batteries / clear after checking ET. GN. | Faulty System | batt | Batteries | 356230 | SK-QRMT-SAHBRA | C1_3955DE_PH15 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM773916 | 0456UP | 02_S_QN-TOWAYRAT_0456UP | main Power Disconnection, weak Batteries, PG Connected. | Faulty System | batt | Batteries | 356277 | 01_S_QN-TOWAYRAT_0456UP | C1_0456UP_PH9 | Rectifiers | Alarms reporting to the OMC/Alarm was exists on rectifier control panel and appeared on the Omc to
IM773934 | 0975UP | 0381_S_BS-MASID-ABYAD_0975UP_X | Due to EC power cutoff , Stolen batteries , PG Connected | Faulty System | batt | Batteries | 356360 | 01_S_BS-MASID-ABYAD_0975UP | C1_0975UP_PH12 | Rectifiers | Alarms reporting to the OMC/Minor alarm doesn't appear on the OMC
IM773934 | 0975UP | 0381_S_BS-MASID-ABYAD_0975UP_X | Due to EC power cutoff , Stolen batteries , PG Connected | Faulty System | batt | Batteries | 356360 | 01_S_BS-MASID-ABYAD_0975UP | C1_0975UP_PH12 | Batteries | Some parts are (missing / stolen)/Batteries and cables are stolen
IM773939 | 3895DE | 0401_S_BH-KFR-ZYADA_3895DE | Share VF / VF GN problem / stolen batteries | Faulty System | batt | Batteries | 324442 | BH-KFR-ZYADA | C1_3895DE_PH14 | Batteries | Item(s) stolen/There is no battery for site
IM773940 | 0674DE | 1381_S_MF-TELYA_0674DE | Access VF. / main power/ batteries under investigation @ L_G_MF-TELYA_0674DE/ clear on PG. | Faulty System | batt | Batteries | 356028 | MF-TELYA | C4_0674DE_PH09 | Rectifiers | Alarms reporting to the OMC/Site down due to power during visite (Check alarms with OMC with capture)
IM773987 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Share VF / VF GN problem / stolen batteries | Faulty System | batt | Batteries | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | Batteries | Item(s) stolen/Stolen
IM773987 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Share VF / VF GN problem / stolen batteries | Faulty System | GN | Generator | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | ATS / Engine | Item(s) stolen/missing battery
IM773987 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Share VF / VF GN problem / stolen batteries | Faulty System | GN | Generator | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage
IM773993 | 3414UP | 0401_S_BS-AHWA_3414UP_X | Due to EC power cutoff , weak batteries , PG Connected | Faulty System | batt | Batteries | 356350 | 01_S_BS-AHWA_3414UP | C1_3414UP_PH14 | Rectifiers | Alarms reporting to the OMC/Loop on the major alarm in DDF
IM773993 | 3414UP | 0401_S_BS-AHWA_3414UP_X | Due to EC power cutoff , weak batteries , PG Connected | Faulty System | batt | Batteries | 356350 | 01_S_BS-AHWA_3414UP | C1_3414UP_PH14 | Batteries | Components faulty/Batteries are faulty and site is down after less than one hour of power disconnected
IM773995 | 3836DE | 0661_S_SK-HAGARSA_3836DE | Main Power / Stolen batteries @ 0661_S_SK-HAGARSA_3836DE / Clear after Power back | Faulty System | batt | Batteries | 345237 | SK-HAGARSA | C1-3836DE-PH14 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM774051 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN. problem / stolen batteries / clear after checking GN. | Faulty System | batt | Batteries | 324500 | SK-AZZAZI | C1_4029DE_PH15 | Batteries | Item(s) stolen/No backup batteries.
IM774051 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN. problem / stolen batteries / clear after checking GN. | Faulty System | GN | Generator | 324500 | SK-AZZAZI | C1_4029DE_PH15 | ATS / Engine | Wrong connection/Some cables are disconnected and need adjust.
IM774051 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN. problem / stolen batteries / clear after checking GN. | Faulty System | GN | Generator | 324500 | SK-AZZAZI | C1_4029DE_PH15 | ATS / Engine | Panorama pictures for each system/Generator battery poles need cleaning, wax and covers.
IM774051 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN. problem / stolen batteries / clear after checking GN. | Faulty System | GN | Generator | 324500 | SK-AZZAZI | C1_4029DE_PH15 | ATS / Engine | Panorama pictures for each system/Overview.
IM774065 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to DG relay problem & weak batteries (T) | Faulty System | DG | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | ATS / Engine | Wrong connection/wrong connections
IM774065 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to DG relay problem & weak batteries (T) | Faulty System | DG | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/floating hoses
IM774065 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to DG relay problem & weak batteries (T) | Faulty System | DG | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/unprotected cable
IM774065 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to DG relay problem & weak batteries (T) | Faulty System | DG | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage
IM774069 | 3096DE | 02891_G_3096DE_OBOUR-DST6 | down due to DG fuel filter problem & no backup (T) | Faulty System | DG | Generator | 345263 | OBOUR-DST6 | C1_3096DE_PH12 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage
IM774090 | 4211UP | 691_OO_LU-GZRT-BAIRAT_4211UP | main Power Disconnection, weak Batteries, Autorcovered. | Faulty System | batt | Batteries | 324828 | LU-GZRT-BAIRAT | C1_4211UP_PH19 | Batteries | Item(s) stolen/Batteries were stolen
IM774120 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG Stopped , weak batteries caused site Down once DG Fix site recovered | Faulty System | batt | Batteries | 356434 | 01_G_SS-RAMADA-SEDR_0371SI | C4_0371SI_PH09 | Batteries | Some parts are (missing / stolen)/Battery string stolen
IM774120 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG Stopped , weak batteries caused site Down once DG Fix site recovered | Faulty System | DG | Generator | 356434 | 01_G_SS-RAMADA-SEDR_0371SI | C4_0371SI_PH09 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage
IM774120 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG Stopped , weak batteries caused site Down once DG Fix site recovered | Faulty System | DG | Generator | 356434 | 01_G_SS-RAMADA-SEDR_0371SI | C4_0371SI_PH09 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage
IM774120 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG Stopped , weak batteries caused site Down once DG Fix site recovered | Faulty System | DG | Generator | 356434 | 01_G_SS-RAMADA-SEDR_0371SI | C4_0371SI_PH09 | ATS / Engine | Components faulty/Generator battery defected
IM774120 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG Stopped , weak batteries caused site Down once DG Fix site recovered | Faulty System | DG | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure
IM774120 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG Stopped , weak batteries caused site Down once DG Fix site recovered | Faulty System | DG | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Wrong connection/generator battery as used in the site and not suitable in High temp
IM774138 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem & no backup & access VF (T) | Faulty System | backup | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | Batteries | Some parts are (missing / stolen)/missing battereis
IM774152 | 0587DE | 0221_S_DK-KFR-KURDI_0587DE | VF Share / Main power / Stolen batteries | Faulty System | batt | Batteries | 324791 | DK-KFR-KURDI | C9_0587DE_PH09 | Batteries | Item(s) stolen/No backup batteries.
IM774163 | 0305UP | 01_S_AT-DEIR-MEHARA_0305UP | Due to EC power cutoff , weak batteries , PG Connected | Faulty System | batt | Batteries | 335158 | 01_S_AT-DEIR-MEHARA_0305UP | C1_0305UP_PH8 | Batteries | Components faulty/Fire panel was switched off
IM774164 | 3867DE | 2101_S_GH-NAWYA_3867DE | Main power / Weak batteries / BDT @ 22/05/2019 Is: 0.00 | Faulty System | batt | Batteries | 324418 | GH-NAWYA | C1_3867DE_PH14 | Batteries | Item(s) stolen/stolen
IM774166 | 0305UP | 01_S_AT-DEIR-MEHARA_0305UP | Due to EC power cutoff , weak batteries , PG Connected | Faulty System | batt | Batteries | 335158 | 01_S_AT-DEIR-MEHARA_0305UP | C1_0305UP_PH8 | Batteries | Components faulty/Fire panel was switched off
IM774183 | 3794UP | 02_E_QN-ELQUBIBAH_3794UP | Generator problem, weak Batteries, MW E/// hanged after restore power, MMU reset HW and replaced Ethernet Cable between Link&BTS. | Faulty System | batt | Batteries | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | Rectifiers | Alarms reporting to the OMC/Rectifier minor alarm was looped at ddf
IM774183 | 3794UP | 02_E_QN-ELQUBIBAH_3794UP | Generator problem, weak Batteries, MW E/// hanged after restore power, MMU reset HW and replaced Ethernet Cable between Link&BTS. | Faulty System | batt | Batteries | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | Batteries | Components faulty/Batteries were faulty ( exploded )
IM774183 | 3794UP | 02_E_QN-ELQUBIBAH_3794UP | Generator problem, weak Batteries, MW E/// hanged after restore power, MMU reset HW and replaced Ethernet Cable between Link&BTS. | Faulty System | Gen | Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage from etisalat Gen
IM774183 | 3794UP | 02_E_QN-ELQUBIBAH_3794UP | Generator problem, weak Batteries, MW E/// hanged after restore power, MMU reset HW and replaced Ethernet Cable between Link&BTS. | Faulty System | generator | Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage from etisalat Gen
IM774183 | 3794UP | 02_E_QN-ELQUBIBAH_3794UP | Generator problem, weak Batteries, MW E/// hanged after restore power, MMU reset HW and replaced Ethernet Cable between Link&BTS. | Faulty System | Gen | Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | ATS / Engine | Unit earth/Gen enclosure earth cable is not connected
IM774183 | 3794UP | 02_E_QN-ELQUBIBAH_3794UP | Generator problem, weak Batteries, MW E/// hanged after restore power, MMU reset HW and replaced Ethernet Cable between Link&BTS. | Faulty System | generator | Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | ATS / Engine | Unit earth/Gen enclosure earth cable is not connected
IM774183 | 3794UP | 02_E_QN-ELQUBIBAH_3794UP | Generator problem, weak Batteries, MW E/// hanged after restore power, MMU reset HW and replaced Ethernet Cable between Link&BTS. | Faulty System | Gen | Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | ATS / Engine | Components faulty/ radiator is defected and connected with extranl water source
IM774183 | 3794UP | 02_E_QN-ELQUBIBAH_3794UP | Generator problem, weak Batteries, MW E/// hanged after restore power, MMU reset HW and replaced Ethernet Cable between Link&BTS. | Faulty System | generator | Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | ATS / Engine | Components faulty/ radiator is defected and connected with extranl water source
IM774183 | 3794UP | 02_E_QN-ELQUBIBAH_3794UP | Generator problem, weak Batteries, MW E/// hanged after restore power, MMU reset HW and replaced Ethernet Cable between Link&BTS. | Faulty System | Gen | Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | ATS / Engine | Components faulty/Gen battey is defected and need new one
IM774183 | 3794UP | 02_E_QN-ELQUBIBAH_3794UP | Generator problem, weak Batteries, MW E/// hanged after restore power, MMU reset HW and replaced Ethernet Cable between Link&BTS. | Faulty System | generator | Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | ATS / Engine | Components faulty/Gen battey is defected and need new one
IM774183 | 3794UP | 02_E_QN-ELQUBIBAH_3794UP | Generator problem, weak Batteries, MW E/// hanged after restore power, MMU reset HW and replaced Ethernet Cable between Link&BTS. | Faulty System | Gen | Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | ATS / Engine | Components faulty/ATS pressing keys and Knob were defected
IM774183 | 3794UP | 02_E_QN-ELQUBIBAH_3794UP | Generator problem, weak Batteries, MW E/// hanged after restore power, MMU reset HW and replaced Ethernet Cable between Link&BTS. | Faulty System | generator | Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | ATS / Engine | Components faulty/ATS pressing keys and Knob were defected
IM774183 | 3794UP | 02_E_QN-ELQUBIBAH_3794UP | Generator problem, weak Batteries, MW E/// hanged after restore power, MMU reset HW and replaced Ethernet Cable between Link&BTS. | Faulty System | Gen | Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | ATS / Engine | Wrong connection/Two cables inserted in one slot and not teminated can cause bad connections
IM774183 | 3794UP | 02_E_QN-ELQUBIBAH_3794UP | Generator problem, weak Batteries, MW E/// hanged after restore power, MMU reset HW and replaced Ethernet Cable between Link&BTS. | Faulty System | generator | Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | ATS / Engine | Wrong connection/Two cables inserted in one slot and not teminated can cause bad connections
IM774183 | 3794UP | 02_E_QN-ELQUBIBAH_3794UP | Generator problem, weak Batteries, MW E/// hanged after restore power, MMU reset HW and replaced Ethernet Cable between Link&BTS. | Faulty System | batt | Batteries | 356303 | 01_S_QN-ELQUBIBAH_3794UP | C4_3794UP_PH15 | Batteries | Some parts are (missing / stolen)/One of Batteries string was stolen
IM774183 | 3794UP | 02_E_QN-ELQUBIBAH_3794UP | Generator problem, weak Batteries, MW E/// hanged after restore power, MMU reset HW and replaced Ethernet Cable between Link&BTS. | Faulty System | Gen | Generator | 356303 | 01_S_QN-ELQUBIBAH_3794UP | C4_3794UP_PH15 | ATS / Engine | Unit earth/Gen enclosure earth cable is missing
IM774183 | 3794UP | 02_E_QN-ELQUBIBAH_3794UP | Generator problem, weak Batteries, MW E/// hanged after restore power, MMU reset HW and replaced Ethernet Cable between Link&BTS. | Faulty System | generator | Generator | 356303 | 01_S_QN-ELQUBIBAH_3794UP | C4_3794UP_PH15 | ATS / Engine | Unit earth/Gen enclosure earth cable is missing
IM774183 | 3794UP | 02_E_QN-ELQUBIBAH_3794UP | Generator problem, weak Batteries, MW E/// hanged after restore power, MMU reset HW and replaced Ethernet Cable between Link&BTS. | Faulty System | Gen | Generator | 356303 | 01_S_QN-ELQUBIBAH_3794UP | C4_3794UP_PH15 | ATS / Engine | Components faulty/Gen battery is faulty
IM774183 | 3794UP | 02_E_QN-ELQUBIBAH_3794UP | Generator problem, weak Batteries, MW E/// hanged after restore power, MMU reset HW and replaced Ethernet Cable between Link&BTS. | Faulty System | generator | Generator | 356303 | 01_S_QN-ELQUBIBAH_3794UP | C4_3794UP_PH15 | ATS / Engine | Components faulty/Gen battery is faulty
IM774183 | 3794UP | 02_E_QN-ELQUBIBAH_3794UP | Generator problem, weak Batteries, MW E/// hanged after restore power, MMU reset HW and replaced Ethernet Cable between Link&BTS. | Faulty System | Gen | Generator | 356303 | 01_S_QN-ELQUBIBAH_3794UP | C4_3794UP_PH15 | ATS / Engine | Components faulty/Gen battery is faulty
IM774183 | 3794UP | 02_E_QN-ELQUBIBAH_3794UP | Generator problem, weak Batteries, MW E/// hanged after restore power, MMU reset HW and replaced Ethernet Cable between Link&BTS. | Faulty System | generator | Generator | 356303 | 01_S_QN-ELQUBIBAH_3794UP | C4_3794UP_PH15 | ATS / Engine | Components faulty/Gen battery is faulty
IM774183 | 3794UP | 02_E_QN-ELQUBIBAH_3794UP | Generator problem, weak Batteries, MW E/// hanged after restore power, MMU reset HW and replaced Ethernet Cable between Link&BTS. | Faulty System | Gen | Generator | 356303 | 01_S_QN-ELQUBIBAH_3794UP | C4_3794UP_PH15 | ATS / Engine | Alarms on equipment (excluding ADM)/Gen has alarm
IM774183 | 3794UP | 02_E_QN-ELQUBIBAH_3794UP | Generator problem, weak Batteries, MW E/// hanged after restore power, MMU reset HW and replaced Ethernet Cable between Link&BTS. | Faulty System | generator | Generator | 356303 | 01_S_QN-ELQUBIBAH_3794UP | C4_3794UP_PH15 | ATS / Engine | Alarms on equipment (excluding ADM)/Gen has alarm
IM774221 | 0648DE | 0381_S_BH-IZ-HUSNI_0648DE | Main power / Stolen batteries | Faulty System | batt | Batteries | 355858 | Ez Hosny LH | C1_0648DE_PH9_TRN | Batteries | Some parts are (missing / stolen)/stolen batteries
IM774221 | 0648DE | 0381_S_BH-IZ-HUSNI_0648DE | Main power / Stolen batteries | Faulty System | batt | Batteries | 355857 | BH-IZ-HUSNI | C1_0648DE_PH9 | Batteries | Some parts are (missing / stolen)/stolen batteries
IM774244 | 0081SI | 01_H_SS-TABA-MARINA-BR_0081SI | Power outage site has weak batteries and access PG problem recovered once power restored | Faulty System | batt | Batteries | 324756 | 01_H_SS-TABA-MARINA-BR_0081SI | C2_0081SI_PH2 | Batteries | Components faulty/defected battery ( string not connected )
IM774265 | 3894CA | 02231_S_3894CA_REHAB-STAGE7 | down due to VF DG problem & stolen batteries & access VF (T) | Faulty System | batt | Batteries | 356204 | REHAB-STAGE7 | C1_3894CA_PH17 | Batteries | Some parts are (missing / stolen)/missing batteries
IM774306 | 0967DE | 0111_D_MF-MAWKEF-2_0967DE | access owner/GN problem/weak batteries | Faulty System | GN | Generator | 335176 | MF-MAWKEF-2 | C2_0967DE_PH11 | ATS / Engine | Wrong connection/Wrong connection (Cables uninstalled inside CB)
IM774359 | 3755DE | 0951_Q_SK-SHARSHIMA_3755DE | GN problem/ batteries under investigation@SK-SHARSHIMA_3755DE/ | Faulty System | GN | Generator | 304145 | SK-SHARSHIMA | C6_3755DE_PH14 | ATS / Engine | Components faulty/Generator has alarm (although it is working)
IM774359 | 3755DE | 0951_Q_SK-SHARSHIMA_3755DE | GN problem/ batteries under investigation@SK-SHARSHIMA_3755DE/ | Faulty System | GN | Generator | 304145 | SK-SHARSHIMA | C6_3755DE_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has oil leakage and its oil seal need adjust and repair.
IM774359 | 3755DE | 0951_Q_SK-SHARSHIMA_3755DE | GN problem/ batteries under investigation@SK-SHARSHIMA_3755DE/ | Faulty System | GN | Generator | 304145 | SK-SHARSHIMA | C6_3755DE_PH14 | ATS / Engine | Panorama pictures for each system/Overview.
IM774394 | 3755DE | 0951_Q_SK-SHARSHIMA_3755DE | GN problem/ batteries under investigation@SK-SHARSHIMA_3755DE/clear on pg but it cannot carry all loads | Faulty System | GN | Generator | 304145 | SK-SHARSHIMA | C6_3755DE_PH14 | ATS / Engine | Components faulty/Generator has alarm (although it is working)
IM774394 | 3755DE | 0951_Q_SK-SHARSHIMA_3755DE | GN problem/ batteries under investigation@SK-SHARSHIMA_3755DE/clear on pg but it cannot carry all loads | Faulty System | GN | Generator | 304145 | SK-SHARSHIMA | C6_3755DE_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has oil leakage and its oil seal need adjust and repair.
IM774394 | 3755DE | 0951_Q_SK-SHARSHIMA_3755DE | GN problem/ batteries under investigation@SK-SHARSHIMA_3755DE/clear on pg but it cannot carry all loads | Faulty System | GN | Generator | 304145 | SK-SHARSHIMA | C6_3755DE_PH14 | ATS / Engine | Panorama pictures for each system/Overview.
IM774400 | 3299DE | 0541_S_KS-ZAAFRAN_3299DE | Share VF / Main power / weak batteries | Faulty System | batt | Batteries | 355873 | KS-ZAAFRAN | C1_3299DE_PH12 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM774403 | 0165UP | 0381_B_AS-APT_0165UP_X | Generator problem,weak Batteries, solved. | Faulty System | Gen | Generator | 345342 | 01_V_AS-APT_0165UP | C4_0165UP_PH03 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage beside gen enclosure
IM774403 | 0165UP | 0381_B_AS-APT_0165UP_X | Generator problem,weak Batteries, solved. | Faulty System | generator | Generator | 345342 | 01_V_AS-APT_0165UP | C4_0165UP_PH03 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage beside gen enclosure
IM774403 | 0165UP | 0381_B_AS-APT_0165UP_X | Generator problem,weak Batteries, solved. | Faulty System | Gen | Generator | 345342 | 01_V_AS-APT_0165UP | C4_0165UP_PH03 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage beside gen enclosure ( Huge fuel leakage )
IM774403 | 0165UP | 0381_B_AS-APT_0165UP_X | Generator problem,weak Batteries, solved. | Faulty System | generator | Generator | 345342 | 01_V_AS-APT_0165UP | C4_0165UP_PH03 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage beside gen enclosure ( Huge fuel leakage )
IM774403 | 0165UP | 0381_B_AS-APT_0165UP_X | Generator problem,weak Batteries, solved. | Faulty System | Gen | Generator | 345342 | 01_V_AS-APT_0165UP | C4_0165UP_PH03 | ATS / Engine | Components faulty/external water supply connected to radiator
IM774403 | 0165UP | 0381_B_AS-APT_0165UP_X | Generator problem,weak Batteries, solved. | Faulty System | generator | Generator | 345342 | 01_V_AS-APT_0165UP | C4_0165UP_PH03 | ATS / Engine | Components faulty/external water supply connected to radiator
IM774408 | 0574UP | 02_S_QN-GARAGOUS_0574UP | main Power Disconnection, weak Batteries, PG Connected. | Faulty System | batt | Batteries | 304201 | 01_S_QN-GARAGOUS_0574UP | C3_0574UP_PH9 | Batteries | Item(s) stolen/Batteries were stolen
IM774429 | 3221UP | 2021_S_SG-AWLAD-NOSIR_3221UP | main Power Disconnection, weak Batteries, PG Connected. | Faulty System | batt | Batteries | 345420 | 01_S_SG-AWLAD-NOSIR_3221UP | C1_3221UP_PH13 | Batteries | Some parts are (missing / stolen)/one string battery was stolen
IM774438 | 0165UP | 0381_B_AS-APT_0165UP_X | Generator problem,weak Batteries, solved. | Faulty System | Gen | Generator | 345342 | 01_V_AS-APT_0165UP | C4_0165UP_PH03 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage beside gen enclosure
IM774438 | 0165UP | 0381_B_AS-APT_0165UP_X | Generator problem,weak Batteries, solved. | Faulty System | generator | Generator | 345342 | 01_V_AS-APT_0165UP | C4_0165UP_PH03 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage beside gen enclosure
IM774438 | 0165UP | 0381_B_AS-APT_0165UP_X | Generator problem,weak Batteries, solved. | Faulty System | Gen | Generator | 345342 | 01_V_AS-APT_0165UP | C4_0165UP_PH03 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage beside gen enclosure ( Huge fuel leakage )
IM774438 | 0165UP | 0381_B_AS-APT_0165UP_X | Generator problem,weak Batteries, solved. | Faulty System | generator | Generator | 345342 | 01_V_AS-APT_0165UP | C4_0165UP_PH03 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage beside gen enclosure ( Huge fuel leakage )
IM774438 | 0165UP | 0381_B_AS-APT_0165UP_X | Generator problem,weak Batteries, solved. | Faulty System | Gen | Generator | 345342 | 01_V_AS-APT_0165UP | C4_0165UP_PH03 | ATS / Engine | Components faulty/external water supply connected to radiator
IM774438 | 0165UP | 0381_B_AS-APT_0165UP_X | Generator problem,weak Batteries, solved. | Faulty System | generator | Generator | 345342 | 01_V_AS-APT_0165UP | C4_0165UP_PH03 | ATS / Engine | Components faulty/external water supply connected to radiator
IM774451 | 0964UP | 0181_S_SG-SALLA_0964UP | main Power Disconnection, weak Batteries, PG Connected. | Faulty System | batt | Batteries | 345407 | SG-SALLA | C2_0964UP_PH12 | Batteries | Some parts are (missing / stolen)/site Batteries were stolen
IM774504 | 0045SI | 01_G_SS-MR66-ABYAD_0045SI | DG Stoppage / weak batteries / access Guard problem / cleared after Gen restored | Faulty System | DG | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure
IM774504 | 0045SI | 01_G_SS-MR66-ABYAD_0045SI | DG Stoppage / weak batteries / access Guard problem / cleared after Gen restored | Faulty System | Gen | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure
IM774504 | 0045SI | 01_G_SS-MR66-ABYAD_0045SI | DG Stoppage / weak batteries / access Guard problem / cleared after Gen restored | Faulty System | DG | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Wrong connection/generator battery as used in the site and not suitable in High temp
IM774504 | 0045SI | 01_G_SS-MR66-ABYAD_0045SI | DG Stoppage / weak batteries / access Guard problem / cleared after Gen restored | Faulty System | Gen | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Wrong connection/generator battery as used in the site and not suitable in High temp
IM774541 | 3903DE | 0501_D_GH-MHLT-MISIR_3903DE | GN problem / stolen batteries | Faulty System | batt | Batteries | 335219 | GH-MHLT-MISIR | C4_3903DE_PH15 | Batteries | Item(s) stolen/There is no battery for site
IM774541 | 3903DE | 0501_D_GH-MHLT-MISIR_3903DE | GN problem / stolen batteries | Faulty System | GN | Generator | 335219 | GH-MHLT-MISIR | C4_3903DE_PH15 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM wrong penetration/CB need proper fixation
IM774545 | 3793DE | 0821_D_SK-SHARQAYA_3793DE | GN problem/Batteries under investigation/clear after replace GN | Faulty System | GN | Generator | 356263 | SK-SHARQAYA | C1-3793DE-PH14 | ATS / Engine | Components faulty/Faulty module.
IM774545 | 3793DE | 0821_D_SK-SHARQAYA_3793DE | GN problem/Batteries under investigation/clear after replace GN | Faulty System | GN | Generator | 356263 | SK-SHARQAYA | C1-3793DE-PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/ATS cables need proper terminals.
IM774624 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | batt | Batteries | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | Batteries | Item(s) stolen/Batteries were stolen
IM774624 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Wrong connection/external cable to the guard connected from gen and not protected
IM774624 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Wrong connection/external cable to the guard connected from gen and not protected
IM774624 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Wrong connection/One Contactor turned on by setting wood inside it
IM774624 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Wrong connection/One Contactor turned on by setting wood inside it
IM774624 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cables not protected in tube
IM774624 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cables not protected in tube
IM774624 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cables not protected
IM774624 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cables not protected
IM774624 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Item(s) stolen/Gen battery is missing
IM774624 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Item(s) stolen/Gen battery is missing
IM774624 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/ Fuel leakage inside Gen
IM774624 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/ Fuel leakage inside Gen
IM774624 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage inside Gen
IM774624 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage inside Gen
IM774624 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage beisde Gen enclosure area need cleaning
IM774624 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage beisde Gen enclosure area need cleaning
IM774624 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Panorama pictures for each system/Open gland in Gen enclosure need insulation
IM774624 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Panorama pictures for each system/Open gland in Gen enclosure need insulation
IM774624 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM774624 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM774624 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Panorama pictures for each system/Last Gen hour meter at Audit G ( 31148 )
IM774624 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | ATS / Engine | Panorama pictures for each system/Last Gen hour meter at Audit G ( 31148 )
IM774636 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/stolen batteries/clear after check GN | Faulty System | batt | Batteries | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | Batteries | Some parts are missing/Battery cabinet need cleaning (from inside) and holes need sealing.
IM774636 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/stolen batteries/clear after check GN | Faulty System | batt | Batteries | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | Batteries | Some parts are missing/Batteries poles need have missing covers.
IM774636 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/stolen batteries/clear after check GN | Faulty System | GN | Generator | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | ATS / Engine | Components faulty/Generator has bad performance and need overall.
IM774636 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/stolen batteries/clear after check GN | Faulty System | GN | Generator | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | ATS / Engine | Panorama pictures for each system/Overview.
IM774642 | 0500RE | 03461_S_0500RE_SZ-REHAB | VF EC power problem / stolen batteries / access PG problem /cleared after power restored | Faulty System | batt | Batteries | 356059 | 01_S_SZ-REHAB_0500RE | 0500RE | Batteries | Some parts are (missing / stolen)/Battery string stolen
IM774648 | 0352UP | 01_J_ASYUT-KHARGA-6-NR_0352UP | Due to Generator problem , Weak batteries , Recovered | Faulty System | Gen | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure
IM774648 | 0352UP | 01_J_ASYUT-KHARGA-6-NR_0352UP | Due to Generator problem , Weak batteries , Recovered | Faulty System | generator | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure
IM774648 | 0352UP | 01_J_ASYUT-KHARGA-6-NR_0352UP | Due to Generator problem , Weak batteries , Recovered | Faulty System | Gen | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Wrong connection/generator battery as used in the site and not suitable in High temp
IM774648 | 0352UP | 01_J_ASYUT-KHARGA-6-NR_0352UP | Due to Generator problem , Weak batteries , Recovered | Faulty System | generator | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | ATS / Engine | Wrong connection/generator battery as used in the site and not suitable in High temp
IM774658 | 0003UP | 0311_N_AS-TROMBAT-AS_0003UP | main Power Disconnection, weak Batteries,Autorecovered. | Faulty System | batt | Batteries | 345338 | 01_N_AS-TROMBAT-AS_0003UP | C1_0003UP_PH0 | Batteries | Some parts are (missing / stolen)/one Batteries string was stolen
IM774664 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to LOP alarm as engine need overhauling action Site has weak backup batteries | Faulty System | backup | Batteries | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | Batteries | Item(s) stolen/One of batteries string was stolen
IM774664 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to LOP alarm as engine need overhauling action Site has weak backup batteries | Faulty System | batt | Batteries | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | Batteries | Item(s) stolen/One of batteries string was stolen
IM774664 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to LOP alarm as engine need overhauling action Site has weak backup batteries | Faulty System | Gen | Generator | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | ATS / Engine | Components faulty/Gen battery is defected
IM774664 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to LOP alarm as engine need overhauling action Site has weak backup batteries | Faulty System | generator | Generator | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | ATS / Engine | Components faulty/Gen battery is defected
IM774664 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to LOP alarm as engine need overhauling action Site has weak backup batteries | Faulty System | Gen | Generator | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Gen battery cables not isolated well
IM774664 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to LOP alarm as engine need overhauling action Site has weak backup batteries | Faulty System | generator | Generator | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Gen battery cables not isolated well
IM774664 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to LOP alarm as engine need overhauling action Site has weak backup batteries | Faulty System | Gen | Generator | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | ATS / Engine | Panorama pictures for each system/Open gland in Gen enclosure need insulation
IM774664 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to LOP alarm as engine need overhauling action Site has weak backup batteries | Faulty System | generator | Generator | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | ATS / Engine | Panorama pictures for each system/Open gland in Gen enclosure need insulation
IM774664 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to LOP alarm as engine need overhauling action Site has weak backup batteries | Faulty System | Gen | Generator | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM774664 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to LOP alarm as engine need overhauling action Site has weak backup batteries | Faulty System | generator | Generator | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM774664 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to LOP alarm as engine need overhauling action Site has weak backup batteries | Faulty System | Gen | Generator | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | ATS / Engine | Panorama pictures for each system/Last Gen hour meter at Auidt G ( 661 )
IM774664 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to LOP alarm as engine need overhauling action Site has weak backup batteries | Faulty System | generator | Generator | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | ATS / Engine | Panorama pictures for each system/Last Gen hour meter at Auidt G ( 661 )
IM774676 | 3349CA | 01126_S_3349CA_IMBABA-6 | down due to main power & weak batteries (T) | Faulty System | batt | Batteries | 303961 | IMBABA-6 | C2_3349CA_PH12 | Batteries | Components faulty/Batteries are in a very bad condition (DC voltage dropped to 42.7V. after 1 min of power disconnecting)
IM774683 | 3002CA | 00926_S_3002CA_BASHTEL1 | down due to main power & stolen batteries at 3002CA_BASHTEL1 (T) | Faulty System | batt | Batteries | 304247 | BASHTEL1 | C1_3002CA_PH9 | Batteries | Item(s) stolen/Stolen batteries and cables
IM774718 | 0011RE | 03426_G_0011RE_SZ-HW33-7 | DG stoppage / stolen batteries / fuel pump problem/ PG connected till gen restored | Faulty System | batt | Batteries | 356077 | 01_G_SZ-HW33-7_0011RE | C1_0011RE_PH1 | Batteries | Some parts are (missing / stolen)/Battery string stolen
IM774718 | 0011RE | 03426_G_0011RE_SZ-HW33-7 | DG stoppage / stolen batteries / fuel pump problem/ PG connected till gen restored | Faulty System | DG | Generator | 356077 | 01_G_SZ-HW33-7_0011RE | C1_0011RE_PH1 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage
IM774718 | 0011RE | 03426_G_0011RE_SZ-HW33-7 | DG stoppage / stolen batteries / fuel pump problem/ PG connected till gen restored | Faulty System | Gen | Generator | 356077 | 01_G_SZ-HW33-7_0011RE | C1_0011RE_PH1 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage
IM774718 | 0011RE | 03426_G_0011RE_SZ-HW33-7 | DG stoppage / stolen batteries / fuel pump problem/ PG connected till gen restored | Faulty System | DG | Generator | 356077 | 01_G_SZ-HW33-7_0011RE | C1_0011RE_PH1 | ATS / Engine | Wrong connection/Power cable has no terminal & worng connection , the two cables should be in one terminal
IM774718 | 0011RE | 03426_G_0011RE_SZ-HW33-7 | DG stoppage / stolen batteries / fuel pump problem/ PG connected till gen restored | Faulty System | Gen | Generator | 356077 | 01_G_SZ-HW33-7_0011RE | C1_0011RE_PH1 | ATS / Engine | Wrong connection/Power cable has no terminal & worng connection , the two cables should be in one terminal
IM774728 | 3065UP | 0641_S_QN-ELARAKI_3065UP | main Power Disconnection, weak Batteries, PG Connected. | Faulty System | batt | Batteries | 356496 | 01_S_QN-ELARAKI_3065UP | C1_3065UP_PH13 | Batteries | Some parts are (missing / stolen)/Batteries were stolen
IM774750 | 3529UP | 1041_E_QN-HISHA_3529UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 355814 | 01_S_QN-HISHA_3529UP | C1_3529UP_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/old fuel leakage beisde Gen enclosure
IM774750 | 3529UP | 1041_E_QN-HISHA_3529UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 355814 | 01_S_QN-HISHA_3529UP | C1_3529UP_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/old fuel leakage beisde Gen enclosure
IM774750 | 3529UP | 1041_E_QN-HISHA_3529UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 355814 | 01_S_QN-HISHA_3529UP | C1_3529UP_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage inside Gen enclosure
IM774750 | 3529UP | 1041_E_QN-HISHA_3529UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 355814 | 01_S_QN-HISHA_3529UP | C1_3529UP_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage inside Gen enclosure
IM774750 | 3529UP | 1041_E_QN-HISHA_3529UP | Generator problem, weak Batteries, solved. | Faulty System | Gen | Generator | 355814 | 01_S_QN-HISHA_3529UP | C1_3529UP_PH14 | ATS / Engine | Unit earth/Gen earth cable is missing
IM774750 | 3529UP | 1041_E_QN-HISHA_3529UP | Generator problem, weak Batteries, solved. | Faulty System | generator | Generator | 355814 | 01_S_QN-HISHA_3529UP | C1_3529UP_PH14 | ATS / Engine | Unit earth/Gen earth cable is missing
IM774758 | 0011RE | 03426_D_0011RE_SZ-HW33-7 | DG stoppage / stolen batteries / fuel pump problem/ PG connected till gen restored | Faulty System | batt | Batteries | 356077 | 01_G_SZ-HW33-7_0011RE | C1_0011RE_PH1 | Batteries | Some parts are (missing / stolen)/Battery string stolen
IM774758 | 0011RE | 03426_D_0011RE_SZ-HW33-7 | DG stoppage / stolen batteries / fuel pump problem/ PG connected till gen restored | Faulty System | DG | Generator | 356077 | 01_G_SZ-HW33-7_0011RE | C1_0011RE_PH1 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage
IM774758 | 0011RE | 03426_D_0011RE_SZ-HW33-7 | DG stoppage / stolen batteries / fuel pump problem/ PG connected till gen restored | Faulty System | Gen | Generator | 356077 | 01_G_SZ-HW33-7_0011RE | C1_0011RE_PH1 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage
IM774758 | 0011RE | 03426_D_0011RE_SZ-HW33-7 | DG stoppage / stolen batteries / fuel pump problem/ PG connected till gen restored | Faulty System | DG | Generator | 356077 | 01_G_SZ-HW33-7_0011RE | C1_0011RE_PH1 | ATS / Engine | Wrong connection/Power cable has no terminal & worng connection , the two cables should be in one terminal
IM774758 | 0011RE | 03426_D_0011RE_SZ-HW33-7 | DG stoppage / stolen batteries / fuel pump problem/ PG connected till gen restored | Faulty System | Gen | Generator | 356077 | 01_G_SZ-HW33-7_0011RE | C1_0011RE_PH1 | ATS / Engine | Wrong connection/Power cable has no terminal & worng connection , the two cables should be in one terminal
IM774820 | 2123DE | 0631_S_DM-M-EZBT-BRG2_2123DE | Main power / Micro / Access PG / Weak batteries | Faulty System | batt | Batteries | 355943 | DM-M-EZBT-BRG2 | C1_2123DE_PH17 | Rectifiers | Alarms reporting to the OMC/alarm door is not reported
IM774820 | 2123DE | 0631_S_DM-M-EZBT-BRG2_2123DE | Main power / Micro / Access PG / Weak batteries | Faulty System | batt | Batteries | 355943 | DM-M-EZBT-BRG2 | C1_2123DE_PH17 | Batteries | Some parts are (missing / stolen)/poles covers
IM774821 | 0954UP | 01_G_MN-DAHMARU_0954UP | VF shared power meter was our of charge and recharged Site has stolen backup batteries | Faulty System | backup | Batteries | 324946 | 01_G_MN-DAHMARU_0954UP | C1_0954UP_PH12 | Batteries | Item(s) stolen/site baateries were stolen
IM774821 | 0954UP | 01_G_MN-DAHMARU_0954UP | VF shared power meter was our of charge and recharged Site has stolen backup batteries | Faulty System | batt | Batteries | 324946 | 01_G_MN-DAHMARU_0954UP | C1_0954UP_PH12 | Batteries | Item(s) stolen/site baateries were stolen
IM774831 | 0629CA | 01134_S_0629CA_KAWMYA-ARABYA | down due to main power & weak batteries (T) | Faulty System | batt | Batteries | 304038 | KAWMYA-ARABYA | C2_0629CA_PH8 | Batteries | Item(s) stolen/Battery cables are stolen
IM774832 | 3178UP | 01_D_AT-BAQUR_3178UP | Generator stopped due to fuel theft problem and site powered on P.G till refuling the generator site has weak backup batteries | Faulty System | backup | Batteries | 324555 | 01_G_AT-BAQUR_3178UP | C2_3178UP_PH13 | Batteries | Components faulty/site batteries were defected and to be changed
IM774832 | 3178UP | 01_D_AT-BAQUR_3178UP | Generator stopped due to fuel theft problem and site powered on P.G till refuling the generator site has weak backup batteries | Faulty System | batt | Batteries | 324555 | 01_G_AT-BAQUR_3178UP | C2_3178UP_PH13 | Batteries | Components faulty/site batteries were defected and to be changed
IM774832 | 3178UP | 01_D_AT-BAQUR_3178UP | Generator stopped due to fuel theft problem and site powered on P.G till refuling the generator site has weak backup batteries | Faulty System | Gen | Generator | 324555 | 01_G_AT-BAQUR_3178UP | C2_3178UP_PH13 | ATS / Engine | Components faulty/Gen missing battery
IM774832 | 3178UP | 01_D_AT-BAQUR_3178UP | Generator stopped due to fuel theft problem and site powered on P.G till refuling the generator site has weak backup batteries | Faulty System | generator | Generator | 324555 | 01_G_AT-BAQUR_3178UP | C2_3178UP_PH13 | ATS / Engine | Components faulty/Gen missing battery
IM774832 | 3178UP | 01_D_AT-BAQUR_3178UP | Generator stopped due to fuel theft problem and site powered on P.G till refuling the generator site has weak backup batteries | Faulty System | Gen | Generator | 324555 | 01_G_AT-BAQUR_3178UP | C2_3178UP_PH13 | ATS / Engine | Wrong connection/Bad isolation for batteries cables
IM774832 | 3178UP | 01_D_AT-BAQUR_3178UP | Generator stopped due to fuel theft problem and site powered on P.G till refuling the generator site has weak backup batteries | Faulty System | generator | Generator | 324555 | 01_G_AT-BAQUR_3178UP | C2_3178UP_PH13 | ATS / Engine | Wrong connection/Bad isolation for batteries cables
IM774843 | 3740DE | 0521_S_KS-MNSHT-ABS_3740DE | Access TE / Main power / Stolen batteries | Faulty System | batt | Batteries | 324805 | KS-MNSHT-ABS | C1_3740DE_Ph14 | Batteries | Item(s) stolen/There is no battery for site
IM774845 | 0479DE | 0591_S_DK-MNS-FRSKOR1_0479DE | Main power @ DK-MNS-FRSKOR1_0479DE / Stolen batteries / Access road problem / PG connected | Faulty System | batt | Batteries | 356389 | DK-MNS-FRSKOR1 | C3_0479DE_PH7 | Batteries | Some parts are (missing / stolen)/stolen batteries
IM774847 | 3368DE | 0201_S_BH-ABO-SHIQAF_3368DE | Share VF / Main power / stolen batteries | Faulty System | batt | Batteries | 324904 | BH-ABO-SHIQAF | C1_3368DE_PH12 | Batteries | Item(s) stolen/There is no battery for site
IM774864 | 3344DE | 0681_S_BH-ELNEGILY_3344DE | VF Share / Main power / Stolen batteries | Faulty System | batt | Batteries | 304214 | BH-ELNEGILY | C3_3344DE_PH12 | Batteries | Item(s) stolen/There is no battery for site
IM774933 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | DG stoppage / weak batteries / fuel filter problem/ cleared after replaced | Faulty System | DG | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/OIL & fuel leakage
IM774933 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | DG stoppage / weak batteries / fuel filter problem/ cleared after replaced | Faulty System | DG | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage
IM774933 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | DG stoppage / weak batteries / fuel filter problem/ cleared after replaced | Faulty System | DG | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Unit earth/alternator not earthed
IM774933 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | DG stoppage / weak batteries / fuel filter problem/ cleared after replaced | Faulty System | DG | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Unit earth/earth bar not connected to main earth bar
IM774933 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | DG stoppage / weak batteries / fuel filter problem/ cleared after replaced | Faulty System | DG | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Unit earth/earth cable not connected
IM774933 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | DG stoppage / weak batteries / fuel filter problem/ cleared after replaced | Faulty System | DG | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/cable not terminated
IM774958 | 3065AL | 03902_S_3065AL_MHWR-DABA-17 | GN problem/ stolen batteries/ restored after solve GN problem | Faulty System | GN | Generator | 324550 | MHWR-DABA-17 | C1_3065AL_PH20 | ATS / Engine | Wrong connection/Wrong connection (Joint cables)
IM774958 | 3065AL | 03902_S_3065AL_MHWR-DABA-17 | GN problem/ stolen batteries/ restored after solve GN problem | Faulty System | GN | Generator | 324550 | MHWR-DABA-17 | C1_3065AL_PH20 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/Cables needs organization
IM775050 | 0011RE | 03426_G_0011RE_SZ-HW33-7 | DG stoppage / stolen batteries / fuel pump problem/ PG connected till gen restored | Faulty System | batt | Batteries | 356077 | 01_G_SZ-HW33-7_0011RE | C1_0011RE_PH1 | Batteries | Some parts are (missing / stolen)/Battery string stolen
IM775050 | 0011RE | 03426_G_0011RE_SZ-HW33-7 | DG stoppage / stolen batteries / fuel pump problem/ PG connected till gen restored | Faulty System | DG | Generator | 356077 | 01_G_SZ-HW33-7_0011RE | C1_0011RE_PH1 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage
IM775050 | 0011RE | 03426_G_0011RE_SZ-HW33-7 | DG stoppage / stolen batteries / fuel pump problem/ PG connected till gen restored | Faulty System | Gen | Generator | 356077 | 01_G_SZ-HW33-7_0011RE | C1_0011RE_PH1 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage
IM775050 | 0011RE | 03426_G_0011RE_SZ-HW33-7 | DG stoppage / stolen batteries / fuel pump problem/ PG connected till gen restored | Faulty System | DG | Generator | 356077 | 01_G_SZ-HW33-7_0011RE | C1_0011RE_PH1 | ATS / Engine | Wrong connection/Power cable has no terminal & worng connection , the two cables should be in one terminal
IM775050 | 0011RE | 03426_G_0011RE_SZ-HW33-7 | DG stoppage / stolen batteries / fuel pump problem/ PG connected till gen restored | Faulty System | Gen | Generator | 356077 | 01_G_SZ-HW33-7_0011RE | C1_0011RE_PH1 | ATS / Engine | Wrong connection/Power cable has no terminal & worng connection , the two cables should be in one terminal
IM775051 | 0001SI | 03504_I_0001SI_IS-GEDAM | DG stoppage / weak batteries / dynamo problem/ cleared | Faulty System | batt | Batteries | 355761 | 01_W_IS-GEDAM_0001SI | C2_0001SI_PH0 | Rectifiers | Alarms reporting to the OMC/Rectifier minor & major alarm not report the OMC
IM775078 | 0329RE | 03838_S_0329RE_RS-SENTIDO-DRM | ET Gen stoppage / weak batteries / cleared after Gen restored | Faulty System | Gen | Generator | 304289 | 01_S_RS-SENTIDO-DRM_0329RE | C1_0329RE_PH12 | ATS / Engine | Panorama pictures for each system/Panorama site view in outside site
IM775080 | 3130CA | K_BASHTEL-ST_2_11319-2_S | was down cascaded 3130CA_BASHTEL-ST which down due to power and stolen batt. (I) | Faulty System | batt | Batteries | 345403 | BASHTEL-ST | C3_3130CA_PH9 | Rectifiers | Alarms reporting to the OMC/Minor alarm due to temprature measurement doesn't appear on the OMC (Loop in DDF)
IM775080 | 3130CA | K_BASHTEL-ST_2_11319-2_S | was down cascaded 3130CA_BASHTEL-ST which down due to power and stolen batt. (I) | Faulty System | batt | Batteries | 345403 | BASHTEL-ST | C3_3130CA_PH9 | Batteries | Some parts are (missing / stolen)/All batteries are stolen
IM775092 | 3953DE | 0361_G_BH-MAARKA_3953DE | access ET/main power/weak batteries/clear after power back | Faulty System | batt | Batteries | 304235 | BH-MAARKA | C1_3953DE_PH15 | Batteries | Components faulty/Faulty battery and cable disconnected
IM775115 | 0576DE | 1611_G_BH-WAFAIYYA_0576DE | Main Power / Stolen batteries | Faulty System | batt | Batteries | 324440 | BH-WAFAIYYA | C2_0576DE_PH9 | Batteries | Item(s) stolen/There is no battery for site
IM775121 | 0971DE | 1931_D_KS-DISOQ-COURT_0971DE | Share ET / Gen problem / Stolen Batteries / Team in site | Faulty System | batt | Batteries | 314424 | KS-DISOQ-COURT | C4_0971DE_PH11 | Batteries | Item(s) stolen/No battery for site
IM775121 | 0971DE | 1931_D_KS-DISOQ-COURT_0971DE | Share ET / Gen problem / Stolen Batteries / Team in site | Faulty System | Gen | Generator | 314424 | KS-DISOQ-COURT | C4_0971DE_PH11 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Cables at 1 slot
IM775121 | 0971DE | 1931_D_KS-DISOQ-COURT_0971DE | Share ET / Gen problem / Stolen Batteries / Team in site | Faulty System | Gen | Generator | 314424 | KS-DISOQ-COURT | C4_0971DE_PH11 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Terminal requried
IM775121 | 0971DE | 1931_D_KS-DISOQ-COURT_0971DE | Share ET / Gen problem / Stolen Batteries / Team in site | Faulty System | Gen | Generator | 314424 | KS-DISOQ-COURT | C4_0971DE_PH11 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Cable need to be terminated well
IM775172 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/Stolen batteries/clear on P.G | Faulty System | batt | Batteries | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | Batteries | Some parts are missing/Battery cabinet need cleaning (from inside) and holes need sealing.
IM775172 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/Stolen batteries/clear on P.G | Faulty System | batt | Batteries | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | Batteries | Some parts are missing/Batteries poles need have missing covers.
IM775172 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/Stolen batteries/clear on P.G | Faulty System | GN | Generator | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | ATS / Engine | Components faulty/Generator has bad performance and need overall.
IM775172 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/Stolen batteries/clear on P.G | Faulty System | GN | Generator | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | ATS / Engine | Panorama pictures for each system/Overview.
IM775175 | 3499UP | 1871_S_AS-GAFAR-SADK_3499UP_X | Main Power Disconenction, weak Batteries, Recovered. | Faulty System | batt | Batteries | 356189 | 01_S_AS-GAFAR-SADK_3499UP | C1_3499UP_PH14 | Batteries | Some parts are (missing / stolen)/Site Batteries were stolen
IM775181 | 0086RE | 03821_C_0086RE_RS-MR44-LASIFA | DG Stoppage / weak batteries / cleared after restored | Faulty System | DG | Generator | 355695 | 01_C_RS-MR44-LASIFA_0086RE | C2_0086RE_PH3 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/add terminals
IM775212 | 3361DE | 0441_S_KS-HAMUL-EST_3361DE | Share VF / Main power / Stolen batteries | Faulty System | batt | Batteries | 355874 | KS-HAMUL-EST | C1_3361DE_PH12 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM775218 | 4021DE | 0181_S_BH-ABQAEEN_4021DE | Share VF / Main power / Stolen batteries | Faulty System | batt | Batteries | 304224 | BH-ABQAEEN | C1_4021DE_PH15 | Batteries | Item(s) stolen/There is no battery for site
IM775267 | 3126DE | 0121_S_DK-HAGYZEYA_3126DE | access VF/main power/Stolen batteries/handel husiynia 2 //manshit amer//hwamida | Faulty System | batt | Batteries | 355992 | DK-HAGYZEYA | C6-3126DE-PH12 | Batteries | Some parts are (missing / stolen)/No backup batteries.
IM775285 | 0596DE | 1691_G_GH-TIRA_0596DE | Main power @ GH-TIRA_0596DE / stolen batteries | Faulty System | batt | Batteries | 324921 | GH-TIRA | C1_0596DE_PH9 | Batteries | Item(s) stolen/stolen batteries
IM775309 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Generator replacment action and site has weak backup batteries , P.G connected | Faulty System | Gen | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | ATS / Engine | Components faulty/Gen battery was defected
IM775309 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Generator replacment action and site has weak backup batteries , P.G connected | Faulty System | generator | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | ATS / Engine | Components faulty/Gen battery was defected
IM775309 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Generator replacment action and site has weak backup batteries , P.G connected | Faulty System | Gen | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/ATS Cables not organized
IM775309 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Generator replacment action and site has weak backup batteries , P.G connected | Faulty System | generator | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization/ATS Cables not organized
IM775339 | 3346DE | 0701_S_BH-KOMOMBO_3346DE | Share VF / Main power / batteries under check | Faulty System | batt | Batteries | 355803 | BH-KOMOMBO | C1_3346DE_PH12 | Rectifiers | Alarms reporting to the OMC/Site has fake power alarm
IM775494 | 4031DE | 1271_D_QL-NAMOL_4031DE | access Guard/GN problem/Stolen batteries/clear after check GN | Faulty System | batt | Batteries | 345429 | QL-NAMOL | C1_4031DE_PH15 | Batteries | Some parts are (missing / stolen)/There is no battery for site
IM775494 | 4031DE | 1271_D_QL-NAMOL_4031DE | access Guard/GN problem/Stolen batteries/clear after check GN | Faulty System | GN | Generator | 345429 | QL-NAMOL | C1_4031DE_PH15 | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side)/Cable need to be terminated well
IM775703 | 3178UP | 01_D_AT-BAQUR_3178UP | Generator stopped due to fuel shortage problem and solved site has weak backup batteries | Faulty System | backup | Batteries | 324555 | 01_G_AT-BAQUR_3178UP | C2_3178UP_PH13 | Batteries | Components faulty/site batteries were defected and to be changed
IM775703 | 3178UP | 01_D_AT-BAQUR_3178UP | Generator stopped due to fuel shortage problem and solved site has weak backup batteries | Faulty System | batt | Batteries | 324555 | 01_G_AT-BAQUR_3178UP | C2_3178UP_PH13 | Batteries | Components faulty/site batteries were defected and to be changed
IM775703 | 3178UP | 01_D_AT-BAQUR_3178UP | Generator stopped due to fuel shortage problem and solved site has weak backup batteries | Faulty System | Gen | Generator | 324555 | 01_G_AT-BAQUR_3178UP | C2_3178UP_PH13 | ATS / Engine | Components faulty/Gen missing battery
IM775703 | 3178UP | 01_D_AT-BAQUR_3178UP | Generator stopped due to fuel shortage problem and solved site has weak backup batteries | Faulty System | generator | Generator | 324555 | 01_G_AT-BAQUR_3178UP | C2_3178UP_PH13 | ATS / Engine | Components faulty/Gen missing battery
IM775703 | 3178UP | 01_D_AT-BAQUR_3178UP | Generator stopped due to fuel shortage problem and solved site has weak backup batteries | Faulty System | Gen | Generator | 324555 | 01_G_AT-BAQUR_3178UP | C2_3178UP_PH13 | ATS / Engine | Wrong connection/Bad isolation for batteries cables
IM775703 | 3178UP | 01_D_AT-BAQUR_3178UP | Generator stopped due to fuel shortage problem and solved site has weak backup batteries | Faulty System | generator | Generator | 324555 | 01_G_AT-BAQUR_3178UP | C2_3178UP_PH13 | ATS / Engine | Wrong connection/Bad isolation for batteries cables
IM775837 | 3866DE | 2001_D_DK-SANBAKHT_3866DE | Generator problem / Stolen Batteries | Faulty System | Gen | Generator | 304185 | DK-SANBAKHT | C3_3866DE_PH14 | ATS / Engine | Components faulty/screen need repair
IM775837 | 3866DE | 2001_D_DK-SANBAKHT_3866DE | Generator problem / Stolen Batteries | Faulty System | generator | Generator | 304185 | DK-SANBAKHT | C3_3866DE_PH14 | ATS / Engine | Components faulty/screen need repair
IM775837 | 3866DE | 2001_D_DK-SANBAKHT_3866DE | Generator problem / Stolen Batteries | Faulty System | Gen | Generator | 304185 | DK-SANBAKHT | C3_3866DE_PH14 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/protect by tray
IM775837 | 3866DE | 2001_D_DK-SANBAKHT_3866DE | Generator problem / Stolen Batteries | Faulty System | generator | Generator | 304185 | DK-SANBAKHT | C3_3866DE_PH14 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/protect by tray
IM775837 | 3866DE | 2001_D_DK-SANBAKHT_3866DE | Generator problem / Stolen Batteries | Faulty System | Gen | Generator | 304185 | DK-SANBAKHT | C3_3866DE_PH14 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/protect
IM775837 | 3866DE | 2001_D_DK-SANBAKHT_3866DE | Generator problem / Stolen Batteries | Faulty System | generator | Generator | 304185 | DK-SANBAKHT | C3_3866DE_PH14 | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/protect
IM775837 | 3866DE | 2001_D_DK-SANBAKHT_3866DE | Generator problem / Stolen Batteries | Faulty System | Gen | Generator | 304185 | DK-SANBAKHT | C3_3866DE_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check oil leakage
IM775837 | 3866DE | 2001_D_DK-SANBAKHT_3866DE | Generator problem / Stolen Batteries | Faulty System | generator | Generator | 304185 | DK-SANBAKHT | C3_3866DE_PH14 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check oil leakage
IM775866 | 3495DE | 0181_S_SK-MAHDIYA_3495DE | Main power/ stolen battery/connect PG | Faulty System | batt | Batteries | 304144 | SK-MAHDIYA | C3_3495DE_PH13 | Batteries | Item(s) stolen/No backup batteries.
IM775868 | 3394DE | 0011_S_B-SAFT-KHALED_3394DE | Share VF / Main Power / Weak Batteries / PG connected | Faulty System | batt | Batteries | 304033 | BH-SAFT-KHALED | C1_3394DE_PH13 | Batteries | Components faulty/Faulty battery
IM775974 | 0955UP | 0551_S_QN-SHRQI-SMHUD_0955UP | main power Disconnection,weak batteries, PG Connected . | Faulty System | batt | Batteries | 355972 | 01_S_QN-SHRQI-SHMHUD_0955UP | C1_0955UP_PH12 | Rectifiers | Alarms reporting to the OMC/High Temp Alarm was exists on rectifier and appeared on the Omc
IM776012 | 0587DE | 0221_S_DK-KFR-KURDI_0587DE | Share VF / Main Power / stolen Batteries / PG handle another sites ( DK-MNS-FRSKOR1_0479DE & Baramoun & DK-DEMYANA-PS_0731DE ) | Faulty System | batt | Batteries | 324791 | DK-KFR-KURDI | C9_0587DE_PH09 | Batteries | Item(s) stolen/No backup batteries.
IM776051 | 3669UP | 0281_N_BS-NAEM-VLG_3669UP_X | Commercial power cutoff and weak backup batteries PLVD disconencted the site loads to save the linked sites P.G connected and site back on air | Faulty System | backup | Batteries | 355953 | 01_N_BS-NAEM-VLG_3669UP | C1_3669UP_PH15 | Batteries | Components faulty/The DC voltage dropped to 47.97 V. after 1 min. of disconnecting the power
IM776051 | 3669UP | 0281_N_BS-NAEM-VLG_3669UP_X | Commercial power cutoff and weak backup batteries PLVD disconencted the site loads to save the linked sites P.G connected and site back on air | Faulty System | batt | Batteries | 355953 | 01_N_BS-NAEM-VLG_3669UP | C1_3669UP_PH15 | Batteries | Components faulty/The DC voltage dropped to 47.97 V. after 1 min. of disconnecting the power
IM776082 | 3344DE | 0681_S_BH-ELNEGILY_3344DE | Share VF / Main Power / stolen Batteries / PG handle another sites ( BH-SAHALI_3844DE & BH-MNSHT-HLBWI_3710DE ) | Faulty System | batt | Batteries | 304214 | BH-ELNEGILY | C3_3344DE_PH12 | Batteries | Item(s) stolen/There is no battery for site
IM776085 | 0479DE | 0591_S_DK-MNS-FRSKOR1_0479DE | Main Power @ DK-MNS-FRSKOR1_0479DE / Stolen batteries / PG connected | Faulty System | batt | Batteries | 356389 | DK-MNS-FRSKOR1 | C3_0479DE_PH7 | Batteries | Some parts are (missing / stolen)/stolen batteries
IM776122 | 3628DE | 0811_S_GH-QSR-BAGHDAD_3628DE | Main power / stolen batteries / PG handle another sites ( GH-GASTA_0833DE & GH-SHBRA-NAMLA_3354DE ) / PG connected | Faulty System | batt | Batteries | 324836 | GH-QSR-BAGHDAD | C2_3628DE_PH13 | Batteries | Item(s) stolen/Stolen batteries
IM776150 | 0673CA | 02654_S_0673CA_ASMA-FAHMY | down due to power probelm @ 0673CA_ASMA-FAHMY and battery weak | Faulty System | batt | Batteries | 356212 | ASMA-FAHMY | C1_0673CA_PH8 | Batteries | Some parts are (missing / stolen)/missing batteries
IM776189 | 0011RE | 03426_G_0011RE_SZ-HW33-7 | DG stoppage / stolen batteries / cleared after Gen restored | Faulty System | batt | Batteries | 356077 | 01_G_SZ-HW33-7_0011RE | C1_0011RE_PH1 | Batteries | Some parts are (missing / stolen)/Battery string stolen
IM776189 | 0011RE | 03426_G_0011RE_SZ-HW33-7 | DG stoppage / stolen batteries / cleared after Gen restored | Faulty System | DG | Generator | 356077 | 01_G_SZ-HW33-7_0011RE | C1_0011RE_PH1 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage
IM776189 | 0011RE | 03426_G_0011RE_SZ-HW33-7 | DG stoppage / stolen batteries / cleared after Gen restored | Faulty System | Gen | Generator | 356077 | 01_G_SZ-HW33-7_0011RE | C1_0011RE_PH1 | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage
IM776189 | 0011RE | 03426_G_0011RE_SZ-HW33-7 | DG stoppage / stolen batteries / cleared after Gen restored | Faulty System | DG | Generator | 356077 | 01_G_SZ-HW33-7_0011RE | C1_0011RE_PH1 | ATS / Engine | Wrong connection/Power cable has no terminal & worng connection , the two cables should be in one terminal
IM776189 | 0011RE | 03426_G_0011RE_SZ-HW33-7 | DG stoppage / stolen batteries / cleared after Gen restored | Faulty System | Gen | Generator | 356077 | 01_G_SZ-HW33-7_0011RE | C1_0011RE_PH1 | ATS / Engine | Wrong connection/Power cable has no terminal & worng connection , the two cables should be in one terminal
IM776202 | 0479DE | 0591_S_DK-MNS-FRSKOR1_0479DE | Main Power @ DK-MNS-FRSKOR1_0479DE / Stolen batteries / PG connected | Faulty System | batt | Batteries | 356389 | DK-MNS-FRSKOR1 | C3_0479DE_PH7 | Batteries | Some parts are (missing / stolen)/stolen batteries
IM776421 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/stolen battery/clear after check Gn | Faulty System | batt | Batteries | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | Batteries | Some parts are missing/Battery cabinet need cleaning (from inside) and holes need sealing.
IM776421 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/stolen battery/clear after check Gn | Faulty System | batt | Batteries | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | Batteries | Some parts are missing/Batteries poles need have missing covers.
IM776421 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/stolen battery/clear after check Gn | Faulty System | GN | Generator | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | ATS / Engine | Components faulty/Generator has bad performance and need overall.
IM776421 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/stolen battery/clear after check Gn | Faulty System | GN | Generator | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | ATS / Engine | Panorama pictures for each system/Overview.
IM776434 | 0553CA | 02127_N_0553CA_SATA | down due to power problem and battery weak | Faulty System | batt | Batteries | 345282 | SATA | C1_0553CA_PH5 | Rectifiers | Alarms reporting to the OMC/Major alarm is active on the rectifier
IM776434 | 0553CA | 02127_N_0553CA_SATA | down due to power problem and battery weak | Faulty System | batt | Batteries | 345282 | SATA | C1_0553CA_PH5 | Batteries | Components faulty/DC voltage dropped to 47.6 V. after 10 seconds of power disconnecting
IM776434 | 0553CA | 02127_N_0553CA_SATA | down due to power problem and battery weak | Faulty System | batt | Batteries | 345282 | SATA | C1_0553CA_PH5 | Batteries | Some parts are (missing / stolen)/Stolen cables of battery string 1
IM776448 | 0657CA | 01766_S_0657CA_BAGDAD-ST | down due to power failure and dead batteries | Faulty System | batt | Batteries | 345255 | BAGDAD-ST | C7_0657CA_PH8 | Batteries | Some parts are missing/missing batteries/ stolen
IM776477 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem and access VF problem and stolen batt | Faulty System | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | Batteries | Some parts are (missing / stolen)/missing battereis
IM776482 | 3394DE | 0011_S_B-SAFT-KHALED_3394DE | Share VF / Main Power / Weak Batteries / PG connected | Faulty System | batt | Batteries | 304033 | BH-SAFT-KHALED | C1_3394DE_PH13 | Batteries | Components faulty/Faulty battery
IM776483 | 0983DE | 1771_S_DK-MIT-ANTAR_0983DE | Main power / stolen batteries / PG handle another sites ( DK-MNS-FRSKOR1_0479DE & Baramoun & DK-DEMYANA-PS_0731DE ) | Faulty System | batt | Batteries | 324896 | DK-MIT-ANTAR | C8_0983DE_PH11 | Batteries | Item(s) stolen/stolen batteries
IM776540 | 0050DE | 0001_S_GH-SHABSHR-HAS_0050DE | Main power @ GH-SHABSHR-HAS_0050DE / batteries under check | Faulty System | batt | Batteries | 304298 | GH-SHABSHR-HAS | C1_0050DE_PH1 | Batteries | Some parts are missing/cover
IM776640 | 3511DE | 1181_D_DK-NUZUL_3511DE | GN problem / weak batteries | Faulty System | GN | Generator | 345377 | DK-NUZUL | C6_3511DE_PH13 | ATS / Engine | Components faulty/Faulty module.
IM776640 | 3511DE | 1181_D_DK-NUZUL_3511DE | GN problem / weak batteries | Faulty System | GN | Generator | 345377 | DK-NUZUL | C6_3511DE_PH13 | ATS / Engine | Wrong connection/Radiator has bad water feeding.

## Connection2
ID | Problem source site code | Problem source site name | Solution | Global Key Word | Global System | Key Word | System | ReportID | Site Name | Site Code | Sub-Class/Criteria/Comment | Incident Start Time | Audit Date | Audit Before Incident
IM758089 | 0427DE | 0061_D_SK-EZBA-SARYA_0427DE | GN problem/ stolen batteries /clear after check GN | batt GN | Batteries Generator | batt GN | Batteries Generator | 345382 | SK-EZBA-SARYA | C2_0427DE_PH4 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) (ATS / Engine/Components faulty/Exhaust fan not working and another not exist) | 2019-08-31 20:04 | 2019-06-16 | TRUE
IM758124 | 3335DE | 0741_D_SK-BERMAKIM_3335DE | GN. Problem / stolen batteries / Clear after check GN | batt GN | Batteries Generator | batt GN | Batteries Generator | 303888 | SK-BERMAKIM | C2_3335DE_PH12 | (Batteries/Item(s) stolen/No backup batteries.) (ATS / Engine/Wrong connection/Sensor has disconnected cable.) (ATS / Engine/Panorama pictures for each system/Overview.) (ATS / Engine/Panorama pictures for each system/Generator has key (no logbook found).) | 2019-08-31 21:57 | 2019-01-19 | TRUE
IM758129 | 0153RE | 03564_Q_0153RE_RS-HILTON-SAHL | DG Stopped due fuel problem , weak batteries //PLVD activated once DG Fix and power restored site Recovered | batt DG PLVD | Batteries Generator Rectifier | DG | Generator | 355600 | 01_H_RS-HILTON-SAHL_0153RE | C1_0153RE_PH8 | (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/check terminals) | 2019-08-31 23:47 | 2019-06-29 | TRUE
IM758140 | 3948DE | 601_D_SK-SMAKEN-SHRQ_3948DE | GN problem/batteries under investigation/clear after check GN | batt GN | Batteries Generator | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | (Batteries/Some parts are (missing / stolen)/missing battereis) | 2019-08-31 23:15 | 2019-08-14 | TRUE
IM758190 | 4011CA | 02353_V_4011CA_MOSTORD-RD2 | down due to main power cut off and stolen batt. (I) | batt | Batteries | batt | Batteries | 355905 | MOSTORD-RD2 | C1_4011CA_PH17 | (Batteries/Some parts are (missing / stolen)/Batteries are stolen) | 2019-09-01 06:07 | 2019-07-25 | TRUE
IM758230 | 0329RE | 03838_S_0329RE_RS-SENTIDO-DRM | down after ETS DG stoppage and site has dead batteries // Recovered after ET DG fixxed | batt DG | Batteries Generator | DG | Generator | 304289 | 01_S_RS-SENTIDO-DRM_0329RE | C1_0329RE_PH12 | (ATS / Engine/Panorama pictures for each system/Panorama site view in outside site) | 2019-09-01 08:35 | 2019-02-19 | TRUE
IM758243 | 0400UP | 651_S_AT-MOHAMADYAT_0400UP | H.T alarm due to defected A/C capacitor in site AT-MOHAMADYAT_0400UP H.T alarm affected the MW link operation that recovered after HW reset | A/C H.T | A/Cs A/Cs | A/C H.T | A/Cs | 324740 | 01_S_AT-MOHAMADYAT_0400UP | C2_0400UP_PH9 | (A/Cs Cooling / Free Cooling / Ventilation/Components faulty/Ice exist in A/c IDU) (A/Cs Cooling / Free Cooling / Ventilation/Components faulty/Ice exist in A/c ODU) (A/Cs Cooling / Free Cooling / Ventilation/Wrong connection/A/c 1 working without control board) | 2019-09-01 08:51 | 2019-04-04 | TRUE
IM758250 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem and stolen batteries and VF access problem (M) | batt DG | Batteries Generator | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | (Batteries/Some parts are (missing / stolen)/missing battereis) | 2019-09-01 09:14 | 2019-08-14 | TRUE
IM758283 | 0433CA | 01867_S_0433CA_MENYET-SEIRG | down due to C.B tripped and stolen batteries and access problem (M) | batt | Batteries | batt | Batteries | 324693 | MENYET-SEIRG | C2_0433CA_PH3 | (Batteries/Item(s) stolen/Three batteries are stolen) | 2019-09-01 09:40 | 2019-04-01 | TRUE
IM758300 | 0400UP | 651_S_AT-MOHAMADYAT_0400UP | H.T alarm due to defected A/C capacitor in site AT-MOHAMADYAT_0400UP H.T alarm affected the MW link operation that recovered after HW reset | A/C H.T | A/Cs A/Cs | A/C H.T | A/Cs | 324740 | 01_S_AT-MOHAMADYAT_0400UP | C2_0400UP_PH9 | (A/Cs Cooling / Free Cooling / Ventilation/Components faulty/Ice exist in A/c IDU) (A/Cs Cooling / Free Cooling / Ventilation/Components faulty/Ice exist in A/c ODU) (A/Cs Cooling / Free Cooling / Ventilation/Wrong connection/A/c 1 working without control board) | 2019-09-01 10:10 | 2019-04-04 | TRUE
IM758362 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | main power/Stolen batteries/clear after power back | batt | Batteries | batt | Batteries | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-01 10:37 | 2019-05-09 | TRUE
IM758369 | 3489DE | 0461_S_DK-KFR-GHANNAM_3489DE | main power/Stolen batteries/clear after power back | batt | Batteries | batt | Batteries | 325088 | DK-KFR-GHANNAM | C1-3489DE-PH13 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-01 11:29 | 2019-05-09 | TRUE
IM758386 | 3720DE | 0651_D_MF-SK-KARADIS_3720DE | GN problem/Stolen batteries@-SK-KARADIS_3720DE/clear check GN | batt GN | Batteries Generator | batt GN | Batteries Generator | 355737 | MF-SK-KARADIS | C2-3720DE-PH14 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Cables have bad connections, proper terminals and proper installtion are rerquired.) | 2019-09-01 12:09 | 2019-07-07 | TRUE
IM758389 | 3720DE | 0651_D_MF-SK-KARADIS_3720DE | GN problem/Stolen batteries@-SK-KARADIS_3720DE/clear check GN | batt GN | Batteries Generator | batt GN | Batteries Generator | 355737 | MF-SK-KARADIS | C2-3720DE-PH14 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Cables have bad connections, proper terminals and proper installtion are rerquired.) | 2019-09-01 12:10 | 2019-07-07 | TRUE
IM758391 | 0615DE | K_GH-KFR-BAB_20860_1 | main power/Stolen batteries@KFR-BAB_0615DE/clear after power back | batt | Batteries | batt | Batteries | 314420 | GH-KFR-BAB | C15_0615DE_PH14 | (Batteries/Item(s) stolen/stolen batteries) | 2019-09-01 12:25 | 2019-03-06 | TRUE
IM758412 | 0329RE | 03838_S_0329RE_RS-SENTIDO-DRM | ET DG failure -site on PG --PG stoppage and site restored after refueled the PG | DG | Generator | DG | Generator | 304289 | 01_S_RS-SENTIDO-DRM_0329RE | C1_0329RE_PH12 | (ATS / Engine/Panorama pictures for each system/Panorama site view in outside site) | 2019-09-01 13:31 | 2019-02-19 | TRUE
IM758413 | 0786DE | 0201_S_SK-DYARAB-NGM2_0786DE | Hi temp/Clear after check AC's | Hi Temp | A/Cs | Hi Temp | A/Cs | 355736 | SK-DYARAB-NGM2 | C8_0786DE_PH09 | (A/Cs Cooling / Free Cooling / Ventilation/Components faulty/A/C2 isn't working and its CB tripped off.) (A/Cs Cooling / Free Cooling / Ventilation/Cables termination/lugs (AC side), lugs (DC side)/A/C's cables need proper terminals.) (A/Cs Cooling / Free Cooling / Ventilation/Some parts are (missing / stolen)/A/C has missing filters.) | 2019-09-01 11:50 | 2019-07-07 | TRUE
IM758434 | 3916DE | 1191_S_BH-BAYDA-2_3916DE | Main power / weak batteries / Last BDT 18/10/2018 / connect PG / lock 2G | batt | Batteries | batt | Batteries | 355465 | BH-BAYDA-2 | C1_3916DE_PH14 | (Batteries/Components faulty/faulty) | 2019-09-01 13:21 | 2019-06-23 | TRUE
IM758470 | 3565DE | 0531_D_DK-BALAMON_3565DE | GN problem/40Min time discharged batteries@BALAMON_3565DE/clear check GN | batt GN | Batteries Generator | GN | Generator | 325113 | DK-BALAMON | C1-3565DE-PH13 | (ATS / Engine/Panorama pictures for each system/Overview.) (ATS / Engine/Panorama pictures for each system/No ATS diagram.) (ATS / Engine/Panorama pictures for each system/Battery poles need cleaning, wax and covers.) | 2019-09-01 14:56 | 2019-05-14 | TRUE
IM758471 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | main power/Stolen batteries/clear after power back | batt | Batteries | batt | Batteries | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-01 14:57 | 2019-05-09 | TRUE
IM758500 | 3531DE | 1341_D_SK-MIT-EZZ_3531DE | GN. Problem / stolen batteries / clear after checking GN. | batt GN | Batteries Generator | batt GN | Batteries Generator | 303843 | SK-MIT-EZZ | C1-3531DE-PH13 | (Batteries/Item(s) stolen/No backup batteries.) (ATS / Engine/Wrong connection/Generator need proper water feeding and radiator need check.) | 2019-09-01 16:34 | 2019-01-16 | TRUE
IM758538 | 0615DE | K_GH-KFR-BAB_20860_1 | main power/Stolen batteries@KFR-BAB_0615DE/clear after power back | batt | Batteries | batt | Batteries | 314420 | GH-KFR-BAB | C15_0615DE_PH14 | (Batteries/Item(s) stolen/stolen batteries) | 2019-09-01 17:16 | 2019-03-06 | TRUE
IM758541 | 0222RE | 03824_G_0222RE_RS-FLAMNCO-HTL | DG failure -site on PG --PG stoppage and site restored after refueled the PG | DG | Generator | DG | Generator | 355690 | 01_G_RS-FLAMNCO-HTL_0222RE | C1_0222RE_PH09 | (ATS / Engine/Components faulty/need battery) | 2019-09-01 18:40 | 2019-01-20 | TRUE
IM758557 | 3714UP | 01_D_SHKH-FDL-GAP-2_3714UP | ET shared generator stopped due to technical error and solved after ET FM team intervention Site has weak backup batteries | backup batt Gen generator | Batteries Batteries Generator Generator | Gen generator | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | (ATS / Engine/Components faulty/Gen battery is faulty) (ATS / Engine/Components faulty/Main c.b inside gen had one faulty slot and one phase welded directly) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage exist under fuel tank) (ATS / Engine/Panorama pictures for each system/Open gland in Gen enclosure need insulation) (ATS / Engine/Panorama pictures for each system/Panorama site view in outside site) (ATS / Engine/Panorama pictures for each system/Last Gen hour meter at Audit G (18510 )) | 2019-09-01 18:03 | 2019-03-13 | TRUE
IM758573 | 3718DE | 0241_S_MF-ABU-HASAN_3718DE | Main Power / batteries under investigation/clear after power back | batt | Batteries | batt | Batteries | 324625 | MF-ABU HASAN | C1_3718DE_PH14 | (Batteries/Item(s) stolen/stolen batteries) | 2019-09-01 18:57 | 2019-03-26 | TRUE
IM758581 | 0418DE | 0081_H_DK-OLELA_0418DE | Generator fault due to hot weather crisis | Gen generator | Generator Generator | Gen generator | Generator | 356228 | DK-OLELA | C1_0418DE_PH4 | (ATS / Engine/Alarms reporting to the OMC/Generator alarm need adjust.) | 2019-09-01 19:43 | 2019-09-07 | FALSE
IM758591 | 3390UP | 0601_D_AT-MAGRIS_3390UP | Generator stopped due to LOP alarm as engine need overhauling action Site has weak backup batteries | backup batt Gen generator | Batteries Batteries Generator Generator | Gen generator | Generator | 304086 | 01_G_AT-MAGRIS_3390UP | C2_3390UP_PH14 | (ATS / Engine/Item(s) stolen/Gen Battery was missing and Battery cables are not isolated) | 2019-09-01 20:03 | 2019-01-31 | TRUE
IM758641 | 0876DE | 0641_Q_PS-RSD-02_0876DE | Access GA / GN problem / last BDT @ 19 OCT 2018 is 02:30 | GN | Generator | GN | Generator | 324939 | PS-RSD-02 | C4_0876DE_PH09 | (ATS / Engine/Components faulty/faulty cover) (ATS / Engine/Components faulty/faulty battery and no poles' covers) (ATS / Engine/Components faulty/replace) (ATS / Engine/Components faulty/faulty radiator) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM organization/arrange and add duct cover and labels) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/clean) (ATS / Engine/Wrong connection/Generator has bad water feeding.) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM organization/Cables need arrangement and unused need to be removed.) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM organization/Cable need adjust or replacement.) (ATS / Engine/Panorama pictures for each system/Overview.) (ATS / Engine/Panorama pictures for each system/Batteries poles need cleaning, wax and cover.) | 2019-09-01 23:15 | 2019-04-24 | TRUE
IM758683 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | Access VF Guard/GN problem/Stolen batteries/clear by check GN | batt GN | Batteries Generator | batt GN | Batteries Generator | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | (Batteries/Item(s) stolen/There is no battery for site) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cable has damaged protective isolation) | 2019-09-02 02:12 | 2019-05-09 | TRUE
IM758687 | 0222RE | 03824_G_0222RE_RS-FLAMNCO-HTL | DG failure -site on PG --PG stoppage and site restored after refueled the PG | DG | Generator | DG | Generator | 355690 | 01_G_RS-FLAMNCO-HTL_0222RE | C1_0222RE_PH09 | (ATS / Engine/Components faulty/need battery) | 2019-09-02 02:58 | 2019-01-20 | TRUE
IM758702 | 3656DE | 0431_E_SK-BANI-HILAL_3656DE | GN problem/Stolen batteries/clear after check GEN | batt Gen GN | Batteries Generator Generator | batt Gen GN | Batteries Generator | 345380 | SK-BANI-HILAL | C04-3656DE-PH13 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot) | 2019-09-02 04:22 | 2019-06-16 | TRUE
IM758703 | 3413DE | 0801_D_PS-KHADIGA_3413DE | GN problem @PS-KHADIGA_3413DE / last BDT @ 28 OCT 2017 is 03:00 | GN | Generator | GN | Generator | 324940 | PS-KHADIGA | C2_3413DE_PH13 | (ATS / Engine/Components faulty/faulty) (ATS / Engine/Wrong connection/remove cable) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM organization/Unused cable need to be removed.) (ATS / Engine/Panorama pictures for each system/Overview.) | 2019-09-02 05:11 | 2019-04-24 | TRUE
IM758738 | 0418DE | 0081_H_DK-OLELA_0418DE | GN problem/Weak batteries /clear | batt GN | Batteries Generator | GN | Generator | 356228 | DK-OLELA | C1_0418DE_PH4 | (ATS / Engine/Alarms reporting to the OMC/Generator alarm need adjust.) | 2019-09-02 07:10 | 2019-09-07 | FALSE
IM758761 | 0222RE | 03824_G_0222RE_RS-FLAMNCO-HTL | DG failure -site on PG --PG stoppage and site restored after refueled the PG | DG | Generator | DG | Generator | 355690 | 01_G_RS-FLAMNCO-HTL_0222RE | C1_0222RE_PH09 | (ATS / Engine/Components faulty/need battery) | 2019-09-02 08:48 | 2019-01-20 | TRUE
IM758786 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem and stolen battery and PG access | batt DG | Batteries Generator | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | (Batteries/Some parts are (missing / stolen)/missing battereis) | 2019-09-02 09:04 | 2019-08-14 | TRUE
IM758791 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN. Problem / stolen batteries / Handling 1651_D_SK-REFAEEN_3841DE / clear after checking GN. | batt GN | Batteries Generator | batt GN | Batteries Generator | 324500 | SK-AZZAZI | C1_4029DE_PH15 | (Batteries/Item(s) stolen/No backup batteries.) (ATS / Engine/Wrong connection/Some cables are disconnected and need adjust.) (ATS / Engine/Panorama pictures for each system/Generator battery poles need cleaning, wax and covers.) (ATS / Engine/Panorama pictures for each system/Overview.) | 2019-09-02 08:03 | 2019-03-13 | TRUE
IM758794 | 0300DE | U_G_BH-NEW-NUBARIYA_0300DE | GN problem / weak batteries / recovered after solved GN problem | batt GN | Batteries Generator | GN | Generator | 356082 | New_Nobarya | C3_0300DE_PH3 | (ATS / Engine/Unit earth/Missing earthling) (ATS / Engine/Wrong connection/Wrong connection) | 2019-09-02 08:06 | 2019-08-22 | TRUE
IM758795 | 4005DE | 0751_D_DK-BASHALOSH_4005DE | GEN problem/Weak batteries/clear after check GEN | batt Gen | Batteries Generator | Gen | Generator | 356229 | DK-BASHALOSH | C4_4005DE_PH15 | (ATS / Engine/Unit earth/Disconnected earth cable.) (ATS / Engine/Components faulty/Battery poles need cleaning, wax and covers.) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Neutral bar need adjust.) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Some cables need proper terminals.) | 2019-09-02 08:19 | 2019-09-07 | FALSE
IM758807 | 3971DE | 0511_S_GH-ABU-GENDI_3971DE | Access PG / Main power / Batteries D9 | batt | Batteries | batt | Batteries | 324794 | GH-ABU-GENDI | C1_3971DE_PH15 | (Batteries/Item(s) stolen/stolen batteries) | 2019-09-02 08:45 | 2019-04-10 | TRUE
IM758826 | 3349CA | 01126_S_3349CA_IMBABA-6 | down due to commercial cut and faulty batteries (MA) | batt | Batteries | batt | Batteries | 303961 | IMBABA-6 | C2_3349CA_PH12 | (Batteries/Components faulty/Batteries are in a very bad condition (DC voltage dropped to 42.7V. after 1 min of power disconnecting)) | 2019-09-02 09:44 | 2019-01-21 | TRUE
IM758865 | 3943DE | 0921_S_SK-AKRASH_3943DE | access ET Guard/ET GEN problem/Stolen batteries @ SK-AKRASH_3943DE/clear on PG/PG can't carry all load | batt Gen | Batteries Generator | batt | Batteries | 303886 | SK-AKRASH | C1_3943DE_PH15 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-02 09:15 | 2019-01-19 | TRUE
IM758872 | 3971DE | 0511_S_GH-ABU-GENDI_3971DE | Access ET / Main power / stolen batteries / connected PG | batt | Batteries | batt | Batteries | 324794 | GH-ABU-GENDI | C1_3971DE_PH15 | (Batteries/Item(s) stolen/stolen batteries) | 2019-09-02 09:28 | 2019-04-10 | TRUE
IM758891 | 0370UP | 1961_G_CAIRO-ASWAN-12_0370UP | Main Power Disconnection, stolen batteries, Autoecovered. | batt | Batteries | batt | Batteries | 304136 | 01_G_CAIRO-ASWAN-12_0370UP | C2_0370UP_PH8 | (Batteries/Item(s) stolen/ Batteries were stolen) | 2019-09-02 10:12 | 2019-02-07 | TRUE
IM758900 | 0442AL | 2401_S_AWAYED-NTH_0442AL | Down Due To Main Power Cutting / Batteries Stolen / PG Access Problem / On Air After Main Power Auto Recovered | batt | Batteries | batt | Batteries | 345440 | S_AWAYED-NTH_0442AL | C2_0442AL_PH9 | (Batteries/Some parts are (missing / stolen)/Stolen Batteries) | 2019-09-02 09:58 | 2019-06-25 | TRUE
IM758940 | 0278CA | 02185_N_0278CA_ABBOUD | down due to main power failure stolen batteries and access PG at site 0278CA_ABBOUD | batt | Batteries | batt | Batteries | 304055 | ABBOUD | C1_0278CA_PH3 | (Batteries/Item(s) stolen/Batteries and cables are stolen) | 2019-09-02 11:05 | 2019-01-29 | TRUE
IM758972 | 0646CA | 02128_N_0646CA_OM-BAYOUMI | down due to power problem and battery faulty @ 0646CA_OM-BAYOUMI | batt | Batteries | batt | Batteries | 345350 | OM-BAYOUMI | C3_0646CA_PH8 | (Rectifiers/Alarms reporting to the OMC/Major alarm is active on the site) (Batteries/Components faulty/Batteries are faulty (Site is down when the power is disconnected)) | 2019-09-02 11:20 | 2019-06-17 | TRUE
IM758980 | 0242CA | 01963_S_0242CA_10TH-RSD2 | DG Stopped , weak batteries , Recovered once DG fix | batt DG | Batteries Generator | batt | Batteries | 356353 | 10TH-RSD2 | C4_0242CA_PH2 | (Batteries/Some parts are (missing / stolen)/Battery string stolen) | 2019-09-02 11:33 | 2019-09-21 | FALSE
IM758985 | 3740DE | 0521_S_KS-MNSHT-ABS_3740DE | Access TE / Main power / stolen batteries | batt | Batteries | batt | Batteries | 324805 | KS-MNSHT-ABS | C1_3740DE_Ph14 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-02 10:38 | 2019-04-08 | TRUE
IM758986 | 0963CA | 02149_S_0963CA_OM-BAYOUMI-WST | down due to power problem and battery faulty @ 0646CA_OM-BAYOUMI | batt | Batteries | batt | Batteries | 345290 | OM-BAYOUMI-WST | C3_0963CA_PH9 | (Rectifiers/Alarms reporting to the OMC/Minor alarm appears on the rectifier due to high battery temp.) | 2019-09-02 11:35 | 2019-06-11 | TRUE
IM759040 | 3526CA | U_V_3526CA_CORNISH-SAHEL | down due to power problem and stolen battery @ 0278CA_ABBOUD | batt | Batteries | batt | Batteries | 355732 | CORNISH-SAHEL | C1_3526CA_PH13 | (Rectifiers/Alarms reporting to the OMC/Power and rectifier alarms don't appear on the OMC) | 2019-09-02 12:11 | 2019-07-06 | TRUE
IM759252 | 3499UP | 1871_S_AS-GAFAR-SADK_3499UP_X | Main Power Disconnection, stolen Batteries, PG Connected | batt | Batteries | batt | Batteries | 356189 | 01_S_AS-GAFAR-SADK_3499UP | C1_3499UP_PH14 | (Batteries/Some parts are (missing / stolen)/Site Batteries were stolen) | 2019-09-02 15:18 | 2019-09-03 | FALSE
IM759283 | 3532DE | 0511_S_SK-NATORA_3532DE | VF GEN problem/stolen batteries/clear afetr check VF GEN | batt Gen | Batteries Generator | batt | Batteries | 356262 | SK-NATORA | C2_3532DE_PH13 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-02 15:09 | 2019-09-11 | FALSE
IM759370 | 0983DE | 1771_S_DK-MIT-ANTAR_0983DE | Main Power / Stolen batteries / connect PG | batt | Batteries | batt | Batteries | 324896 | DK-MIT-ANTAR | C8_0983DE_PH11 | (Batteries/Item(s) stolen/stolen batteries) | 2019-09-02 18:09 | 2019-04-14 | TRUE
IM759372 | 3955DE | 0731_S_SK-QRMT-SAHBRA_3955DE | Main Power / Weak batteries/P.G handel nodal sites | batt | Batteries | batt | Batteries | 356230 | SK-QRMT-SAHBRA | C1_3955DE_PH15 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-02 18:33 | 2019-09-07 | FALSE
IM759408 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to generator problem (fuel theft case ) and restored | Gen generator | Generator Generator | Gen generator | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | (ATS / Engine/Wrong connection/wrong connections) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/floating hoses) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/unprotected cable) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage) | 2019-09-02 20:28 | 2019-03-26 | TRUE
IM759411 | 3656DE | 0431_E_SK-BANI-HILAL_3656DE | GN problem/Stolen batteries/Clear after check GN | batt GN | Batteries Generator | batt GN | Batteries Generator | 345380 | SK-BANI-HILAL | C04-3656DE-PH13 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot) | 2019-09-02 19:50 | 2019-06-16 | TRUE
IM759424 | 0112RE | 03828_H_0112RE_QUSER-MARSA3 | DG Stopped , dead batteries , PLVD disconnected Sites , once team arrived and fix DG Site Recovered | batt DG PLVD | Batteries Generator Rectifier | DG | Generator | 355488 | 01_W_QUSER-MARSA3_0112RE | C4_0112RE_PH4 | (ATS / Engine/Unit earth/Gen enclosure earth cable is missing) (ATS / Engine/Components faulty/Gen battery is faulty) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Two cables inserted in one slot and not teminated can cause bad connections) | 2019-09-02 20:56 | 2019-06-25 | TRUE
IM759438 | 0469DE | 0741_D_MF-ABU-MASHHOR_0469DE | HT. @ 0741_D_MF-ABU-MASHHOR_0469DE / clear after checking ACs | Acs HT. | A/Cs A/Cs | Acs HT. | A/Cs | 304342 | MF-ABU-MASHHOR | C2_0469DE_PH6 | (A/Cs Cooling / Free Cooling / Ventilation/Components faulty/not cooling) (A/Cs Cooling / Free Cooling / Ventilation/Components faulty/faulty A/C) | 2019-09-02 20:36 | 2019-02-26 | TRUE
IM759452 | 0658DE | 0661_D_BH-MNSHYT-KHYAT_0658DE | GN problem @ BH-MNSHYT-KHYAT_0658DE / BDT @ 24/05/2019 is : 1.00 hr | GN | Generator | GN | Generator | 356260 | BH-MNSHYT-KHYAT | C2_0658DE_PH9 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has leakage) (ATS / Engine/Components below/over rate (excluding main power feeder if not hot)/Generator has high voltage) | 2019-09-02 22:06 | 2019-09-05 | FALSE
IM759469 | 3499UP | 1871_S_AS-GAFAR-SADK_3499UP_X | Main Power Disconnection, Stolen Batteries, PG Connected. | batt | Batteries | batt | Batteries | 356189 | 01_S_AS-GAFAR-SADK_3499UP | C1_3499UP_PH14 | (Batteries/Some parts are (missing / stolen)/Site Batteries were stolen) | 2019-09-02 22:48 | 2019-09-03 | FALSE
IM759484 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | access VF/VF. GN. Problem /Stolen batteries / clear on PG. | batt GN | Batteries Generator | batt GN | Batteries Generator | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | (Batteries/Item(s) stolen/There is no battery for site) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cable has damaged protective isolation) | 2019-09-02 23:32 | 2019-05-09 | TRUE
IM759508 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to DG fuel run out and PLD disconnect loads and access problem with SOC 1727 (M) | DG | Generator | DG | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | (ATS / Engine/Wrong connection/wrong connections) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/floating hoses) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/unprotected cable) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage) | 2019-09-03 01:26 | 2019-03-26 | TRUE
IM759521 | 4251DE | 03304_S_4251DE_QL-ABU-GHIT2 | main power/stolen batteries/clear after power back | batt | Batteries | batt | Batteries | 355722 | QL-ABU-GHIT2 | C1_4251DE_PH17 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) | 2019-09-03 03:05 | 2019-07-04 | TRUE
IM759527 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to DG fuel run out and access with SOC problem No 1727 (M) | DG | Generator | DG | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | (ATS / Engine/Wrong connection/wrong connections) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/floating hoses) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/unprotected cable) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage) | 2019-09-03 03:58 | 2019-03-26 | TRUE
IM759548 | 3548UP | 711_S_AT-BANI-MAGD_3548UP | Commercial power cutoff and weak backup batteries VF guard night access problem till 08:00 AM P.G connected and site back on air | backup batt | Batteries Batteries | backup batt | Batteries | 324828 | LU-GZRT-BAIRAT | C1_4211UP_PH19 | (Batteries/Item(s) stolen/Batteries were stolen) | 2019-09-03 04:34 | 2019-04-14 | TRUE
IM759612 | 3916DE | 1191_S_BH-BAYDA-2_3916DE | Main power / weak batteries / Last BDT 18/10/2018 | batt | Batteries | batt | Batteries | 355465 | BH-BAYDA-2 | C1_3916DE_PH14 | (Batteries/Components faulty/faulty) | 2019-09-03 08:08 | 2019-06-23 | TRUE
IM759613 | 0605DE | 0041_S_DK-MAHMUDIYYA_0605DE | Main power @ DK-MAHMUDIYYA_0605DE / stolen batteries | batt | Batteries | batt | Batteries | 304053 | DK-MAHMUDIYYA | C2_0605DE_PH9 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-03 08:23 | 2019-01-29 | TRUE
IM759623 | 3894CA | 02231_S_3894CA_REHAB-STAGE7 | down due to DG problem and battery stolen | batt DG | Batteries Generator | batt | Batteries | 356204 | REHAB-STAGE7 | C1_3894CA_PH17 | (Batteries/Some parts are (missing / stolen)/missing batteries) | 2019-09-03 08:51 | 2019-08-14 | TRUE
IM759659 | 0433CA | 01867_S_0433CA_MENYET-SEIRG | down due to power meter problem and battery faulty and PG accessed | batt | Batteries | batt | Batteries | 324693 | MENYET-SEIRG | C2_0433CA_PH3 | (Batteries/Item(s) stolen/Three batteries are stolen) | 2019-09-03 09:13 | 2019-04-01 | TRUE
IM759667 | 0418DE | 0081_H_DK-OLELA_0418DE | GN problem/Weak batteries/clear after check GN | batt GN | Batteries Generator | GN | Generator | 356228 | DK-OLELA | C1_0418DE_PH4 | (ATS / Engine/Alarms reporting to the OMC/Generator alarm need adjust.) | 2019-09-03 09:25 | 2019-09-07 | FALSE
IM759732 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Gen generator | Generator Generator | Gen generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | (ATS / Engine/Wrong connection/external cable to the guard connected from gen and not protected) (ATS / Engine/Wrong connection/One Contactor turned on by setting wood inside it) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cables not protected in tube) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cables not protected) (ATS / Engine/Item(s) stolen/Gen battery is missing) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/ Fuel leakage inside Gen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage inside Gen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage beisde Gen enclosure area need cleaning) (ATS / Engine/Panorama pictures for each system/Open gland in Gen enclosure need insulation) (ATS / Engine/Panorama pictures for each system/Panorama site view in outside site) (ATS / Engine/Panorama pictures for each system/Last Gen hour meter at Audit G ( 31148 )) | 2019-09-03 11:01 | 2019-01-16 | TRUE
IM759749 | 0370UP | 1961_G_CAIRO-ASWAN-12_0370UP | Main Power Disconnection, Weak Batteries, Autorecovered. | batt | Batteries | batt | Batteries | 304136 | 01_G_CAIRO-ASWAN-12_0370UP | C2_0370UP_PH8 | (Batteries/Item(s) stolen/ Batteries were stolen) | 2019-09-03 11:05 | 2019-02-07 | TRUE
IM759755 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | batt DG Gen | Batteries Generator Generator | DG Gen | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/OIL & fuel leakage ) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage ) (ATS / Engine/Unit earth/alternator not earthed) (ATS / Engine/Unit earth/earth bar not connected to main earth bar ) (ATS / Engine/Unit earth/earth cable not connected ) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/cable not terminated ) | 2019-09-03 11:22 | 2019-07-03 | TRUE
IM759795 | 3532DE | 0511_S_SK-NATORA_3532DE | access VF/VF GN problem/Stolen batteries/clear after GN working | batt GN | Batteries Generator | batt | Batteries | 356262 | SK-NATORA | C2_3532DE_PH13 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-03 10:45 | 2019-09-11 | FALSE
IM759806 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Generator stopped due to LOP as engine need overhauling action Site has weak backup batteries | backup batt Gen generator | Batteries Batteries Generator Generator | Gen generator | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage of the engine) (ATS / Engine/Unit earth/Stolen earth connections of the genset panel) (ATS / Engine/Components faulty/The rubber bases of the radiator are faulty) (ATS / Engine/Components faulty/The dynamo belt needs to be tensioned) (ATS / Engine/Wrong connection/The negative pole of the battery isn't connected) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Missing terminals of cables connected to contactors and CBs inside the genset panel) | 2019-09-03 11:41 | 2019-07-30 | TRUE
IM759808 | 0608UP | 1071_D_MN-BANI-ROH_0608UP | Owner of the site switched off the main Generator C.B due to his own problems Site has weak backup batteries | backup batt Gen generator | Batteries Batteries Generator Generator | Gen generator | Generator | 356181 | 01_G_MN-BANI-ROH_0608UP | C1_0608UP_PH9 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage) (ATS / Engine/Components faulty/faulty battery) (ATS / Engine/Components faulty/need battery) (ATS / Engine/Wrong connection/remove wrong connection) | 2019-09-03 12:13 | 2019-08-28 | TRUE
IM759843 | 3866DE | 2001_D_DK-SANBAKHT_3866DE | Access Guard / GN problem / stolen batteries | batt GN | Batteries Generator | GN | Generator | 304185 | DK-SANBAKHT | C3_3866DE_PH14 | (ATS / Engine/Components faulty/screen need repair) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/protect by tray ) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/protect) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check oil leakage ) | 2019-09-03 11:15 | 2019-02-07 | TRUE
IM759856 | 3948UP | 0111_S_BS-MNSHAT-ASEM_3948UP_X | Generator stopped due to dynamo problem and changed Site has weak backup batteries | backup batt Gen generator | Batteries Batteries Generator Generator | backup batt Gen generator | Batteries Generator | 356347 | 01_S_BS-MNSHAT-ASEM_3948UP | C1_3948UP_PH16 | (Batteries/Some parts are (missing / stolen)/Batteries are stolen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil and water leakage of the engine) (ATS / Engine/Components faulty/Faulty display of the genset) (ATS / Engine/Components faulty/Defected rubber bases of the radiator) (ATS / Engine/Components faulty/Broken cover of the genset) (ATS / Engine/Components faulty/The rain cap is broken) (ATS / Engine/Wrong connection/The genset battery is disconnected) (ATS / Engine/Wrong connection/Equipments are not fixed and disconnected cables inside the genset panel) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Missing terminals of power cables connected inside the genset panel) (ATS / Engine/Filters condition oil/fuel/air/The air filter and cover aren't fixed) | 2019-09-03 12:38 | 2019-09-17 | FALSE
IM759911 | 3892DE | 0171_S_BH-ZWIT-HUMOR_3892DE | Main power / stolen batteries / Rectifier Module faulty | batt rect | Batteries Rectifier | batt | Batteries | 324905 | BH-ZWIT-HUMOR | C1_3892DE_PH14 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-03 12:36 | 2019-04-17 | TRUE
IM759946 | 0481UP | 0331_Q_SG-QARAN_0481UP | Owner Deliberatly switched off main Generator C.B Due to Finincial problem, solved. | Gen generator | Generator Generator | Gen generator | Generator | 356515 | 01_H_SG-QARAN_0481UP | C1_0481UP_PH9 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage beside Gen enclosure ) (ATS / Engine/Unit earth/Gen earth bar is not fixed ) (ATS / Engine/Components faulty/Gen need new battery) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/ Missing terminals at gen C.B inside Ats panel) | 2019-09-03 14:14 | 2019-10-10 | FALSE
IM759964 | 0223RE | 03853_G_0223RE_RS-VERA-CLUB | DG Stopped , Stolen batteries , Recovered once DG problem solved | batt DG | Batteries Generator | batt DG | Batteries Generator | 355521 | 01_G_RS-VERA-CLUB_0223RE | C1_0223RE_PH9 | (Rectifiers/Alarms reporting to the OMC/Rectifer alarm not appeared on the omc ( looped at ddf racl )) (Batteries/Some parts are (missing / stolen)/some of site batteries missing poles covers) (ATS / Engine/Unit earth/Gen earth cable is missing) (ATS / Engine/Components faulty/Emergency stop not working) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Two cables inserted in one slot and not teminated can cause bad connections) | 2019-09-03 14:32 | 2019-06-27 | TRUE
IM759984 | 3124UP | 1761_S_AS-SILWA-BHRY_3124UP_X | Main Power Disconnection, Stolen Batteries, PG Connected. | batt | Batteries | batt | Batteries | 355937 | 01_S_AS-SILWA-BHRY_3124UP | C1_3124UP_PH13 | (Rectifiers/Alarms reporting to the OMC/Rectifer minor alarm is not appeared on the omc and looped) | 2019-09-03 15:01 | 2019-08-01 | TRUE
IM759997 | 3835DE | 0651_S_SK-SHNT-HRABWA_3835DE | Main Power / stolen batteries @SK-SHNT-HRABWA_3835DE/ Clear after power back | batt | Batteries | batt | Batteries | 345236 | SK-SHNT-HRABWA | C1_3835DE_PH14 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-03 14:30 | 2019-06-03 | TRUE
IM759999 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | access VF/VF GN problem/Stolen batteries | batt GN | Batteries Generator | batt GN | Batteries Generator | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | (Batteries/Item(s) stolen/There is no battery for site) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cable has damaged protective isolation) | 2019-09-03 14:52 | 2019-05-09 | TRUE
IM760001 | 0983DE | 1771_S_DK-MIT-ANTAR_0983DE | Main power / Stolen batteries | batt | Batteries | batt | Batteries | 324896 | DK-MIT-ANTAR | C8_0983DE_PH11 | (Batteries/Item(s) stolen/stolen batteries) | 2019-09-03 14:56 | 2019-04-14 | TRUE
IM760036 | 0646CA | 02128_N_0646CA_OM-BAYOUMI | down due to power problem @ 0646CA_OM-BAYOUMI and weak battery | batt | Batteries | batt | Batteries | 345350 | OM-BAYOUMI | C3_0646CA_PH8 | (Rectifiers/Alarms reporting to the OMC/Major alarm is active on the site) (Batteries/Components faulty/Batteries are faulty (Site is down when the power is disconnected)) | 2019-09-03 15:27 | 2019-06-17 | TRUE
IM760038 | 3089UP | 2141_S_SG-GALAWEYA_3089UP | Main Power Disconnection, Stolen Batteries, PG Connected . | batt | Batteries | batt | Batteries | 356371 | 01_S_SG-GALAWEYA_3089UP | C1_3089UP_PH13 | (Batteries/Some parts are (missing / stolen)/site batteries were Stolen) | 2019-09-03 16:15 | 2019-09-18 | FALSE
IM760101 | 0508DE | 1151_Q_BH-KOM-BERKA_0508DE | GN problem / Solar theft case / Transfer Solar / Connect PG | GN | Generator | GN | Generator | 304064 | BH-KOM-BERKA | C1_0508DE_PH8 | (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cable has damaged protective isolation) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Burned terminals) | 2019-09-03 17:20 | 2019-01-29 | TRUE
IM760103 | 3819CA | 02815_S_3819CA_MADINATY-11 | down due to power problem and battery stolen | batt | Batteries | batt | Batteries | 324704 | MADINATY-11 | C1_3819CA_PH16 | (Batteries/Some parts are missing/missing batteries) | 2019-09-03 16:40 | 2019-03-27 | TRUE
IM760132 | 0427DE | 0061_D_SK-EZBA-SARYA_0427DE | GN problem/stolen batteries | batt GN | Batteries Generator | batt GN | Batteries Generator | 345382 | SK-EZBA-SARYA | C2_0427DE_PH4 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) (ATS / Engine/Components faulty/Exhaust fan not working and another not exist) | 2019-09-03 18:24 | 2019-06-16 | TRUE
IM760146 | 0418DE | 0081_H_DK-OLELA_0418DE | GN problem/Weak batteries/clear after check GN | batt GN | Batteries Generator | GN | Generator | 356228 | DK-OLELA | C1_0418DE_PH4 | (ATS / Engine/Alarms reporting to the OMC/Generator alarm need adjust.) | 2019-09-03 16:20 | 2019-09-07 | FALSE
IM760150 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/Weak batteries/clear after check GN | batt GN | Batteries Generator | batt GN | Batteries Generator | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | (Batteries/Some parts are missing/Battery cabinet need cleaning (from inside) and holes need sealing.) (Batteries/Some parts are missing/Batteries poles need have missing covers.) (ATS / Engine/Components faulty/Generator has bad performance and need overall.) (ATS / Engine/Panorama pictures for each system/Overview.) | 2019-09-03 19:16 | 2019-05-21 | TRUE
IM760205 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | access VF/VF. GN. Problem /Stolen batteries / clear on PG. | batt GN | Batteries Generator | batt GN | Batteries Generator | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | (Batteries/Item(s) stolen/There is no battery for site) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cable has damaged protective isolation) | 2019-09-03 23:55 | 2019-05-09 | TRUE
IM760291 | 0332UP | 0691_G_MN-GABAL-TEIR_0332UP | Commercial power cutoff and STB generator stopped , Site has weak backup batteries , Recovered | backup batt Gen generator | Batteries Batteries Generator Generator | backup batt Gen generator | Batteries Generator | 325017 | 01_G_MN-GABAL-TEIR_0332UP | C1_0332UP_PH8 | (Batteries/Components faulty/battery need to be changed) (ATS / Engine/Components faulty/change it) | 2019-09-04 07:13 | 2019-04-28 | TRUE
IM760329 | 0038CA | S_MAGLESALSHAAB_64597_S1_V | down due to commercial cut and faulty batteries and access problem (MA) | batt | Batteries | batt | Batteries | 355810 | MAGLESALSHAAB | C2_0038CA_PH0 | (Rectifiers/Alarms reporting to the OMC/Major and minor alarms are active on the rectifier (Battery fuse & Psys high)) | 2019-09-04 09:19 | 2019-07-16 | TRUE
IM760334 | 0707DE | 1081_D_GH-RGDYA-MAHLA_0707DE | GN problem @ GH-RGDYA-MAHLA_0707DE / Stolen batteries | batt GN | Batteries Generator | GN | Generator | 324607 | GH-RGDYA-MAHLA | C1_0707DE_PH9 | (ATS / Engine/Item(s) stolen/Missing battery) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Cleaning and isolation) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Clean and fix nut) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Clean) | 2019-09-04 09:02 | 2019-03-17 | TRUE
IM760347 | 3828DE | 0961_S_BH-GWAD-HUSNI_3828DE | Main power / stolen batteries / PG connected | batt | Batteries | batt | Batteries | 356184 | BH-GWAD-HUSNI | C1_3828DE_PH14 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) | 2019-09-04 09:14 | 2019-09-02 | TRUE
IM760391 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | Gen Problem caused site down , Site suffering from (Fueling filter problem) , Site suffering from weak batteries , we need to replace weak batteries Recovered once DG fix | batt DG Gen | Batteries Generator Generator | DG Gen | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/OIL & fuel leakage ) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage ) (ATS / Engine/Unit earth/alternator not earthed) (ATS / Engine/Unit earth/earth bar not connected to main earth bar ) (ATS / Engine/Unit earth/earth cable not connected ) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/cable not terminated ) | 2019-09-04 10:15 | 2019-07-03 | TRUE
IM760422 | 0490SI | 03534_S_0490SI_IS-NASR | Outage power in area located site // access PG // weak batteries Recovered once power restored | batt | Batteries | batt | Batteries | 356007 | 01_S_IS-NASR_0490SI | C2_0490SI_PH14 | (Rectifiers/Alarms reporting to the OMC/Rectifier alarm , A/C & door not apear on CAP) (Batteries/Components faulty/Battery voltag reading drop to 46 volt after we disconnect th rectifier C.B (Check the batteries)) | 2019-09-04 09:52 | 2019-08-07 | TRUE
IM760456 | 3126DE | 0121_S_DK-HAGYZEYA_3126DE | main power/Stolen batteries/handel SK-SAWALEH_3338DE,SK-TELRAK_0798DE,TAMEY-AMDID_0347D | batt | Batteries | batt | Batteries | 355992 | DK-HAGYZEYA | C6-3126DE-PH12 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-04 09:32 | 2019-08-07 | TRUE
IM760471 | 3628DE | 0811_S_GH-QSR-BAGHDAD_3628DE | Main power / stolen batteries / PG connected | batt | Batteries | batt | Batteries | 324836 | GH-QSR-BAGHDAD | C2_3628DE_PH13 | (Batteries/Item(s) stolen/Stolen batteries) | 2019-09-04 10:08 | 2019-04-15 | TRUE
IM760475 | 3352DE | 0071_D_BH-SHBRA-OSEEM_3352DE | Access VF. / Main Power / Stolen batteries / Clear after power back | batt | Batteries | batt | Batteries | 325117 | BH-SHBRA-OSEEM | C1_3352DE_PH12 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-04 10:24 | 2019-05-12 | TRUE
IM760498 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | access VF/VF. GN. Problem /Stolen batteries / clear on PG. | batt GN | Batteries Generator | batt GN | Batteries Generator | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | (Batteries/Item(s) stolen/There is no battery for site) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cable has damaged protective isolation) | 2019-09-04 12:04 | 2019-05-09 | TRUE
IM760522 | 3385DE | 0671_S_BH-GHAZALA-VLG_3385DE | Main power / weak batteries / handle another sites BH-KFR-QASHASH_0545DE & BH-KFR-MUSTNAB_3520de / PG now in way | batt | Batteries | batt | Batteries | 355780 | BH-GHAZALA-VLG | C2_3385DE_PH13 | (Rectifiers/Alarms reporting to the OMC/Site down due to power (Check alarms with OMC)) | 2019-09-04 12:27 | 2019-07-11 | TRUE
IM760530 | 0626DE | 0171_S_BH-KHRABA-FCT_0626DE | Main power/SCG/Weak batteries@KHRABA-FCT_0626DE/ clear after checking GN. | batt GN | Batteries Generator | GN | Generator | 304233 | BH-KHRABA-FCT | C1_0626DE_PH9 | (ATS / Engine/Components faulty/Small generator disconnected and has missing ATS components (To be connected or removed)) (ATS / Engine/Components faulty/Small generator disconnected and has missing ATS components (To be installed or removed)) | 2019-09-04 12:44 | 2019-02-14 | TRUE
IM760553 | 0430CA | U_S_0430CA_MAHMASHAH | down due to Deliberately switched off by owner and battery weak and PG access | batt | Batteries | batt | Batteries | 356046 | SZ-MALLAHA | 0364RE | (Batteries/Some parts are (missing / stolen)/Missing battery pole cover) | 2019-09-04 13:13 | 2019-08-18 | TRUE
IM760610 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Generator stopped , Site has weak backup batteries , Recovered | backup batt Gen generator | Batteries Batteries Generator Generator | Gen generator | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | (ATS / Engine/Components faulty/Gen battery was defected) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM organization/ATS Cables not organized) | 2019-09-04 14:00 | 2019-05-18 | TRUE
IM760630 | 0405RE | 03878_S_0405RE_RS-MRSA-NAKARI | ET DG Stopped , No Backup installed , once DG problem solved site recovered | backup DG | Batteries Generator | backup | Batteries | 356420 | 01_S_RS-MRSA-NAKARI_0405RE | C1_0405RE_PH15 | (Batteries/Some parts are (missing / stolen)/Batteries were stolen) | 2019-09-04 14:32 | 2019-09-26 | FALSE
IM760632 | 3828DE | 0961_S_BH-GWAD-HUSNI_3828DE | Main power / stolen batteries / PG connected | batt | Batteries | batt | Batteries | 356184 | BH-GWAD-HUSNI | C1_3828DE_PH14 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) | 2019-09-04 13:33 | 2019-09-02 | TRUE
IM760635 | 3751DE | 0021_S_DK-SHRKA2-VLG_3751DE | Main power / stolen batteries | batt | Batteries | batt | Batteries | 304052 | DK-SHRKA2-VLG | C1_3751DE_PH14 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-04 13:22 | 2019-01-29 | TRUE
IM760657 | 3916DE | 1191_S_BH-BAYDA-2_3916DE | Main power / weak batteries (BDT @ 18/10/2018 Is: 0.10) / PG in the way / was handling other sites BH-KOMBO_3978DE and BH-GWAD-HUS NI_3828DE / BH-GWAD-HUSNI_3828DE power back now and PG moved to BAYDA-2 | batt | Batteries | batt | Batteries | 355465 | BH-BAYDA-2 | C1_3916DE_PH14 | (Batteries/Components faulty/faulty) | 2019-09-04 14:40 | 2019-06-23 | TRUE
IM760699 | 3413DE | 0801_D_PS-KHADIGA_3413DE | GN problem @PS-KHADIGA_3413DE / last BDT @ 28 OCT 2017 is 03:00 | GN | Generator | GN | Generator | 324940 | PS-KHADIGA | C2_3413DE_PH13 | (ATS / Engine/Components faulty/faulty) (ATS / Engine/Wrong connection/remove cable) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM organization/Unused cable need to be removed.) (ATS / Engine/Panorama pictures for each system/Overview.) | 2019-09-02 05:11 | 2019-04-24 | TRUE
IM760710 | 3828DE | 0961_S_BH-GWAD-HUSNI_3828DE | Main power / stolen batteries / PG connected | batt | Batteries | batt | Batteries | 356184 | BH-GWAD-HUSNI | C1_3828DE_PH14 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) | 2019-09-04 15:58 | 2019-09-02 | TRUE
IM760740 | 3249DE | 0601_D_BH-TEROUGI_3249DE | GN problem / batteries under check | batt GN | Batteries Generator | GN | Generator | 304212 | BH-TEROUGI | C2_3249DE_PH12 | (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Damaged cables isolation) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Burned terminal) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot) | 2019-09-04 16:27 | 2019-02-12 | TRUE
IM760759 | 0145SI | 01_G_SS-MR66-GYPSM2_0145SI | E// link problem , access TE after 4PM Emergency permission sent , once reset MMU Site recovered | Gen | Generator | Gen | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure ) (ATS / Engine/Wrong connection/generator battery as used in the site and not suitable in High temp) | 2019-09-04 17:15 | 2019-07-01 | TRUE
IM760795 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due DG dynamo problem and batt. not installed (I) | batt DG | Batteries Generator | batt DG | Batteries Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | (Batteries/Some parts are missing/missing batteries) (ATS / Engine/Wrong connection/wrong connection) | 2019-09-04 18:59 | 2019-02-26 | TRUE
IM760828 | 0760DE | 0151_Q_SK-JAWSAK-VLG_0760DE | GN problem/batteries under investigation/clear after check GN | batt GN | Batteries Generator | GN | Generator | 304032 | BH-SHANDID | C2_3464DE_PH13 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has leakage) (ATS / Engine/Components below rate (excluding main power feeder if not hot)/Generator voltage need adjustment) | 2019-09-04 20:37 | 2019-01-24 | TRUE
IM760867 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN problem @SK-MIT-GABIR_3833DE/GN working and cascaded site Dahmasha down on progress | GN | Generator | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | (ATS / Engine/Wrong connection/Welding cables) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot) | 2019-09-04 23:14 | 2019-06-16 | TRUE
IM760885 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries Caused site Down , once team arrive and fix DG problem site recovered with cascaded | batt DG | Batteries Generator | batt DG | Batteries Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | (Batteries/Some parts are (missing / stolen)/Battery string stolen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage) (ATS / Engine/Unit earth/Earth cable disconnected) (ATS / Engine/Components faulty/Generator indicator broken & not work) (ATS / Engine/Components faulty/Ventilation fan not work) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Power cable has no terminal) | 2019-09-05 01:56 | 2019-09-09 | FALSE
IM760896 | 0222RE | 03824_G_0222RE_RS-FLAMNCO-HTL | DG Stopped , stolen batteries Caused site Down , once team arrive and fix DG problem site recovered | batt DG | Batteries Generator | DG | Generator | 355690 | 01_G_RS-FLAMNCO-HTL_0222RE | C1_0222RE_PH09 | (ATS / Engine/Components faulty/need battery) | 2019-09-05 02:04 | 2019-01-20 | TRUE
IM760924 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN problem @SK-MIT-GABIR_3833DE/GN working | GN | Generator | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | (ATS / Engine/Wrong connection/Welding cables) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot) | 2019-09-05 05:32 | 2019-06-16 | TRUE
IM760936 | 0041SI | L_S_SS-RAS-ABU-RDS_0041SI | DG Stopped , access Nigh H&S Recovered once DG problem solved | DG | Generator | DG | Generator | 356372 | 01_H_SS-RAS-ABU-RDS_0041SI | C3_0041SI_PH2 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Genset oil leakage) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Air filter not found & fuel around the air filter housing) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel on the container floor) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Unclean V.F genset area) (ATS / Engine/Components faulty/Defected genset battery) (ATS / Engine/Components faulty/Cables damage isolation & bad connections) (ATS / Engine/Wrong connection/Wrong cables connections , use double terminals) (ATS / Engine/Wrong connection/A.C / D.C converted used as a charger in the genset) (ATS / Engine/Wrong connection/Deep cycle battery used as a starter in the genset) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Missing ATS cables terminals) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Remain cables & terminals in the genset gauage indicators box) | 2019-09-05 05:46 | 2019-09-23 | FALSE
IM760939 | 0648DE | 0381_S_BH-IZ-HUSNI_0648DE | Main power @BH-IZ-HUSNI_0648DE / weak batteries / PG connected | batt | Batteries | batt | Batteries | 355857 | BH-IZ-HUSNI | C1_0648DE_PH9 | (Batteries/Some parts are (missing / stolen)/stolen batteries) | 2019-09-05 05:53 | 2019-07-22 | TRUE
IM760949 | 0285DE | K_BH-ABU-HUMMUS_20855_1 | GN problem @ BH-ABU-HUMMUS_0285DE / weak batteries / Last BDT at 25-Oct-18 is 2 Hrs | batt GN | Batteries Generator | batt | Batteries | 345403 | BASHTEL-ST | C3_3130CA_PH9 | (Rectifiers/Alarms reporting to the OMC/Minor alarm due to temprature measurement doesn't appear on the OMC (Loop in DDF)) (Batteries/Some parts are (missing / stolen)/All batteries are stolen) | 2019-09-05 06:32 | 2019-06-19 | TRUE
IM760951 | 3955DE | 0731_S_SK-QRMT-SAHBRA_3955DE | access ET/ET GN problem/batteries under investigation//Stolen batteires | batt GN | Batteries Generator | batt | Batteries | 356230 | SK-QRMT-SAHBRA | C1_3955DE_PH15 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-05 06:51 | 2019-09-07 | FALSE
IM760979 | 0095SI | 0201_S_SS-SUN-MON-STR_0095SI | utage power in area located site , dead batteries , access PG Auto-Recovered once power restored | batt | Batteries | batt | Batteries | 355557 | 01_S_SS-SUN-MON-STR_0095SI | C1_0095SI_PH03 | (Batteries/Components faulty/salty battery pole ) | 2019-09-05 07:26 | 2019-07-03 | TRUE
IM761012 | 0954UP | 01_G_MN-DAHMARU_0954UP | Commercial power cutoff and stolen backup batteries EC power recovered and site back on air | backup batt | Batteries Batteries | backup batt | Batteries | 324946 | 01_G_MN-DAHMARU_0954UP | C1_0954UP_PH12 | (Batteries/Item(s) stolen/site baateries were stolen) | 2019-09-05 09:15 | 2019-04-25 | TRUE
IM761047 | 3555CA | 00042_L_3555CA_SAMA-TOWER | down due to DG problem and stolen batteries (MA) | batt DG | Batteries Generator | batt DG | Batteries Generator | 345256 | SAMA-TOWER | C2_3555CA_PH13 | (Batteries/Some parts are missing/missing batteries) (ATS / Engine/Wrong connection/welded cables) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage) | 2019-09-05 10:10 | 2019-05-25 | TRUE
IM761055 | 0615DE | K_GH-KFR-BAB_20860_1 | Main power/Stolen batteries @GH-KFR-BAB_0615DE/clear after power back | batt | Batteries | batt | Batteries | 314420 | GH-KFR-BAB | C15_0615DE_PH14 | (Batteries/Item(s) stolen/stolen batteries) | 2019-09-05 09:13 | 2019-03-06 | TRUE
IM761078 | 0016UP | 00276_I_0016UP_DES1 | down due to DG problem and weak batteries (MA) | batt DG | Batteries Generator | DG | Generator | 324979 | DES1 | C2_0016UP_PH0 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage) | 2019-09-05 10:28 | 2019-04-30 | TRUE
IM761084 | 0479DE | 0591_S_DK-MNS-FRSKOR1_0479DE | Main power @ DK-MNS-FRSKOR1_0479DE / stolen batteries / Connect PG | batt | Batteries | batt | Batteries | 356389 | DK-MNS-FRSKOR1 | C3_0479DE_PH7 | (Batteries/Some parts are (missing / stolen)/stolen batteries) | 2019-09-05 09:56 | 2019-09-24 | FALSE
IM761109 | 3892DE | 0171_S_BH-ZWIT-HUMOR_3892DE | Main power / stolen batteries | batt | Batteries | batt | Batteries | 324905 | BH-ZWIT-HUMOR | C1_3892DE_PH14 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-05 10:18 | 2019-04-17 | TRUE
IM761114 | 3191DE | 0971_D_GH-BALQINA_3191DE | GN problem / stolen batteries | batt GN | Batteries Generator | batt GN | Batteries Generator | 304240 | GH-BALQINA | C4_3191DE_PH12 | (Batteries/Item(s) stolen/stolen batteries) (ATS / Engine/Components faulty/connect and check) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/sharp edges) (ATS / Engine/Item(s) stolen/stolen battery) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage) | 2019-09-05 10:35 | 2019-02-18 | TRUE
IM761119 | 3352DE | 0071_D_BH-SHBRA-OSEEM_3352DE | Main power/stolen batteries/clear on P.G | batt | Batteries | batt | Batteries | 325117 | BH-SHBRA-OSEEM | C1_3352DE_PH12 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-05 10:49 | 2019-05-12 | TRUE
IM761164 | 3765UP | 2251_S_SG-NAGA-ELNGAR_3765UP | Main power disconnection , Stolen batteries , P.G connected | batt | Batteries | batt | Batteries | 345419 | 01_S_SG-NAGA-ELNGAR_3765UP | C1_3765UP_PH15 | (Batteries/Some parts are (missing / stolen)/batteries were stolen) | 2019-09-05 10:52 | 2019-06-20 | TRUE
IM761177 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem & no backup & access VF (T) | backup DG | Batteries Generator | backup | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | (Batteries/Some parts are (missing / stolen)/missing battereis) | 2019-09-05 11:35 | 2019-08-14 | TRUE
IM761287 | 3454DE | 1061_D_GH-MAHLT-MENOF_3454DE | ET Share / GN problem / Stolen batteries | batt GN | Batteries Generator | batt GN | Batteries Generator | 324838 | GH-MAHLT-MENOF | C2_3454DE_PH13 | (Batteries/Item(s) stolen/Stolen Batteries) (ATS / Engine/Item(s) stolen/stolen batteries) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) | 2019-09-05 13:20 | 2019-04-10 | TRUE
IM761293 | 3191DE | 0971_D_GH-BALQINA_3191DE | GN problem / stolen batteries / Team waiting guard / and follow with SOC / connect PG | batt GN | Batteries Generator | batt GN | Batteries Generator | 304240 | GH-BALQINA | C4_3191DE_PH12 | (Batteries/Item(s) stolen/stolen batteries) (ATS / Engine/Components faulty/connect and check) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/sharp edges) (ATS / Engine/Item(s) stolen/stolen battery) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage) | 2019-09-05 13:35 | 2019-02-18 | TRUE
IM761296 | 3943DE | 0921_S_SK-AKRASH_3943DE | access ET/ET GN problem/Stolen batteries@SK-AKRASH_3943DE/clear on P.G | batt GN | Batteries Generator | batt | Batteries | 303886 | SK-AKRASH | C1_3943DE_PH15 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-05 13:43 | 2019-01-19 | TRUE
IM761339 | 0339UP | 0351_G_MN-SALEEBA_0339UP | Generator stopped , Site has weak backup batteries , Recovered | backup batt Gen generator | Batteries Batteries Generator Generator | Gen generator | Generator | 324684 | 01_G_MN-SALEEBA_0339UP | C3_0339UP_PH8 | (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/protect cable) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage) | 2019-09-05 14:34 | 2019-03-28 | TRUE
IM761358 | 3775DE | 0471_D_DK-DABBOS-VLG_3775DE | GN problem / BDT @ 09/09/2018 Is: 3.00 / Team work at site | GN | Generator | GN | Generator | 325073 | DK-DABBOS-VLG | C1_3775DE_PH14 | (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/bad terminals) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) | 2019-09-05 14:45 | 2019-05-07 | TRUE
IM761421 | 0618DE | 0101_G_GH-SAFT-TURAB_0618DE | Main power problem / SB GN stopped / Weak batteries BDT @ 19/11/2018 Is: 1.00/ Connect PG | batt GN | Batteries Generator | GN | Generator | 324605 | GH-SAFT-TURAB | C11_0618DE_PH09 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Clean) | 2019-09-05 16:06 | 2019-03-17 | TRUE
IM761488 | 3943DE | 0921_S_SK-AKRASH_3943DE | access ET/ET GN problem/Stolen batteries@SK-AKRASH_3943DE | batt GN | Batteries Generator | batt | Batteries | 303886 | SK-AKRASH | C1_3943DE_PH15 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-05 19:53 | 2019-01-19 | TRUE
IM761553 | 3955DE | 0731_S_SK-QRMT-SAHBRA_3955DE | access ET/ET GN problem/Stolen batteries | batt GN | Batteries Generator | batt | Batteries | 356230 | SK-QRMT-SAHBRA | C1_3955DE_PH15 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-06 00:15 | 2019-09-07 | FALSE
IM761576 | 0411RE | 03870_S_0411RE_RS-BRAYKA-BAY | DG Stopped , stolen batteries Caused site Down , once team arrive and fix DG problem site recovered | batt DG | Batteries Generator | batt DG | Batteries Generator | 356418 | 01_S_RS-BRAYKA-BAY_0411RE | C1_0411RE_PH15 | (Batteries/Some parts are (missing / stolen)/Batteries were stolen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Open gland in Gen enclosure need insulation) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Two cables inserted in one slot and not teminated can cause bad connections ) | 2019-09-06 02:15 | 2019-09-26 | FALSE
IM761582 | 3681DE | 1781_D_BH-MNSHYT-HMOR_3681DE | Access Guard " 1638 " / GN problem / Weak batteries | batt GN | Batteries Generator | GN | Generator | 355781 | BH-MNSHAT-HMOR | C5_3681DE_PH13 | (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminals requried) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminal requried) | 2019-09-06 01:55 | 2019-07-11 | TRUE
IM761599 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries Caused site Down , once team arrive and fix DG problem site recovered with cascaded | batt DG | Batteries Generator | batt DG | Batteries Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | (Batteries/Some parts are (missing / stolen)/Battery string stolen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage) (ATS / Engine/Unit earth/Earth cable disconnected) (ATS / Engine/Components faulty/Generator indicator broken & not work) (ATS / Engine/Components faulty/Ventilation fan not work) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Power cable has no terminal) | 2019-09-06 04:32 | 2019-09-09 | FALSE
IM761655 | 3791DE | 1671_D_SK-ABU-HARIZ_3791DE | main Power / Stolen Batteries / clear after power back | batt | Batteries | batt | Batteries | 335162 | SK-ABU-HARIZ | C2_3791DE_PH14 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-06 06:40 | 2019-05-21 | TRUE
IM761657 | 0682DE | 0861_S_MF-TAHA-SHBRA2_0682DE | access T.E/Hi temp/clear after check | Hi Temp | A/Cs | Hi Temp | A/Cs | 324623 | MF- TAHA-SHBRA2 | C1_0682DE_PH9 | (A/Cs Cooling / Free Cooling / Ventilation/Components faulty/check ) (A/Cs Cooling / Free Cooling / Ventilation/Components faulty/faulty A/C2) | 2019-09-06 06:46 | 2019-03-26 | TRUE
IM761662 | 3435DE | 1531_S_SK-AMRIT_3435DE | main Power / Weak Batteries / clear after power back | batt | Batteries | batt | Batteries | 324455 | SK-AMRIT | C1-3435DE-PH13 | (Batteries/Components faulty/Batteries can't carry site.) | 2019-09-06 06:52 | 2019-03-10 | TRUE
IM761671 | 3751DE | 0021_S_DK-SHRKA2-VLG_3751DE | Main power / stolen batteries / PG connected | batt | Batteries | batt | Batteries | 304052 | DK-SHRKA2-VLG | C1_3751DE_PH14 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-06 07:16 | 2019-01-29 | TRUE
IM761675 | 2083DE | 0021_S_GH-M-KITCHENER_2083DE | Access Corp. " Kher Zaman - Hypermarket " /Main power / HDSL not secured / Weak batteries | batt | Batteries | batt | Batteries | 324872 | GH-M-KITCHENER | C1_2083DE_PH16 | (Batteries/Some parts are missing/Clean and add poles covers) (Batteries/Some parts are missing/Clean and add covers ) | 2019-09-06 07:26 | 2019-04-17 | TRUE
IM761726 | 0735DE | 0711_G_GH-TANTA-HW2_0735DE | Main power @ GH-TANTA-HW2_0735DE / Stolen batteries | batt | Batteries | batt | Batteries | 324537 | GH-TANTA-HW2 | C1_0735DE_PH9 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-06 11:47 | 2019-03-14 | TRUE
IM761753 | 3333DE | 0181_S_BH-OM-SABER_3333DE | main Power / Stolen Batteries / clear after power back | batt | Batteries | batt | Batteries | 304089 | BH-OM-SABER_SSS0 | C1_3333DE_PH12 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-06 12:27 | 2019-01-30 | TRUE
IM761755 | 3756DE | 1121_D_SK-HALAWAT_3756DE | GN problem/ batteries under investigation @SK-HALAWAT_3756DE/GN working | batt GN | Batteries Generator | GN | Generator | 304142 | SK-HALAWAT | C1-3756DE-PH14 | (ATS / Engine/Components faulty/Generator has bad condition and needs overhaul.) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM organization/Sensor cables need replacement.) (ATS / Engine/Cables/Feeders/Jumpers/Coaxial/FO/PCM connection tightness/Neutral bar need fixation.) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/ATS cables need proper terminals.) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has a lot of leakage.) | 2019-09-06 12:37 | 2019-02-09 | TRUE
IM761757 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries , , Recovered once DG fix | batt DG | Batteries Generator | batt DG | Batteries Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | (Batteries/Some parts are (missing / stolen)/Battery string stolen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage) (ATS / Engine/Unit earth/Earth cable disconnected) (ATS / Engine/Components faulty/Generator indicator broken & not work) (ATS / Engine/Components faulty/Ventilation fan not work) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Power cable has no terminal) | 2019-09-06 13:44 | 2019-09-09 | FALSE
IM761764 | 0140AL | U_S_0140AL_ABOUYOUSIF-WST | main power problem / weak batteries / commercial power auto recovered | batt | Batteries | batt | Batteries | 304353 | ABU_YOUSSEF_WEST | C1_0140AL_PH3 | (Batteries/Item(s) stolen/Stolen batteries) | 2019-09-06 12:40 | 2019-02-26 | TRUE
IM761768 | 0975UP | 0381_S_BS-MASID-ABYAD_0975UP_X | Commercial power cutoff and stolen backup batteries P.G connected and site back on air | backup batt | Batteries Batteries | backup batt | Batteries | 356360 | 01_S_BS-MASID-ABYAD_0975UP | C1_0975UP_PH12 | (Rectifiers/Alarms reporting to the OMC/Minor alarm doesn't appear on the OMC) (Batteries/Some parts are (missing / stolen)/Batteries and cables are stolen) | 2019-09-06 12:50 | 2019-09-17 | FALSE
IM761770 | 3807UP | 0631_D_QN-MHAMID-QBLY_3807UP | due to Generator problem, stolen batteries in site QN-MHAMID-QBLY_3807UP, P.G connected | batt Gen generator | Batteries Generator Generator | batt Gen generator | Batteries Generator | 355794 | 01_G_QN-MHAMID-QBLY_3807UP | C1_3807UP_PH15 | (Rectifiers/Alarms reporting to the OMC/Rectifier minor alarm was looped at ddf) (ATS / Engine/Unit earth/Earth bar is missing) (ATS / Engine/Components faulty/Gen enclosure Screen press keys were defected) (ATS / Engine/Filters condition oil/fuel/air/Air Filter cover is not fixed) | 2019-09-06 12:55 | 2019-07-14 | TRUE
IM761796 | 3894CA | 02231_S_3894CA_REHAB-STAGE7 | down due to VF DG problem & stolen batteries & access VF (T) | batt DG | Batteries Generator | batt | Batteries | 356204 | REHAB-STAGE7 | C1_3894CA_PH17 | (Batteries/Some parts are (missing / stolen)/missing batteries) | 2019-09-06 14:06 | 2019-08-14 | TRUE
IM761799 | 3828DE | 0961_S_BH-GWAD-HUSNI_3828DE | Main Powr problem / stolen batteries | batt | Batteries | batt | Batteries | 356184 | BH-GWAD-HUSNI | C1_3828DE_PH14 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) | 2019-09-06 13:40 | 2019-09-02 | TRUE
IM761808 | 3414UP | 0401_S_BS-AHWA_3414UP_X | Commercial power cutoff and weak backup batteries P.G connected ad site back on air | backup batt | Batteries Batteries | backup batt | Batteries | 356350 | 01_S_BS-AHWA_3414UP | C1_3414UP_PH14 | (Rectifiers/Alarms reporting to the OMC/Loop on the major alarm in DDF) (Batteries/Components faulty/Batteries are faulty and site is down after less than one hour of power disconnected) | 2019-09-06 13:35 | 2019-09-17 | FALSE
IM761872 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN problem/stolen batteries @MIT-GABIR_3833DE/GN working | batt GN | Batteries Generator | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | (ATS / Engine/Wrong connection/Welding cables) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot) | 2019-09-06 17:16 | 2019-06-16 | TRUE
IM761873 | 0734DE | 0441_D_MF-TANTA-HW1_0734DE | GN problem / solar theft case / stolen batteries / PG connected | batt GN | Batteries Generator | batt GN | Batteries Generator | 356142 | MF-TANTA-HW1 | C1_0734DE_PH9 | (Rectifiers/Alarms reporting to the OMC/Site has fake power alarm) (Batteries/Some parts are (missing / stolen)/There is no battery for site) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has leakage) | 2019-09-06 17:27 | 2019-08-27 | TRUE
IM761895 | 3290DE | 1171_D_MF-QATTA_3290DE | GN problem/batteries not installed / clear after GN working(Fuel PUMP) | batt GN | Batteries Generator | GN | Generator | 355961 | MF-QATTA | C3_3290DE_PH12 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has leakage) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminals requried) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Cable need to be terminated well) | 2019-09-06 21:23 | 2019-08-03 | TRUE
IM761918 | 0595DE | 0281_G_DK-NISHA_0595DE | Main power /weak batteries (BDT @ 30/07/2018 Is: 3.00) | batt | Batteries | batt | Batteries | 324924 | DK-NISHAA | C1_0595DE_PH9 | (Batteries/Some parts are missing/cover) | 2019-09-06 23:07 | 2019-04-22 | TRUE
IM761926 | 3775DE | 0471_D_DK-DABBOS-VLG_3775DE | GN problem / BDT @ 09/09/2018 Is: 3.00 under check | GN | Generator | GN | Generator | 325073 | DK-DABBOS-VLG | C1_3775DE_PH14 | (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/bad terminals) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) | 2019-09-07 00:40 | 2019-05-07 | TRUE
IM761937 | 0375UP | 0561_N_CAIRO-ASWAN-17_0375UP | Main power disconnection , stolen batteries , ETS owner access problem ( Unreachable ) , Recovered after EC power back . | batt | Batteries | batt | Batteries | 324845 | 01_A_CAIRO-ASWAN-17_0375UP | C1_0375UP_PH8 | (Batteries/Item(s) stolen/Batteries were stolen) | 2019-09-07 02:19 | 2019-04-14 | TRUE
IM761949 | 4021DE | 0181_S_BH-ABQAEEN_4021DE | Access VF Guard payment problem / Expected Main C.B switched off / Stolen batteries / Power exist at site area / Call VF office ma nager can't support / Call Mr. Hossam told inform Mabrouk/ calling Bolaky | batt | Batteries | batt | Batteries | 304224 | BH-ABQAEEN | C1_4021DE_PH15 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-07 02:19 | 2019-02-13 | TRUE
IM761951 | 3955DE | 0731_S_SK-QRMT-SAHBRA_3955DE | ET gen problem/ battery under invistoigation/ ET GN working | batt Gen GN | Batteries Generator Generator | batt | Batteries | 356230 | SK-QRMT-SAHBRA | C1_3955DE_PH15 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-07 03:25 | 2019-09-07 | TRUE
IM761960 | 0435UP | 02_G_SG-GAZAZRA_0435UP | Main power disconnnection , stolen batteries , P.G connected | batt | Batteries | batt | Batteries | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | (Batteries/Item(s) stolen/site batteries were stolen) (Batteries/Item(s) stolen/Batteries were stolen) | 2019-09-07 06:30 | 2019-04-04 | TRUE
IM761972 | 0127DE | 0061_H_GH-MRO4-QUTUR_0127DE | Main power @ GH-MR04-QUTUR_0127DE / Stolen batteries / Connect PG / Cells Hanged / Split request | batt | Batteries | batt | Batteries | 304205 | 9_S_GH-MR04-QUTUR_0127DE_SS00 | C4_0127DE_PH2 | (Batteries/Item(s) stolen/stolen batteries) | 2019-09-07 06:06 | 2019-02-14 | TRUE
IM761990 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , Recovered | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage of the engine) (ATS / Engine/Unit earth/Stolen earth connections of the genset panel) (ATS / Engine/Components faulty/The rubber bases of the radiator are faulty) (ATS / Engine/Components faulty/The dynamo belt needs to be tensioned) (ATS / Engine/Wrong connection/The negative pole of the battery isn't connected) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Missing terminals of cables connected to contactors and CBs inside the genset panel) | 2019-09-07 07:10 | 2019-07-30 | TRUE
IM761993 | 0240RE | 03485_S_0240RE_SZ-SUEZ-NTH | Outage power in area located site , access PG , dead batteries once power restored site Recovered | batt | Batteries | batt | Batteries | 355923 | 01_S_SZ-SUEZ-NTH_0240RE | C1_0240RE_PH9 | (Rectifiers/Alarms reporting to the OMC/Rectifier Major & Minor , A/C & door alarm not appear on CAP) | 2019-09-07 07:02 | 2019-07-30 | TRUE
IM761994 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Due to Generator problem , Stolen batteries , Recovered | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 304381 | BH-ABU-HUMMUS | C2_0285DE_PH3 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) (ATS / Engine/Unit earth/fake earth) (ATS / Engine/Components faulty/faulty) (ATS / Engine/Components faulty/replace) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Cables at 1 slot) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot) | 2019-09-07 07:15 | 2019-03-03 | TRUE
IM762000 | 4005DE | 0751_D_DK-BASHALOSH_4005DE | GN problem/ batteries under invistgation /GN working | batt GN | Batteries Generator | GN | Generator | 356229 | DK-BASHALOSH | C4_4005DE_PH15 | (ATS / Engine/Unit earth/Disconnected earth cable.) (ATS / Engine/Components faulty/Battery poles need cleaning, wax and covers.) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Neutral bar need adjust.) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Some cables need proper terminals.) | 2019-09-07 05:50 | 2019-09-07 | TRUE
IM762004 | 0983DE | 1771_S_DK-MIT-ANTAR_0983DE | Main power / Stolen batteries | batt | Batteries | batt | Batteries | 324896 | DK-MIT-ANTAR | C8_0983DE_PH11 | (Batteries/Item(s) stolen/stolen batteries) | 2019-09-07 07:50 | 2019-04-14 | TRUE
IM762005 | 3681DE | 1781_D_BH-MNSHYT-HMOR_3681DE | GN problem / Weak batteries | batt GN | Batteries Generator | GN | Generator | 355781 | BH-MNSHAT-HMOR | C5_3681DE_PH13 | (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminals requried) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminal requried) | 2019-09-07 07:55 | 2019-07-11 | TRUE
IM762024 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Main power / Stolen batteries / VF Share | batt | Batteries | batt | Batteries | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | (Batteries/Item(s) stolen/Stolen) | 2019-09-07 09:10 | 2019-03-25 | TRUE
IM762028 | 0324UP | 1421_S_MN-BARTABAT_0324UP | Due to EC power cutoff , Stolen batteries , PG Connected | batt | Batteries | batt | Batteries | 324919 | 01_S_MN-BARTABAT_0324UP | C1_0324UP_PH8 | (Batteries/Item(s) stolen/Site batteries were stolen) | 2019-09-07 08:24 | 2019-04-20 | TRUE
IM762035 | 3514DE | 1901_S_DK-KFR-GHENINA_3514DE | Main power @ DK-KFR-GHENINA_3514DE / Weak batteries / BDT @ 04/08/2019 Is: 0.00 | batt | Batteries | batt | Batteries | 324923 | DK-KFR-GHENINA | C3_3514DE_PH13 | (Batteries/Item(s) stolen/stolen Batteries) | 2019-09-07 09:33 | 2019-04-22 | TRUE
IM762069 | 3594DE | 1241_S_BH-TAYRIYA_3594DE | Main power/stolen battery/power back | batt | Batteries | batt | Batteries | 325119 | BH-TAYRIYA | C1-3594DE-PH13 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-07 10:17 | 2019-05-12 | TRUE
IM762072 | 3484DE | 0231_S_SK-MIT-BASHAR_3484DE | Main power/ battery under invitigation/power back | batt | Batteries | batt | Batteries | 356055 | SK-MIT-BASHAR | C2-3484DE-PH13 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) | 2019-09-07 10:33 | 2019-08-18 | TRUE
IM762075 | 3898DE | 0821_S_BH-ZUBAYDA_3898DE | Main power / Stolen batteries / SC GN problem / PG connected | batt GN | Batteries Generator | batt GN | Batteries Generator | 335128 | BH-ZUBAYDA | C1_3898DE_PH14 | (Batteries/Item(s) stolen/There is no battery for site) (ATS / Engine/Components faulty/There is no battery for site (Check small generator operation)) | 2019-09-07 10:44 | 2019-05-15 | TRUE
IM762124 | 3368DE | 0201_S_BH-ABO-SHIQAF_3368DE | Access VF / Main power / stolen batteries | batt | Batteries | batt | Batteries | 324904 | BH-ABO-SHIQAF | C1_3368DE_PH12 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-07 13:05 | 2019-04-17 | TRUE
IM762146 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem and stolen batteries and access VF problem(M) | batt DG | Batteries Generator | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | (Batteries/Some parts are (missing / stolen)/missing battereis) | 2019-09-07 14:18 | 2019-08-14 | TRUE
IM762167 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Main power / Stolen batteries / VF Share | batt | Batteries | batt | Batteries | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | (Batteries/Item(s) stolen/Stolen) | 2019-09-07 14:11 | 2019-03-25 | TRUE
IM762196 | 3775DE | 0471_D_DK-DABBOS-VLG_3775DE | GN problem / BDT @ 09/09/2018 Is: 3.00 under check / PG connected | GN | Generator | GN | Generator | 325073 | DK-DABBOS-VLG | C1_3775DE_PH14 | (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/bad terminals) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) | 2019-09-07 15:51 | 2019-05-07 | TRUE
IM762214 | 0736CA | 02118_D_0736CA_PETROL-PIPELINS | down due to DG filter problem and stolen batteries (M) | batt DG | Batteries Generator | batt DG | Batteries Generator | 356154 | PETROL-PIPELINS | C2_0736CA_PH9 | (Batteries/Some parts are (missing / stolen)/Batteries and cables are stolen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Signs of oil and fuel leakage arround the genset) (ATS / Engine/Unit earth/Stolen earth connections of the ATS panel) (ATS / Engine/Components faulty/White exhaust of the engine) (ATS / Engine/Wrong connection/Wrong connections of cables connected to the ATS trans.) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Missing terminals of power cables connected to the ATS contactors) | 2019-09-07 17:05 | 2019-08-26 | TRUE
IM762247 | 3720DE | 0651_D_MF-SK-KARADIS_3720DE | GN problem/Stolen battery@SK-KARADIS_3720DE/ clear | batt GN | Batteries Generator | batt GN | Batteries Generator | 355737 | MF-SK-KARADIS | C2-3720DE-PH14 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Cables have bad connections, proper terminals and proper installtion are rerquired.) | 2019-09-07 17:57 | 2019-07-07 | TRUE
IM762248 | 0427DE | 0061_D_SK-EZBA-SARYA_0427DE | GN problem/Stolen battery/ clear | batt GN | Batteries Generator | batt GN | Batteries Generator | 345382 | SK-EZBA-SARYA | C2_0427DE_PH4 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) (ATS / Engine/Components faulty/Exhaust fan not working and another not exist) | 2019-09-07 18:21 | 2019-06-16 | TRUE
IM762283 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to DG HT problem and stolen batt. (I) | HT batt DG | A/Cs Batteries Generator | batt DG | Batteries Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | (Batteries/Some parts are missing/missing batteries) (ATS / Engine/Wrong connection/wrong connection) | 2019-09-07 21:06 | 2019-02-26 | TRUE
IM762304 | 0517RE | 03217_E_0517RE_SZ-GALALA-CAMP | Site access Night H&S unsafe road DG Stopped , stolen batteries , recovered once tea access site and fix DG | batt DG | Batteries Generator | batt DG | Batteries Generator | 304374 | SZ-GALALA-CAMP | 0517RE | (Batteries/Components faulty/stolen batteries ) (ATS / Engine/Components faulty/missing battery ) (ATS / Engine/Wrong connection/wrong connection for cables ) (ATS / Engine/Wrong connection/welded cables ) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/power cable not protected inside PVC or tray ) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/fuel tank pipes not protected inside tray ) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/broken PVC ) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/cable not terminated ) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/cables not terminated ) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/bad termination for cable ) | 2019-09-07 23:30 | 2019-02-24 | TRUE
IM762317 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem and access VF & stolen batt. (I) | batt DG | Batteries Generator | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | (Batteries/Some parts are (missing / stolen)/missing battereis) | 2019-09-08 00:53 | 2019-08-14 | TRUE
IM762350 | 0268RE | 03848_G_0268RE_RS-BDWYA-MARSA | DG Stopped , dead batteries PLVD disconnect Site to save cascaded Once team arrive and solve DG problem site recovered | batt DG PLVD | Batteries Generator Rectifier | DG | Generator | 304329 | 01_G_RS-BDWYA-MARSA_0268RE | C2_0268RE_PH9 | (ATS / Engine/Components faulty/Gen battery is faulty) (ATS / Engine/Panorama pictures for each system/Open gland in Gen enclosure need insulation) (ATS / Engine/Panorama pictures for each system/Last Gen hour meter at Audit G ( 9838 )) (ATS / Engine/Panorama pictures for each system/Panorama site view in outside site) | 2019-09-08 02:37 | 2019-02-20 | TRUE
IM762355 | 3413DE | 0801_D_PS-KHADIGA_3413DE | Access GA @ PS-KHADIGA_3413DE / GN stopped / BDT @ 08/10/2018 Is: 3.00 | GN | Generator | GN | Generator | 324940 | PS-KHADIGA | C2_3413DE_PH13 | (ATS / Engine/Components faulty/faulty) (ATS / Engine/Wrong connection/remove cable) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM organization/Unused cable need to be removed.) (ATS / Engine/Panorama pictures for each system/Overview.) | 2019-09-08 04:09 | 2019-04-24 | TRUE
IM762365 | 3784DE | 0661_S_KS-DAQLIT_3784DE | Main power / Weak batteries / VF Share | batt | Batteries | batt | Batteries | 335221 | KS-DAQLIT | C3_3784DE_PH14 | (Batteries/Components faulty/Faulty battery (battearies are ballooned)) | 2019-09-08 04:42 | 2019-05-26 | TRUE
IM762405 | 3191DE | 0971_D_GH-BALQINA_3191DE | GN problem / stolen batteries | batt GN | Batteries Generator | batt GN | Batteries Generator | 304240 | GH-BALQINA | C4_3191DE_PH12 | (Batteries/Item(s) stolen/stolen batteries) (ATS / Engine/Components faulty/connect and check) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/sharp edges) (ATS / Engine/Item(s) stolen/stolen battery) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage) | 2019-09-08 07:57 | 2019-02-18 | TRUE
IM762425 | 0127DE | 0061_H_GH-MRO4-QUTUR_0127DE | Main power @ GH-MR04-QUTUR_0127DE / Stolen batteries / Connect PG / Cells Hanged / Split request | batt | Batteries | batt | Batteries | 304205 | 9_S_GH-MR04-QUTUR_0127DE_SS00 | C4_0127DE_PH2 | (Batteries/Item(s) stolen/stolen batteries) | 2019-09-07 06:06 | 2019-02-14 | TRUE
IM762436 | 3368DE | 0201_S_BH-ABO-SHIQAF_3368DE | Access VF / Main power / stolen batteries | batt | Batteries | batt | Batteries | 324904 | BH-ABO-SHIQAF | C1_3368DE_PH12 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-07 13:05 | 2019-04-17 | TRUE
IM762481 | 0329RE | 03838_S_0329RE_RS-SENTIDO-DRM | ET DG Stopped , stolen batteries , access PG due unsafe road , stolen batteries Once DG fix Site recovered | batt DG | Batteries Generator | DG | Generator | 304289 | 01_S_RS-SENTIDO-DRM_0329RE | C1_0329RE_PH12 | (ATS / Engine/Panorama pictures for each system/Panorama site view in outside site) | 2019-09-08 10:32 | 2019-02-19 | TRUE
IM762484 | 3126DE | 0121_S_DK-HAGYZEYA_3126DE | Main Power/stolen battery/PG connected | batt | Batteries | batt | Batteries | 355992 | DK-HAGYZEYA | C6-3126DE-PH12 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-08 09:53 | 2019-08-07 | TRUE
IM762498 | 0267RE | U_S_RS-NADA-MARSA_0267RE | Outage power in Hotel located site , dead batteries , access PG Once power restored site recovered | batt | Batteries | batt | Batteries | 304306 | 01_S_RS-NADA-MARSA_0267RE | C1_0267RE_PH9 | (Batteries/Components faulty/No back up power ( Batteries were damged also salty )) (Batteries/Item(s) stolen/Batteries connections were stolen also ( No back up power )) | 2019-09-08 10:44 | 2019-02-20 | TRUE
IM762500 | 3333DE | 0181_S_BH-OM-SABER_3333DE | Access VF. / Main Power / Stolen batteries/clear after power back | batt | Batteries | batt | Batteries | 304089 | BH-OM-SABER_SSS0 | C1_3333DE_PH12 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-08 10:14 | 2019-01-30 | TRUE
IM762584 | 3199UP | 0641_S_AT-GANADLAH_3199UP | Due to EC power cutoff , Stolen batteries , Recovered | batt | Batteries | batt | Batteries | 303847 | 01_S_AT-GANADLAH_3199UP | C2_3199UP_PH13 | (Batteries/Item(s) stolen/site Batteries were Stolen) | 2019-09-08 11:14 | 2019-01-15 | TRUE
IM762669 | 3501DE | 0501_S_SK-SANIYA_3501DE | access owner/the owner switch MCB OFF/Finencial problem/Stolen batteries | batt | Batteries | batt | Batteries | 345238 | SK-SANIYA | C1-3501DE-PH13 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-08 13:28 | 2019-06-03 | TRUE
IM762813 | 0749UP | 1251_Q_AT-MANFALOUT-2_0749UP | Due to Generator problem , weak batteries , Recovered | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 356128 | 01_H_AT-MANFALOUT-2_0749UP | C2_0749UP_PH11 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leaage) (ATS / Engine/Components faulty/gen need new battery) | 2019-09-08 18:56 | 2019-08-24 | TRUE
IM762856 | 3521UP | 02_G_QN-HIBILAT-WST_3521UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | batt Gen generator | Batteries Generator Generator | batt Gen generator | Batteries Generator | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | (Batteries/Item(s) stolen/Batteries were stolen) (ATS / Engine/Components faulty/Gen battery is faulty need new one) (ATS / Engine/Panorama pictures for each system/Last gen hour meter at Audit g ( 4570 )) (ATS / Engine/Panorama pictures for each system/Panorama site view in outside site) | 2019-09-08 21:40 | 2019-04-04 | TRUE
IM762870 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem & no backup & access VF (T) | backup DG | Batteries Generator | backup | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | (Batteries/Some parts are (missing / stolen)/missing battereis) | 2019-09-08 21:54 | 2019-08-14 | TRUE
IM762898 | 0711AL | 03058_G_0711AL_MM-AMWAJ | GN problem/ GN total failure/ restored on Honda till change the GN engine | GN | Generator | GN | Generator | 345399 | MS-AMWAJ | C5_0711AL_PH14 | (ATS / Engine/Unit earth/Earth not connected) (ATS / Engine/Components faulty/Emergency key not working) (ATS / Engine/Components faulty/Housing so broken) | 2019-09-09 01:31 | 2019-06-20 | TRUE
IM762914 | 3898DE | 0821_S_BH-ZUBAYDA_3898DE | Main power / Stolen batteries / SC GN problem | batt GN | Batteries Generator | batt GN | Batteries Generator | 335128 | BH-ZUBAYDA | C1_3898DE_PH14 | (Batteries/Item(s) stolen/There is no battery for site) (ATS / Engine/Components faulty/There is no battery for site (Check small generator operation)) | 2019-09-08 23:06 | 2019-05-15 | TRUE
IM762924 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Due to Generator problem , weak batteries , Recovered | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | (ATS / Engine/Components faulty/Gen battery was defected) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM organization/ATS Cables not organized) | 2019-09-09 02:35 | 2019-05-18 | TRUE
IM762933 | 0711AL | 03058_G_0711AL_MM-AMWAJ | GN problem/ GN total failure/ Honda connected continuously/ honda failed/ restored on another honda till change the GN engine | GN | Generator | GN | Generator | 345399 | MS-AMWAJ | C5_0711AL_PH14 | (ATS / Engine/Unit earth/Earth not connected) (ATS / Engine/Components faulty/Emergency key not working) (ATS / Engine/Components faulty/Housing so broken) | 2019-09-09 05:16 | 2019-06-20 | TRUE
IM762966 | 3590DE | 1631_S_BH-HADIN_3590DE | Main power / Stolen batteries / SC GN problem | batt GN | Batteries Generator | batt GN | Batteries Generator | 324439 | BH-HADIN | C2_3590DE_PH13 | (Batteries/Item(s) stolen/There is no battery for site) (ATS / Engine/Components faulty/Check small generator operation (There is no battery for site)) | 2019-09-09 05:47 | 2019-03-07 | TRUE
IM762985 | 3065UP | 0641_S_QN-ELARAKI_3065UP | Main power disconnection , Stolen batteries , P.G connected | batt | Batteries | batt | Batteries | 356496 | 01_S_QN-ELARAKI_3065UP | C1_3065UP_PH13 | (Batteries/Some parts are (missing / stolen)/Batteries were stolen) | 2019-09-09 07:09 | 2019-10-07 | FALSE
IM762994 | 3590DE | 1631_S_BH-HADIN_3590DE | GN problem / stolen batteries | batt GN | Batteries Generator | batt GN | Batteries Generator | 324439 | BH-HADIN | C2_3590DE_PH13 | (Batteries/Item(s) stolen/There is no battery for site) (ATS / Engine/Components faulty/Check small generator operation (There is no battery for site)) | 2019-09-09 07:34 | 2019-03-07 | TRUE
IM763020 | 3828DE | 0961_S_BH-GWAD-HUSNI_3828DE | Main power / stolen batteries | batt | Batteries | batt | Batteries | 356184 | BH-GWAD-HUSNI | C1_3828DE_PH14 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) | 2019-09-09 08:41 | 2019-09-02 | TRUE
IM763033 | 0964UP | 0181_S_SG-SALLA_0964UP | Main power disconnection ,batteries are suspected to be weak , P.G connected | batt | Batteries | batt | Batteries | 345407 | SG-SALLA | C2_0964UP_PH12 | (Batteries/Some parts are (missing / stolen)/site Batteries were stolen) | 2019-09-09 08:58 | 2019-06-19 | TRUE
IM763052 | 3151UP | 1561_S_BS-QIMAN-AROS_3151UP | Due to EC power cutoff , weak batteries , PG Connected | batt | Batteries | batt | Batteries | 355911 | 01_S_BS-QIMAN-AROS_3151UP | C2_3151UP_PH13 | (Rectifiers/Alarms reporting to the OMC/Loop on the minor alarm in DDF (Port 6)) (Rectifiers/Alarms reporting to the OMC/The power alarm is faulty (Always active on the rectifier and OMC)) | 2019-09-09 09:38 | 2019-07-28 | TRUE
IM763087 | 0711AL | 03058_G_0711AL_MM-AMWAJ | GN problem/ GN total failure/ Honda connected continuously/ honda failed/ restored on another honda till change the GN engine | GN | Generator | GN | Generator | 345399 | MS-AMWAJ | C5_0711AL_PH14 | (ATS / Engine/Unit earth/Earth not connected) (ATS / Engine/Components faulty/Emergency key not working) (ATS / Engine/Components faulty/Housing so broken) | 2019-09-09 09:56 | 2019-06-20 | TRUE
IM763104 | 0324UP | 1421_S_MN-BARTABAT_0324UP | Due to EC power cutoff , Stolen batteries , PG Connected | batt | Batteries | batt | Batteries | 324919 | 01_S_MN-BARTABAT_0324UP | C1_0324UP_PH8 | (Batteries/Item(s) stolen/Site batteries were stolen) | 2019-09-09 10:17 | 2019-04-20 | TRUE
IM763115 | 3628DE | 0811_S_GH-QSR-BAGHDAD_3628DE | Main power / Stolen batteries | batt | Batteries | batt | Batteries | 324836 | GH-QSR-BAGHDAD | C2_3628DE_PH13 | (Batteries/Item(s) stolen/Stolen batteries) | 2019-09-09 10:08 | 2019-04-15 | TRUE
IM763132 | 3836DE | 0661_S_SK-HAGARSA_3836DE | Main power at site SK-HAGARSA_3836DE/Stolen battery/site clear@EC come back | batt | Batteries | batt | Batteries | 345237 | SK-HAGARSA | C1-3836DE-PH14 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-09 10:28 | 2019-06-03 | TRUE
IM763166 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Due to Generator problem , weak batteries , PG Connected | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | (ATS / Engine/Components faulty/Gen battery was defected) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM organization/ATS Cables not organized) | 2019-09-09 11:04 | 2019-05-18 | TRUE
IM763198 | 0149CA | 02181_S_0149CA_HAKIME | down due to power problem and battery stolen | batt | Batteries | batt | Batteries | 324801 | HAKIME | C1_0149CA_PH1 | (Batteries/Item(s) stolen/All batteries are stolen) (Batteries/Item(s) stolen/All batteries are stolen and cables are disconnected) | 2019-09-09 11:36 | 2019-04-09 | TRUE
IM763203 | 4342DE | U_S_4342DE_BAHTIM8 | down due to commercial cut and stolen batteries at 4342DE_BAHTIM8 | batt | Batteries | batt | Batteries | 356147 | U_S_4342DE_BAHTIM8 | C1_4342DE_PH18 | (Rectifiers/Alarms reporting to the OMC/Rectifier alarms don't appear on the OMC) (Batteries/Some parts are (missing / stolen)/All batteries are stolen) | 2019-09-09 11:39 | 2019-08-26 | TRUE
IM763219 | 3344DE | 0681_S_BH-ELNEGILY_3344DE | Share VF / VF guard switched off Orange C.B / Main power / stolen batteries | batt | Batteries | batt | Batteries | 304214 | BH-ELNEGILY | C3_3344DE_PH12 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-09 11:42 | 2019-02-12 | TRUE
IM763221 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Share VF / VF GN problem / stolen batteries / PG handle other sites | batt GN | Batteries Generator | batt GN | Batteries Generator | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | (Batteries/Item(s) stolen/Stolen) (ATS / Engine/Item(s) stolen/missing battery) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) | 2019-09-09 11:39 | 2019-03-25 | TRUE
IM763307 | 0954UP | 01_G_MN-DAHMARU_0954UP | Due to EC power cutoff , Stolen batteries , Recovered | batt | Batteries | batt | Batteries | 324946 | 01_G_MN-DAHMARU_0954UP | C1_0954UP_PH12 | (Batteries/Item(s) stolen/site baateries were stolen) | 2019-09-09 12:58 | 2019-04-25 | TRUE
IM763323 | 0641UP | 0931_G_BS-KAMBISH-VLG_0641UP_X | Due to Generator problem , weak batteries , PG Connected | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 355976 | 01_G_BS-KAMBISH-VLG_0641UP | C1_0641UP_PH9 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage of the engine) (ATS / Engine/Unit earth/Stolen earth connections of the genset panel) (ATS / Engine/Components faulty/The rubber bases of the radiator are faulty) (ATS / Engine/Components faulty/The dynamo belt needs to be tensioned) (ATS / Engine/Wrong connection/The negative pole of the battery isn't connected) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Missing terminals of cables connected to contactors and CBs inside the genset panel) | 2019-09-09 13:19 | 2019-07-30 | TRUE
IM763382 | 3776UP | 02_G_SG-HARJA-QARAN_3776UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | batt Gen generator | Batteries Generator Generator | batt Gen generator | Batteries Generator | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | (Batteries/Item(s) stolen/Batteries were stolen) (ATS / Engine/Components faulty/Gen battery is faulty need new one) (ATS / Engine/Panorama pictures for each system/Last gen hour meter at Audit g ( 4570 )) (ATS / Engine/Panorama pictures for each system/Panorama site view in outside site) | 2019-09-09 14:14 | 2019-04-04 | TRUE
IM763429 | 0370UP | 1961_G_CAIRO-ASWAN-12_0370UP | Main power disconnection ,batteries are suspected to be weak , P.G connected | batt | Batteries | batt | Batteries | 304136 | 01_G_CAIRO-ASWAN-12_0370UP | C2_0370UP_PH8 | (Batteries/Item(s) stolen/ Batteries were stolen) | 2019-09-09 14:57 | 2019-02-07 | TRUE
IM763540 | 3349CA | 01126_S_3349CA_IMBABA-6 | down due to commercial cut and stolen batteries (MA) | batt | Batteries | batt | Batteries | 303961 | IMBABA-6 | C2_3349CA_PH12 | (Batteries/Components faulty/Batteries are in a very bad condition (DC voltage dropped to 42.7V. after 1 min of power disconnecting)) | 2019-09-09 16:39 | 2019-01-21 | TRUE
IM763568 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem and no battery and PG access | batt DG | Batteries Generator | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | (Batteries/Some parts are (missing / stolen)/missing battereis) | 2019-09-09 17:42 | 2019-08-14 | TRUE
IM763574 | 3955DE | 0731_S_SK-QRMT-SAHBRA_3955DE | access ET/ET GN peoblem/Stolen batteries/clear after GN working | batt GN | Batteries Generator | batt | Batteries | 356230 | SK-QRMT-SAHBRA | C1_3955DE_PH15 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-09 16:45 | 2019-09-07 | TRUE
IM763607 | 0076DE | 0561_H_DK-BATRAH_0076DE | Main power / stolen batteries | batt | Batteries | batt | Batteries | 304322 | BATRAH | C1_0076DE_PH1 | (Batteries/Item(s) stolen/stolen batteries) | 2019-09-09 19:07 | 2019-02-25 | TRUE
IM763629 | 0517RE | 03217_E_0517RE_SZ-GALALA-CAMP | Site Down Due To DG Power Alarm - Access RD H&S - Recovered once DG problem solved | DG | Generator | DG | Generator | 304374 | SZ-GALALA-CAMP | 0517RE | (ATS / Engine/Components faulty/missing battery ) (ATS / Engine/Wrong connection/wrong connection for cables ) (ATS / Engine/Wrong connection/welded cables ) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/power cable not protected inside PVC or tray ) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/fuel tank pipes not protected inside tray ) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/broken PVC ) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/cable not terminated ) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/cables not terminated ) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/bad termination for cable ) | 2019-09-09 20:26 | 2019-02-24 | TRUE
IM763724 | 0268RE | 03848_G_0268RE_RS-BDWYA-MARSA | Site Down Due To DG Power Alarm - weak batteries - Recovered once DG problem solved | batt DG | Batteries Generator | DG | Generator | 304329 | 01_G_RS-BDWYA-MARSA_0268RE | C2_0268RE_PH9 | (ATS / Engine/Components faulty/Gen battery is faulty) (ATS / Engine/Panorama pictures for each system/Open gland in Gen enclosure need insulation) (ATS / Engine/Panorama pictures for each system/Last Gen hour meter at Audit G ( 9838 )) (ATS / Engine/Panorama pictures for each system/Panorama site view in outside site) | 2019-09-10 02:33 | 2019-02-20 | TRUE
IM763752 | 3729UP | 01_E_WAHT-BHREY-ENT_3729UP | Due to Generator problem , weak batteries , Recovered | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure ) (ATS / Engine/Wrong connection/generator battery as used in the site and not suitable in High temp) | 2019-09-10 06:29 | 2019-07-01 | TRUE
IM763765 | 3199UP | 0641_S_AT-GANADLAH_3199UP | Due to EC power cutoff , Stolen batteries , Recovered | batt | Batteries | batt | Batteries | 303847 | 01_S_AT-GANADLAH_3199UP | C2_3199UP_PH13 | (Batteries/Item(s) stolen/site Batteries were Stolen) | 2019-09-10 07:34 | 2019-01-15 | TRUE
IM763843 | 3009AL | 03232_D_3009AL_MM-ALMN-APT2 | GN problem/ weak batteries/ restored after solve GN problem | batt GN | Batteries Generator | batt GN | Batteries Generator | 324992 | MM-ALMN-APT2 | C1_3009AL_PH19 | (Batteries/Components faulty/stolen batteries ) (ATS / Engine/Components faulty/missing battery ) (ATS / Engine/Wrong connection/wrong connection for cables ) (ATS / Engine/Wrong connection/welded cables ) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/power cable not protected inside PVC or tray ) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/fuel tank pipes not protected inside tray ) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/broken PVC ) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/cable not terminated ) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/cables not terminated ) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/bad termination for cable ) (ATS / Engine/Components faulty/Burned generator need to be replaced.) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Vodafone gen has leakage.) | 2019-09-10 09:58 | 2019-05-01 | TRUE
IM763844 | 0964UP | 0181_S_SG-SALLA_0964UP | Main power disconnection ,batteries are suspected to be weak , recovered when EC power come back | batt | Batteries | batt | Batteries | 345407 | SG-SALLA | C2_0964UP_PH12 | (Batteries/Some parts are (missing / stolen)/site Batteries were stolen) | 2019-09-10 08:57 | 2019-06-19 | TRUE
IM763849 | 3333DE | 0181_S_BH-OM-SABER_3333DE | main power/stolen battery/power back | batt | Batteries | batt | Batteries | 304089 | BH-OM-SABER_SSS0 | C1_3333DE_PH12 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-10 09:41 | 2019-01-30 | TRUE
IM763850 | 3489DE | 0461_S_DK-KFR-GHANNAM_3489DE | main power/stolen battery/power back | batt | Batteries | batt | Batteries | 325088 | DK-KFR-GHANNAM | C1-3489DE-PH13 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-10 09:50 | 2019-05-09 | TRUE
IM763876 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to DG VF problem and no battery and PG access | batt DG | Batteries Generator | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | (Batteries/Some parts are (missing / stolen)/missing battereis) | 2019-09-10 10:06 | 2019-08-14 | TRUE
IM763908 | 0316RE | 03493_S_0316RE_SZ-GHAZZALY | Power outage // access PG // Weak batteries // Recovered | batt | Batteries | batt | Batteries | 355925 | 01_S_SZ-GHAZZALY_0316RE | C2_0316RE_PH12 | (Rectifiers/Alarms reporting to the OMC/Alarm on the rectifier ) | 2019-09-10 10:53 | 2019-07-30 | TRUE
IM763929 | 3490UP | 01_D_AT-ELHASANI_3490UP | Due to Generator problem , weak batteries , Recovered | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 356124 | 01_G_AT-ELHASANI_3490UP | C2_3490UP_PH14 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leaage from ET gen) (ATS / Engine/Components faulty/Gen need new battery) | 2019-09-10 10:36 | 2019-08-24 | TRUE
IM764013 | 3798DE | 1471_S_SK-MNZL-MYMON_3798DE | Main power/stolen battery/connect PG | batt | Batteries | batt | Batteries | 355763 | SK-MNZL-MYMON | C2-3798DE-PH14 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-10 11:39 | 2019-07-10 | TRUE
IM764022 | 0076DE | 0561_H_DK-BATRAH_0076DE | Main Power / stolen batteries | batt | Batteries | batt | Batteries | 304322 | BATRAH | C1_0076DE_PH1 | (Batteries/Item(s) stolen/stolen batteries) | 2019-09-10 12:13 | 2019-02-25 | TRUE
IM764033 | 0421DE | 0721_H_MF-MANSH-SOLTN_0421DE | Main power/battery under invistigation/power back | batt | Batteries | batt | Batteries | 304300 | MF-MANSH-SOLTN | C1_0421DE_PH4 | (Batteries/Some parts are missing/Battery racks are placed directly under A/C IDU) | 2019-09-10 12:25 | 2019-02-21 | TRUE
IM764120 | 0427DE | 0061_D_SK-EZBA-SARYA_0427DE | GEN problem/stolen battery/generator working | batt Gen generator | Batteries Generator Generator | batt Gen generator | Batteries Generator | 345382 | SK-EZBA-SARYA | C2_0427DE_PH4 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) (ATS / Engine/Components faulty/Exhaust fan not working and another not exist) | 2019-09-10 13:06 | 2019-06-16 | TRUE
IM764182 | 3777UP | 1281_E_AS-RAGHAMA_3777UP_X | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | batt Gen generator | Batteries Generator Generator | batt Gen generator | Batteries Generator | 355941 | 01_G_AS-RAGHAMA_3777UP | C2_3777UP_PH15 | (Batteries/Components faulty/One Battery was explosion) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage) (ATS / Engine/Unit earth/Gen earth cable is missing) | 2019-09-10 14:32 | 2019-08-02 | TRUE
IM764214 | 3775DE | 0471_D_DK-DABBOS-VLG_3775DE | GN problem / batteries under check | batt GN | Batteries Generator | GN | Generator | 325073 | DK-DABBOS-VLG | C1_3775DE_PH14 | (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/bad terminals) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) | 2019-09-10 14:45 | 2019-05-07 | TRUE
IM764243 | 3578UP | 01_N_SG-KOUM-ELASFR_3578UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 355944 | 01_N_SG-KOUM-ELASFR_3578UP | C3_3578UP_PH14 | (ATS / Engine/Components faulty/Gen battery is faulty) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Missing terminals) (ATS / Engine/Filters condition oil/fuel/air/Air filter need clean) | 2019-09-10 15:07 | 2019-08-01 | TRUE
IM764261 | 3298UP | 01_S_SG-SHOHADAA_3298UP | Main power disconnection , Stolen batteries , P.G connected | batt | Batteries | batt | Batteries | 356366 | 01_O_SG-RYAYNA-HAGR_3744UP | C1_3744UP_PH16 | (Batteries/Some parts are (missing / stolen)/Site batteries were Stolen) | 2019-09-10 16:01 | 2019-09-18 | FALSE
IM764301 | 3744UP | 01_S_SG-RYAYNA-HAGR_3744UP | Generator Problem ,Stolen batteries ,Recovered after solvig the generator problem . | batt Gen generator | Batteries Generator Generator | batt Gen generator | Batteries Generator | 356366 | 01_O_SG-RYAYNA-HAGR_3744UP | C1_3744UP_PH16 | (Batteries/Some parts are (missing / stolen)/Site batteries were Stolen) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Missing terminals in power cables) | 2019-09-10 17:56 | 2019-09-18 | FALSE
IM764305 | 3170DE | 0971_S_MF-WARDAN-2_3170DE | main power/battery under ivistigation/connect @MF-KHTATBA-FRM& MF-KHATATBA-RD | batt | Batteries | batt | Batteries | 355958 | MF-WARDAN-2 | C1_3170DE_PH12 | (Batteries/Some parts are (missing / stolen)/Disconnected battery strng) | 2019-09-10 18:03 | 2019-08-03 | TRUE
IM764307 | 3276UP | 02_G_QN-BAKHANES_3276UP | Generator Problem- Alternator problem , Stolen Batteries , P.G Connected | batt Gen generator | Batteries Generator Generator | batt Gen generator | Batteries Generator | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | (Batteries/Item(s) stolen/Batteries were stolen) (ATS / Engine/Components faulty/Gen battery is faulty need new one) (ATS / Engine/Panorama pictures for each system/Last gen hour meter at Audit g ( 4570 )) (ATS / Engine/Panorama pictures for each system/Panorama site view in outside site) | 2019-09-10 19:03 | 2019-04-04 | TRUE
IM764311 | 3454DE | 1061_D_GH-MAHLT-MENOF_3454DE | Access ET / GN problem / stolen batteries | batt GN | Batteries Generator | batt GN | Batteries Generator | 324838 | GH-MAHLT-MENOF | C2_3454DE_PH13 | (Batteries/Item(s) stolen/Stolen Batteries) (ATS / Engine/Item(s) stolen/stolen batteries) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) | 2019-09-10 18:11 | 2019-04-10 | TRUE
IM764360 | 0038RE | 00210_C_0038RE_3P-SZ-RAS-ABU-DRAJ | Site Down Due To DG Power Alarm - dead batteries PLVD disconnect site to save cascaded Recovered once DG problem solved | batt DG PLVD | Batteries Generator Rectifier | DG | Generator | 304375 | SZ-RAS-ABU-DRAJ | C3_0038RE_PH2 | (ATS / Engine/Components faulty/missing battery ) (ATS / Engine/Wrong connection/welded cables ) (ATS / Engine/Wrong connection/wrong connection & jumper on the contactor) (ATS / Engine/Wrong connection/cable not isolated ) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/cables not terminated ) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage ) | 2019-09-10 20:54 | 2019-02-24 | TRUE
IM764363 | 0316RE | 03493_S_0316RE_SZ-GHAZZALY | Power outage // access PG // Weak batteries // Recovered | batt | Batteries | batt | Batteries | 355925 | 01_S_SZ-GHAZZALY_0316RE | C2_0316RE_PH12 | (Rectifiers/Alarms reporting to the OMC/Alarm on the rectifier ) | 2019-09-10 21:01 | 2019-07-30 | TRUE
IM764374 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to DG low water level and stolen batteries (M) | batt DG | Batteries Generator | batt DG | Batteries Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | (Batteries/Some parts are missing/missing batteries) (ATS / Engine/Wrong connection/wrong connection) | 2019-09-10 21:43 | 2019-02-26 | TRUE
IM764388 | 3712DE | 0221_G_BH-QAMHA_3712DE | Main power problem " Disconnected by EC" @ BH-QAMHA_3712DE / SC GN not work due to SC / Solved and work on SC GN | GN | Generator | GN | Generator | 304258 | BH-QAMHA | C1_3712DE_PH14 | (ATS / Engine/Components faulty/Small generator not working // Site has history generator status alarm) | 2019-09-10 22:43 | 2019-02-19 | TRUE
IM764412 | 0646CA | 02128_N_0646CA_OM-BAYOUMI | down due to power failure and faulty batteries and no PG access (M) | batt | Batteries | batt | Batteries | 345350 | OM-BAYOUMI | C3_0646CA_PH8 | (Rectifiers/Alarms reporting to the OMC/Major alarm is active on the site) (Batteries/Components faulty/Batteries are faulty (Site is down when the power is disconnected)) | 2019-09-11 01:49 | 2019-06-17 | TRUE
IM764445 | 3454DE | 1061_D_GH-MAHLT-MENOF_3454DE | ET Share / GN problem / Stolen batteries | batt GN | Batteries Generator | batt GN | Batteries Generator | 324838 | GH-MAHLT-MENOF | C2_3454DE_PH13 | (Batteries/Item(s) stolen/Stolen Batteries) (ATS / Engine/Item(s) stolen/stolen batteries) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) | 2019-09-11 04:22 | 2019-04-10 | TRUE
IM764493 | 3639UP | 0501_G_LU-ODYSAT-QBLY_3639UP | PM generator ; Stolen batteries , Recovered | batt Gen generator | Batteries Generator Generator | batt Gen generator | Batteries Generator | 356474 | 01_G_LU-ODYSAT-QBLY_3639UP | C1_3639UP_PH14 | (Batteries/Some parts are (missing / stolen)/Batteries were stolen) (ATS / Engine/Unit earth/Gen enclosure earth cable is missing) (ATS / Engine/Unit earth/Missing earth cable at ATS panel) (ATS / Engine/Wrong connection/Two cables inserted in one slot can cause bad connections) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/ cable is loose inside ATS panel) | 2019-09-11 07:40 | 2019-10-01 | FALSE
IM764511 | 3464DE | 0151_Q_BH-SHANDID_3464DE | GN problem @BH-SHANDID_3464DE / stolen batteries | batt GN | Batteries Generator | GN | Generator | 304032 | BH-SHANDID | C2_3464DE_PH13 | (ATS / Engine/Components below rate (excluding main power feeder if not hot)/Generator voltage need adjustment) | 2019-09-11 07:25 | 2019-01-24 | TRUE
IM764516 | 0324UP | 1421_S_MN-BARTABAT_0324UP | Due to EC power cutoff , Stolen batteries , PG Connected | batt | Batteries | batt | Batteries | 324919 | 01_S_MN-BARTABAT_0324UP | C1_0324UP_PH8 | (Batteries/Item(s) stolen/Site batteries were stolen) | 2019-09-11 08:22 | 2019-04-20 | TRUE
IM764615 | 0022SI | 03519_H_0022SI_IS-ABU-ATWA | Outage power in area located site , stolen batteries , once team arrive to connect PG power restored and site recovered | batt | Batteries | batt | Batteries | 325082 | 01_H_IS-ABU-ATWA_0022SI | C8_0022SI_PH1 | (Batteries/Item(s) stolen/Battery string stolen) | 2019-09-11 10:12 | 2019-05-04 | TRUE
IM764618 | 0427DE | 0061_D_SK-EZBA-SARYA_0427DE | access Guard/GN problem/Stolen batteries/clear | batt GN | Batteries Generator | batt GN | Batteries Generator | 345382 | SK-EZBA-SARYA | C2_0427DE_PH4 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) (ATS / Engine/Components faulty/Exhaust fan not working and another not exist) | 2019-09-11 09:29 | 2019-06-16 | TRUE
IM764621 | 3126DE | 0121_S_DK-HAGYZEYA_3126DE | main power/Stolen batteries handel SK Roda,,DK-TAG-ELIZZ_ | batt | Batteries | batt | Batteries | 355992 | DK-HAGYZEYA | C6-3126DE-PH12 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-11 09:47 | 2019-08-07 | TRUE
IM764623 | 3830DE | 1311_S_BH-MHLT-KYL_3830DE | Share VF / Main power / Stolen batteries | batt | Batteries | batt | Batteries | 356185 | BH-MHLT-KYL | C1_3830DE_PH14 | (Batteries/Some parts are (missing / stolen)/No battery for site) | 2019-09-11 10:13 | 2019-09-02 | TRUE
IM764624 | 3532DE | 0511_S_SK-NATORA_3532DE | access Guard/week battery/clear after power back | batt | Batteries | batt | Batteries | 356262 | SK-NATORA | C2_3532DE_PH13 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-11 10:18 | 2019-09-11 | TRUE
IM764654 | 0993UP | 0041_S_AT-ELOUNA_0993UP | Due to EC power cutoff , weak batteries , PG Connected | batt | Batteries | batt | Batteries | 355474 | 01_S_AT-ELOUNA_0993UP | C1_0993UP_PH12 | (Rectifiers/Alarms reporting to the OMC/Power alarm not appeared on the omc) | 2019-09-11 10:07 | 2019-06-26 | TRUE
IM764707 | 3953DE | 0361_G_BH-MAARKA_3953DE | access ET/main power/weak batteries/clear after power back | batt | Batteries | batt | Batteries | 304235 | BH-MAARKA | C1_3953DE_PH15 | (Batteries/Components faulty/Faulty battery and cable disconnected) | 2019-09-11 10:46 | 2019-02-14 | TRUE
IM764717 | 3784DE | 0661_S_KS-DAQLIT_3784DE | Share VF / Main power / faulty batteries | batt | Batteries | batt | Batteries | 335221 | KS-DAQLIT | C3_3784DE_PH14 | (Batteries/Components faulty/Faulty battery (battearies are ballooned)) | 2019-09-11 11:18 | 2019-05-26 | TRUE
IM764723 | 3628DE | 0811_S_GH-QSR-BAGHDAD_3628DE | Main power / stolen batteries | batt | Batteries | batt | Batteries | 324836 | GH-QSR-BAGHDAD | C2_3628DE_PH13 | (Batteries/Item(s) stolen/Stolen batteries) | 2019-09-11 10:58 | 2019-04-15 | TRUE
IM764745 | 0285DE | 1401_G_BH-ABU-HUMMUS_0285DE | GN problem / weak batteries | batt GN | Batteries Generator | GN | Generator | 304381 | BH-ABU-HUMMUS | C2_0285DE_PH3 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) (ATS / Engine/Unit earth/fake earth) (ATS / Engine/Components faulty/faulty) (ATS / Engine/Components faulty/replace) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Cables at 1 slot) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot) | 2019-09-11 11:56 | 2019-03-03 | TRUE
IM764750 | 0490SI | 03534_S_0490SI_IS-NASR | Outage power in area located site , dead batteries , once team arrive to connect PG power restored and site recovered | batt | Batteries | batt | Batteries | 356007 | 01_S_IS-NASR_0490SI | C2_0490SI_PH14 | (Rectifiers/Alarms reporting to the OMC/Rectifier alarm , A/C & door not apear on CAP) (Batteries/Components faulty/Battery voltag reading drop to 46 volt after we disconnect th rectifier C.B (Check the batteries)) | 2019-09-11 11:51 | 2019-08-07 | TRUE
IM764782 | 0003UP | 0311_N_AS-TROMBAT-AS_0003UP | Main power disconnection ,batteries are suspected to be weak , recovered when EC power come back | batt | Batteries | batt | Batteries | 345338 | 01_N_AS-TROMBAT-AS_0003UP | C1_0003UP_PH0 | (Batteries/Some parts are (missing / stolen)/one Batteries string was stolen) | 2019-09-11 12:00 | 2019-06-12 | TRUE
IM764806 | 0517DE | 1541_G_QL-TUKH-TRAIN_0517DE | access Guard/main power/weak batteries/clear after power back | batt | Batteries | batt | Batteries | 303890 | QL-TUKH-TRAIN BSC | C1_0517DE_PH8 | (Batteries/Item(s) stolen/stolen batteries) | 2019-09-11 12:56 | 2019-01-19 | TRUE
IM764852 | 4057DE | 0011_D_SK-SALHIYA-NTH_4057DE | GN problem/Stolen batteries/clear after check GN | batt GN | Batteries Generator | batt GN | Batteries Generator | 324501 | SK-SALHIYA-NTH | C3_4057DE_PH15 | (Batteries/Item(s) stolen/No backup batteries.) (ATS / Engine/Components faulty/Faulty GCM module.) (ATS / Engine/Wrong connection/Some cables disconnected.) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has oil leakage and bad condition.) (ATS / Engine/Panorama pictures for each system/Overview.) | 2019-09-11 12:56 | 2019-03-13 | TRUE
IM764857 | 3628DE | 0811_S_GH-QSR-BAGHDAD_3628DE | Main power / stolen batteries / connected PG | batt | Batteries | batt | Batteries | 324836 | GH-QSR-BAGHDAD | C2_3628DE_PH13 | (Batteries/Item(s) stolen/Stolen batteries) | 2019-09-11 13:14 | 2019-04-15 | TRUE
IM764871 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to DG problem and restored after clean fuel cycle and stolen batteries | batt DG | Batteries Generator | batt DG | Batteries Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | (Batteries/Some parts are missing/missing batteries) (ATS / Engine/Wrong connection/wrong connection) | 2019-09-11 14:01 | 2019-02-26 | TRUE
IM764884 | 3743UP | 01_E_MN-EBAD-SHRONA_3743UP | Due to Generator problem , weak batteries , Recovered | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 324960 | 01_S_MN-EBAD-SHRONA_3743UP | C3_3743UP_PH15 | (ATS / Engine/Components faulty/Gen battery is missing) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Main power cable is not protected in Pac Tube) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Battery cables not isolated) (ATS / Engine/Panorama pictures for each system/Panorama) | 2019-09-11 13:36 | 2019-04-25 | TRUE
IM764889 | 3445UP | 591_D_MN-TOKH_3445UP | Due to Generator problem , Stolen batteries , Recovered | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 356182 | 01_G_MN-TOKH_3445UP | C1_3445UP_PH14 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage) (ATS / Engine/Components faulty/need battery) | 2019-09-11 14:16 | 2019-08-28 | TRUE
IM764924 | 3712DE | 0221_G_BH-QAMHA_3712DE | GN problem @BH-QAMHA_3712DE / batteries under check | batt GN | Batteries Generator | GN | Generator | 304258 | BH-QAMHA | C1_3712DE_PH14 | (ATS / Engine/Components faulty/Small generator not working // Site has history generator status alarm) | 2019-09-11 13:47 | 2019-02-19 | TRUE
IM764934 | 0370UP | 1961_G_CAIRO-ASWAN-12_0370UP | Main power disconnection , stolen batteries , recovered when EC power come back | batt | Batteries | batt | Batteries | 304136 | 01_G_CAIRO-ASWAN-12_0370UP | C2_0370UP_PH8 | (Batteries/Item(s) stolen/ Batteries were stolen) | 2019-09-11 15:06 | 2019-02-07 | TRUE
IM764954 | 3074UP | 01_D_QN-QENAWEYA_3074UP | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 324506 | 01_G_QN-QENAWEYA_3074UP | C1_3074UP_PH13 | (ATS / Engine/Components faulty/Gen battery is faulty) (ATS / Engine/Components faulty/Main c.b inside gen had one faulty slot and one phase welded directly) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage exist under fuel tank) (ATS / Engine/Panorama pictures for each system/Open gland in Gen enclosure need insulation) (ATS / Engine/Panorama pictures for each system/Panorama site view in outside site) (ATS / Engine/Panorama pictures for each system/Last Gen hour meter at Audit G (18510 )) | 2019-09-11 15:24 | 2019-03-13 | TRUE
IM765018 | 0280DE | 0601_Q_BH-KOMHMADA-NTH_0280DE | GN problem @ BH-KOMHMADA-NTH_0280DE / Stolen batteries | batt GN | Batteries Generator | batt GN | Batteries Generator | 355878 | BH-KOMHMDA-NTH | C6_0280DE_PH3 | (Batteries/Some parts are (missing / stolen)/Stolen ) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Leakage) (ATS / Engine/Unit earth/Disconnected) | 2019-09-11 17:09 | 2019-07-21 | TRUE
IM765025 | 0613DE | 00167_D_0613DE_SANDORINI-CLUB | GN problem/Batteries under investigation/clear after check GN | batt GN | Batteries Generator | GN | Generator | 303981 | Sandorini Country Club | C1_0613DE_PH9 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check and clean) | 2019-09-11 17:11 | 2019-01-22 | TRUE
IM765048 | 0339UP | 0351_G_MN-SALEEBA_0339UP | Due to Generator problem , weak batteries , Recovered | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 324684 | 01_G_MN-SALEEBA_0339UP | C3_0339UP_PH8 | (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/protect cable) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage) | 2019-09-11 18:50 | 2019-03-28 | TRUE
IM765069 | 0164RE | 03835_S_0164RE_RS-QUSEIR-ENT | Outage power in area located site , dead batteries , access PG Recovered once power restored | batt | Batteries | batt | Batteries | 356402 | 01_S_RS-QUSEIR-ENT_0164RE | C1_0164RE_PH9 | (Rectifiers/Alarms reporting to the OMC/Rectifer minor alarm was looped at ddf rack) | 2019-09-11 17:03 | 2019-09-25 | FALSE
IM765125 | 0658DE | 0661_D_BH-MNSHYT-KHYAT_0658DE | GN problem @ BH-MNSHYT-KHYAT_0658DE / weak batteries / power alarm received 10:30 PM | batt GN | Batteries Generator | GN | Generator | 356260 | BH-MNSHYT-KHYAT | C2_0658DE_PH9 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has leakage) (ATS / Engine/Components below/over rate (excluding main power feeder if not hot)/Generator has high voltage) | 2019-09-11 22:19 | 2019-09-05 | TRUE
IM765159 | 0427DE | 0061_D_SK-EZBA-SARYA_0427DE | GN. Problem /Stolen batteries / clear after checking GN. | batt GN | Batteries Generator | batt GN | Batteries Generator | 345382 | SK-EZBA-SARYA | C2_0427DE_PH4 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) (ATS / Engine/Components faulty/Exhaust fan not working and another not exist) | 2019-09-11 22:21 | 2019-06-16 | TRUE
IM765165 | 3259UP | 1401_G_BS-MAIDUM_3259UP | Generator stopped due to LOP alarm and site has stolen backup batteries | backup batt Gen generator | Batteries Batteries Generator Generator | Gen generator | Generator | 304381 | BH-ABU-HUMMUS | C2_0285DE_PH3 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) (ATS / Engine/Unit earth/fake earth) (ATS / Engine/Components faulty/faulty) (ATS / Engine/Components faulty/replace) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Cables at 1 slot) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot) | 2019-09-11 23:22 | 2019-03-03 | TRUE
IM765200 | 3551UP | 1981_D_SG-ABOU-AZIZ_3551UP | TT will be modified as we received automation mails at 04:05 am , Generator Stoppage , Weak batteries ; Solved | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 304169 | 01_G_SG-ABOU-AZIZ_3551UP | C2_3551UP_PH14 | (ATS / Engine/Components faulty/Gen battery is faulty ) | 2019-09-12 03:04 | 2019-02-09 | TRUE
IM765210 | 3712DE | 0221_G_BH-QAMHA_3712DE | GN problem @BH-QAMHA_3712DE / batteries under check | batt GN | Batteries Generator | GN | Generator | 304258 | BH-QAMHA | C1_3712DE_PH14 | (ATS / Engine/Components faulty/Small generator not working // Site has history generator status alarm) | 2019-09-12 02:58 | 2019-02-19 | TRUE
IM765211 | 0102RE | 00086_S_0102RE_SZ-STLLADEMARE | Outage power in area located site , dead batteries , access PG Recovered once power restored | batt | Batteries | batt | Batteries | 324988 | SZ-STLLADEMARE | C3_0102RE_PH3 | (Batteries/Item(s) stolen/Battery string stolen) | 2019-09-12 04:36 | 2019-05-01 | TRUE
IM765231 | 3594DE | 1241_S_BH-TAYRIYA_3594DE | Main Power / stolen batteries / clear after power back | batt | Batteries | batt | Batteries | 325119 | BH-TAYRIYA | C1-3594DE-PH13 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-12 05:54 | 2019-05-12 | TRUE
IM765233 | 3352DE | 0071_D_BH-SHBRA-OSEEM_3352DE | Access VF. / Main Power / Stolen batteries / Clear after power back | batt | Batteries | batt | Batteries | 325117 | BH-SHBRA-OSEEM | C1_3352DE_PH12 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-12 06:21 | 2019-05-12 | TRUE
IM765234 | 3102UP | 1431_K_QN-MOSTAAMARA_3102UP_X | Due to Gen stopped Problem , stolen batteries , solved. | batt Gen | Batteries Generator | batt Gen | Batteries Generator | 324765 | 01_G_QN-MOSTAAMARA_3102UP | C1_3102UP_PH13 | (Batteries/Item(s) stolen/Batteries were stolen) (ATS / Engine/Wrong connection/cables were welded in Gen) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Missing terminals at gen C.B inside Ats panel ) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/bad connection inside ats panel) (ATS / Engine/Item(s) stolen/Gen battery is missing) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage inside Gen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage beside Gen enclosure) (ATS / Engine/Panorama pictures for each system/Open gland in Gen enclosure need insulation) (ATS / Engine/Panorama pictures for each system/Panorama site view in outside site) | 2019-09-12 07:08 | 2019-04-07 | TRUE
IM765268 | 3454DE | 1061_D_GH-MAHLT-MENOF_3454DE | Share ET / GN stopped / Stolen batteries | batt GN | Batteries Generator | batt GN | Batteries Generator | 324838 | GH-MAHLT-MENOF | C2_3454DE_PH13 | (Batteries/Item(s) stolen/Stolen Batteries) (ATS / Engine/Item(s) stolen/stolen batteries) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) | 2019-09-12 07:08 | 2019-04-10 | TRUE
IM765278 | 0029RE | 03478_S_0029RE_SZ-SUEZ9 | Outage power in area located site , dead batteries , access PG Recovered once power restored | batt | Batteries | batt | Batteries | 345368 | 01_S_SZ-SUEZ9_0029RE | C1_0029RE_PH1 | (Batteries/Cables termination/lugs (AC side), lugs (DC side)/Loose in the battery cable) | 2019-09-12 08:51 | 2019-06-17 | TRUE
IM765379 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN. Problem / batteries under investigation@MIT-GABIR_3833DE / Clear after checking GN | batt GN | Batteries Generator | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | (ATS / Engine/Wrong connection/Welding cables) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot) | 2019-09-12 10:18 | 2019-06-16 | TRUE
IM765386 | 0150UP | 0191_H_GIZA-LUXOR-19_0150UP | Main power disconnection ,batteries are suspected to be weak , P.G connected | batt | Batteries | batt | Batteries | 356518 | 01_W_GIZA-LUXOR-19_0150UP | C1_0150UP_PH3 | (Batteries/Components faulty/backup voltage drop too fast ( batteries need recheck) ) | 2019-09-12 11:10 | 2019-10-10 | FALSE
IM765438 | 3551CA | 02797_G_3551CA_MADINATY-2 | down due to PM problem & no backup & access PG (T) | backup | Batteries | backup | Batteries | 324699 | MADINATY-2 | C1_3551CA_PH13 | (Batteries/Some parts are missing/missing batteries) | 2019-09-12 12:08 | 2019-03-27 | TRUE
IM765464 | 0581DE | 1571_S_SK-IKYAD-BHARIA_0581DE | Hi temp/clear after check Ac's | Hi Temp | A/Cs | Hi Temp | A/Cs | 324498 | SK-IKYAD-BHARIA | C1_0581DE_PH9 | (A/Cs Cooling / Free Cooling / Ventilation/Components faulty/Faulty A/C (site working on one A/C only).) | 2019-09-12 11:26 | 2019-03-13 | TRUE
IM765469 | 3454DE | 1061_D_GH-MAHLT-MENOF_3454DE | ET Share / GN problem / Stolen batteries | batt GN | Batteries Generator | batt GN | Batteries Generator | 324838 | GH-MAHLT-MENOF | C2_3454DE_PH13 | (Batteries/Item(s) stolen/Stolen Batteries) (ATS / Engine/Item(s) stolen/stolen batteries) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) | 2019-09-12 11:53 | 2019-04-10 | TRUE
IM765483 | 3110DE | 1681_D_GH-SHUBRA-RIS_3110DE | Acccess VF / VF GN problem @ GH-SHUBRA-RIS_3110DE / weak batteries | batt GN | Batteries Generator | GN | Generator | 324613 | GH-SHUBRA-RIS | C1_3110DE_PH12 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) | 2019-09-12 12:00 | 2019-03-25 | TRUE
IM765506 | 3126DE | 0121_S_DK-HAGYZEYA_3126DE | main power/Stolen batteries/handel SK-SAWALEH_3338DE,SK-TELRAK_0798DE,TAMEY-AMDID_0347D | batt | Batteries | batt | Batteries | 355992 | DK-HAGYZEYA | C6-3126DE-PH12 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-12 12:38 | 2019-08-07 | TRUE
IM765531 | 0050DE | 0001_S_GH-SHABSHR-HAS_0050DE | Main power / batteries under check / connected PG | batt | Batteries | batt | Batteries | 304298 | GH-SHABSHR-HAS | C1_0050DE_PH1 | (Batteries/Some parts are missing/cover) | 2019-09-12 13:00 | 2019-02-23 | TRUE
IM765543 | 3368DE | 0201_S_BH-ABO-SHIQAF_3368DE | Access VF / Main power / stolen batteries | batt | Batteries | batt | Batteries | 324904 | BH-ABO-SHIQAF | C1_3368DE_PH12 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-12 13:09 | 2019-04-17 | TRUE
IM765544 | 3590DE | 1631_S_BH-HADIN_3590DE | GN problem / stolen batteries / connected PG | batt GN | Batteries Generator | batt GN | Batteries Generator | 324439 | BH-HADIN | C2_3590DE_PH13 | (Batteries/Item(s) stolen/There is no battery for site) (ATS / Engine/Components faulty/Check small generator operation (There is no battery for site)) | 2019-09-12 13:17 | 2019-03-07 | TRUE
IM765605 | 3151UP | 1561_S_BS-QIMAN-AROS_3151UP | Due to EC power cutoff , weak batteries , PG Connected | batt | Batteries | batt | Batteries | 355911 | 01_S_BS-QIMAN-AROS_3151UP | C2_3151UP_PH13 | (Rectifiers/Alarms reporting to the OMC/Loop on the minor alarm in DDF (Port 6)) (Rectifiers/Alarms reporting to the OMC/The power alarm is faulty (Always active on the rectifier and OMC)) | 2019-09-12 14:31 | 2019-07-28 | TRUE
IM765621 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Due to Generator problem , weak batteries , Recovered | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | (ATS / Engine/Components faulty/Gen battery was defected) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM organization/ATS Cables not organized) | 2019-09-12 15:01 | 2019-05-18 | TRUE
IM765626 | 0673CA | 02654_S_0673CA_ASMA-FAHMY | down due to main power & weak batteries at 0673CA_ASMA-FAHMY (T) | batt | Batteries | batt | Batteries | 356212 | ASMA-FAHMY | C1_0673CA_PH8 | (Batteries/Some parts are (missing / stolen)/missing batteries) | 2019-09-12 15:08 | 2019-08-19 | TRUE
IM765658 | 0038RE | 00210_C_0038RE_3P-SZ-RAS-ABU-DRAJ | DG Stopped , dead batteries , once team arrive and fix DG Site recovered | batt DG | Batteries Generator | DG | Generator | 304375 | SZ-RAS-ABU-DRAJ | C3_0038RE_PH2 | (ATS / Engine/Components faulty/missing battery ) (ATS / Engine/Wrong connection/welded cables ) (ATS / Engine/Wrong connection/wrong connection & jumper on the contactor) (ATS / Engine/Wrong connection/cable not isolated ) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/cables not terminated ) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage ) | 2019-09-12 16:00 | 2019-02-24 | TRUE
IM765668 | 3089UP | 2141_S_SG-GALAWEYA_3089UP | Main power disconnection ,batteries stolen , Power meter out of Charge , Escalated , our team in site to Connect PG and waiting Guard more than 45min , VF team solved power meter also , recovered . | batt | Batteries | batt | Batteries | 356371 | 01_S_SG-GALAWEYA_3089UP | C1_3089UP_PH13 | (Batteries/Some parts are (missing / stolen)/site batteries were Stolen) | 2019-09-12 16:05 | 2019-09-18 | FALSE
IM765683 | 0427DE | 0061_D_SK-EZBA-SARYA_0427DE | GN problem/no battery/team on way | batt GN | Batteries Generator | batt GN | Batteries Generator | 345382 | SK-EZBA-SARYA | C2_0427DE_PH4 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) (ATS / Engine/Components faulty/Exhaust fan not working and another not exist) | 2019-09-12 16:08 | 2019-06-16 | TRUE
IM765693 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Share VF / Main power / Stolen batteries | batt | Batteries | batt | Batteries | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | (Batteries/Item(s) stolen/Stolen) | 2019-09-12 16:17 | 2019-03-25 | TRUE
IM765715 | 0490SI | 03534_S_0490SI_IS-NASR | Outage power in area located site , dead batteries , once team arrive to connect PG power restored and site recovered | batt | Batteries | batt | Batteries | 356007 | 01_S_IS-NASR_0490SI | C2_0490SI_PH14 | (Rectifiers/Alarms reporting to the OMC/Rectifier alarm , A/C & door not apear on CAP) (Batteries/Components faulty/Battery voltag reading drop to 46 volt after we disconnect th rectifier C.B (Check the batteries)) | 2019-09-12 17:46 | 2019-08-07 | TRUE
IM765728 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN problem/Stolen batteries/clear after check GN | batt GN | Batteries Generator | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | (ATS / Engine/Wrong connection/Welding cables) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot) | 2019-09-12 17:44 | 2019-06-16 | TRUE
IM765742 | 3620DE | 0631_S_QL-BATIMDA_3620DE | access Guard/Guard switch MCB OFF finencial problem/Stolen batteries@QL-BATMIDA_3620DE | batt | Batteries | batt | Batteries | 356052 | QL-BATIMDA | C02_3620DE_PH13 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) | 2019-09-12 19:48 | 2019-08-18 | TRUE
IM765774 | 0734DE | 0441_D_MF-TANTA-HW1_0734DE | GN problem / solar theft case / stolen batteries / PG connected | batt GN | Batteries Generator | batt GN | Batteries Generator | 356142 | MF-TANTA-HW1 | C1_0734DE_PH9 | (Rectifiers/Alarms reporting to the OMC/Site has fake power alarm) (Batteries/Some parts are (missing / stolen)/There is no battery for site) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has leakage) | 2019-09-12 22:04 | 2019-08-27 | TRUE
IM765780 | 0711DE | 0701_S_GH-GOMHORIYAH_0711DE | Access TE " access blocked " / H.T alarm / hanging BTS | H.T | A/Cs | H.T | A/Cs | 335126 | GH-GOMHORIYAH | C2_0711DE_PH09 | (A/Cs Cooling / Free Cooling / Ventilation/Components faulty/Faulty ) (A/Cs Cooling / Free Cooling / Ventilation/Wrong connection/terminals in one slot) | 2019-09-12 19:18 | 2019-05-14 | TRUE
IM765788 | 0485DE | K_MF-BARAHIM_21106_1 | Main power /Batteries under investigation@BARAHIM_0485DE/clear after power back | batt | Batteries | batt | Batteries | 304303 | MF-BARAHIM | C5_0485DE_PH7 | (Batteries/Some parts are missing/Battery without covers) | 2019-09-12 23:24 | 2019-02-21 | TRUE
IM765858 | 3798DE | 1471_S_SK-MNZL-MYMON_3798DE | power crises/Main power/Stolen batteries@MNZL-MYMON_3798DE/handel nodal sites AWLAD-MUSA,,Fadadna | batt | Batteries | batt | Batteries | 355763 | SK-MNZL-MYMON | C2-3798DE-PH14 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-13 05:28 | 2019-07-10 | TRUE
IM765863 | 3823DE | 1121_G_SK-DAHTAMON_3823DE | power crises/Main power/Stolen batteries/handel nodal sites AWLAD-MUSA,,Fadadna | batt | Batteries | batt | Batteries | 303844 | SK-DAHTAMON | C1_3823DE_PH14 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-13 05:31 | 2019-01-16 | TRUE
IM765865 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to dynamo problem and site has weak backup batteries | backup batt Gen generator | Batteries Batteries Generator Generator | backup batt Gen generator | Batteries Generator | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | (Batteries/Item(s) stolen/One of batteries string was stolen) (ATS / Engine/Components faulty/Gen battery is defected) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Gen battery cables not isolated well) (ATS / Engine/Panorama pictures for each system/Open gland in Gen enclosure need insulation) (ATS / Engine/Panorama pictures for each system/Panorama site view in outside site) (ATS / Engine/Panorama pictures for each system/Last Gen hour meter at Auidt G ( 661 )) | 2019-09-13 06:48 | 2019-05-02 | TRUE
IM765870 | 3245CA | 01973_S_3245CA_10th-RSD-6 | EC power outage / weak batteries / cleared on PG till E power restored | batt | Batteries | batt | Batteries | 356443 | 10TH-RSD-6 | C4_3245CA_PH11 | (Batteries/Some parts are (missing / stolen)/Battery string stolen) | 2019-09-13 07:20 | 2019-10-02 | FALSE
IM765873 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG Stoppage / weak batteries /radiator problem / cleared after power restored | batt DG | Batteries Generator | batt DG | Batteries Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | (Batteries/Some parts are (missing / stolen)/Battery string stolen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage) (ATS / Engine/Components faulty/Generator battery defected) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure ) (ATS / Engine/Wrong connection/generator battery as used in the site and not suitable in High temp) | 2019-09-13 07:39 | 2019-07-01 | TRUE
IM765923 | 3009AL | 03232_D_3009AL_MM-ALMN-APT2 | VF guard access problem/ GN problem/ weak batteries/ restored after solve GN problem | batt GN | Batteries Generator | GN | Generator | 324992 | MM-ALMN-APT2 | C1_3009AL_PH19 | (ATS / Engine/Components faulty/Burned generator need to be replaced.) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Vodafone gen has leakage.) | 2019-09-13 09:43 | 2019-05-01 | TRUE
IM765938 | 0490SI | 03534_S_0490SI_IS-NASR | EC power outage /weak batteries / cleared after power restored | batt | Batteries | batt | Batteries | 356007 | 01_S_IS-NASR_0490SI | C2_0490SI_PH14 | (Rectifiers/Alarms reporting to the OMC/Rectifier alarm , A/C & door not apear on CAP) (Batteries/Components faulty/Battery voltag reading drop to 46 volt after we disconnect th rectifier C.B (Check the batteries)) | 2019-09-13 09:35 | 2019-08-07 | TRUE
IM765970 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to Deliberately Switched Off & stolen batteries (T) | batt | Batteries | batt | Batteries | 314391 | REHAB-G17 | C1_3492CA_PH13 | (Batteries/Some parts are missing/missing batteries) | 2019-09-13 11:59 | 2019-02-26 | TRUE
IM765987 | 3333DE | 0181_S_BH-OM-SABER_3333DE | Main power/week battery/clear after power back | batt | Batteries | batt | Batteries | 304089 | BH-OM-SABER_SSS0 | C1_3333DE_PH12 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-13 12:07 | 2019-01-30 | TRUE
IM765989 | 3299DE | 0541_S_KS-ZAAFRAN_3299DE | Main power / Weak batteries / VF Share / BDT @ 16/03/2019 Is: 1.00 | batt | Batteries | batt | Batteries | 355873 | KS-ZAAFRAN | C1_3299DE_PH12 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) | 2019-09-13 12:53 | 2019-07-22 | TRUE
IM766047 | 3126DE | 0121_S_DK-HAGYZEYA_3126DE | main power/Stolen batteries/handel SK-SAWALEH_3338DE,SK-TELRAK_0798DE,TAMEY-AMDID_0347D | batt | Batteries | batt | Batteries | 355992 | DK-HAGYZEYA | C6-3126DE-PH12 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-13 14:53 | 2019-08-07 | TRUE
IM766078 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to DG Fuel Pump problem & stolen batteries (T) | batt DG | Batteries Generator | batt DG | Batteries Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | (Batteries/Some parts are missing/missing batteries) (ATS / Engine/Wrong connection/wrong connection) | 2019-09-13 16:26 | 2019-02-26 | TRUE
IM766086 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG stoppage / weak batteries / cleared after power restored | batt DG | Batteries Generator | batt DG | Batteries Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | (Batteries/Some parts are (missing / stolen)/Battery string stolen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage) (ATS / Engine/Components faulty/Generator battery defected) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure ) (ATS / Engine/Wrong connection/generator battery as used in the site and not suitable in High temp) | 2019-09-13 17:25 | 2019-07-01 | TRUE
IM766091 | 0324UP | 1421_S_MN-BARTABAT_0324UP | Commercial power cut off and site has stolen backup batteries, recovered | backup batt | Batteries Batteries | backup batt | Batteries | 324919 | 01_S_MN-BARTABAT_0324UP | C1_0324UP_PH8 | (Batteries/Item(s) stolen/Site batteries were stolen) | 2019-09-13 18:31 | 2019-04-20 | TRUE
IM766155 | 0882DE | 1091_D_GH-MHLA-BHR-ST_0882DE | GN problem @ GH-MHLA-BHR-ST_0882DE / batteries under check | batt GN | Batteries Generator | GN | Generator | 324934 | GH-MHLA-BHR-ST | C6_0882DE_PH09 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check, clean) | 2019-09-13 23:01 | 2019-04-24 | TRUE
IM766161 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problrm/stolen batteries/clear after check GN | batt GN | Batteries Generator | batt GN | Batteries Generator | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | (Batteries/Some parts are missing/Battery cabinet need cleaning (from inside) and holes need sealing.) (Batteries/Some parts are missing/Batteries poles need have missing covers.) (ATS / Engine/Components faulty/Generator has bad performance and need overall.) (ATS / Engine/Panorama pictures for each system/Overview.) | 2019-09-14 00:03 | 2019-05-21 | TRUE
IM766179 | 0882DE | 1091_D_GH-MHLA-BHR-ST_0882DE | GN problem @ GH-MHLA-BHR-ST_0882DE / batteries under check / connect PG / lock 2G | batt GN | Batteries Generator | GN | Generator | 324934 | GH-MHLA-BHR-ST | C6_0882DE_PH09 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check, clean) | 2019-09-14 02:10 | 2019-04-24 | TRUE
IM766181 | 0914CA | 00138_L_0914CA_MAADI-TABARK | down due to DG LOP and stolen batt. (I) | batt DG | Batteries Generator | batt | Batteries | 345257 | MAADI-TABARK | C1_0914CA_PH09 | (Batteries/Some parts are missing/missing batteries) | 2019-09-14 03:49 | 2019-05-25 | TRUE
IM766186 | 0303AL | 0451_N_WARDIAN-EST_0303AL | High Temperature Problem / Problem Solved after solving A/Cs Problem and reset BTS | A/Cs | A/Cs | A/Cs | A/Cs | 355916 | N_WARDIAN-EST_0303AL | C1_0303AL_PH4 | (A/Cs Cooling / Free Cooling / Ventilation/Components faulty/Battery cabinet A/C isn't working and its control board need check.) (A/Cs Cooling / Free Cooling / Ventilation/Components faulty/A/C1 isn't working and its CB tripped off.) | 2019-09-14 02:14 | 2019-07-29 | TRUE
IM766210 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG stoppage / weak batteries / cleared after power restored | batt DG | Batteries Generator | batt DG | Batteries Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | (Batteries/Some parts are (missing / stolen)/Battery string stolen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage) (ATS / Engine/Components faulty/Generator battery defected) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure ) (ATS / Engine/Wrong connection/generator battery as used in the site and not suitable in High temp) | 2019-09-13 22:47 | 2019-07-01 | TRUE
IM766211 | 0223UP | 0261_C_SG-DIER-NAYASSA_0223UP | Due to Generator problem due to LOP alarm, weak batteries , Recovered | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 324451 | 01_G_SG-DIER-NAYASSA_0223UP | C1_0223UP_PH5 | (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Battery cables to be isolated well) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM organization/ATS cables notorgnized and unused cable not isolated) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Missing terminals inside ATS) (ATS / Engine/Item(s) stolen/Gen battery is missing) (ATS / Engine/Panorama pictures for each system/Panorama) | 2019-09-14 06:19 | 2019-03-09 | TRUE
IM766212 | 3778UP | 1291_S_AS-SABIL_3778UP_X | Main power disconnection and SCG isn't worked, Stolen batteries ,SCG did not work due to Fueling Problem , P.G connected | batt | Batteries | batt | Batteries | 356225 | 01_S_AS-SABIL_3778UP | C1_3778UP_PH15 | (Batteries/Some parts are (missing / stolen)/Batteries were stolen) | 2019-09-14 06:29 | 2019-09-04 | TRUE
IM766228 | 3514DE | 1901_S_DK-KFR-GHENINA_3514DE | Main power @ DK-KFR-GHENINA_3514DE / weak batteries | batt | Batteries | batt | Batteries | 324923 | DK-KFR-GHENINA | C3_3514DE_PH13 | (Batteries/Item(s) stolen/stolen Batteries) | 2019-09-14 06:16 | 2019-04-22 | TRUE
IM766229 | 3514DE | 1901_S_DK-KFR-GHENINA_3514DE | Main power @ DK-KFR-GHENINA_3514DE / weak batteries | batt | Batteries | batt | Batteries | 324923 | DK-KFR-GHENINA | C3_3514DE_PH13 | (Batteries/Item(s) stolen/stolen Batteries) | 2019-09-14 06:16 | 2019-04-22 | TRUE
IM766241 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem and access VF problem & stolen batt. (I) | batt DG | Batteries Generator | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | (Batteries/Some parts are (missing / stolen)/missing battereis) | 2019-09-14 06:56 | 2019-08-14 | TRUE
IM766253 | 3455UP | 0921_S_QN-ELNUGOU_3455UP | Main power disconnection ,batteries are suspected to be weak , P.G connected | batt | Batteries | batt | Batteries | 355996 | 01_S_QN-ELNUGOU_3455UP | C1_3455UP_PH14 | (Rectifiers/Alarms reporting to the OMC/Alarm was exists on rectifier control panel and appeared on the Omc to be cleared) (Batteries/Some parts are (missing / stolen)/Missing batteries poles covers) | 2019-09-14 07:38 | 2019-08-06 | TRUE
IM766256 | 3812UP | 0631_E_SG-MNSHAH2_3812UP | Main power disconnection ,batteries are suspected to be weak, Autorecovered. | batt | Batteries | batt | Batteries | 355794 | 01_G_QN-MHAMID-QBLY_3807UP | C1_3807UP_PH15 | (Rectifiers/Alarms reporting to the OMC/Rectifier minor alarm was looped at ddf) | 2019-09-14 07:02 | 2019-07-14 | TRUE
IM766270 | 3712DE | 0221_G_BH-QAMHA_3712DE | Main power problem @ BH-QAMHA_3712DE / SC GN problem | GN | Generator | GN | Generator | 304258 | BH-QAMHA | C1_3712DE_PH14 | (ATS / Engine/Components faulty/Small generator not working // Site has history generator status alarm) | 2019-09-14 08:18 | 2019-02-19 | TRUE
IM766273 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN problem/stolen battery@Mit Gaber/clear after GN working | batt GN | Batteries Generator | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | (ATS / Engine/Wrong connection/Welding cables) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot) | 2019-09-14 07:28 | 2019-06-16 | TRUE
IM766281 | 3245CA | 01973_S_3245CA_10th-RSD-6 | EC power outage / weak batteries / cleared after power restored | batt | Batteries | batt | Batteries | 356443 | 10TH-RSD-6 | C4_3245CA_PH11 | (Batteries/Some parts are (missing / stolen)/Battery string stolen) | 2019-09-14 08:35 | 2019-10-02 | FALSE
IM766330 | 4251DE | 03304_S_4251DE_QL-ABU-GHIT2 | main power/stolen batteries /clear after power back | batt | Batteries | batt | Batteries | 355722 | QL-ABU-GHIT2 | C1_4251DE_PH17 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) | 2019-09-14 09:56 | 2019-07-04 | TRUE
IM766373 | 3895DE | 0401_S_BH-KFR-ZYADA_3895DE | Share VF / VF GN problem / stolen batteries / then BTS problem / SM problem faulty / RP3 alarm | batt GN | Batteries Generator | batt | Batteries | 324442 | BH-KFR-ZYADA | C1_3895DE_PH14 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-14 09:45 | 2019-03-07 | TRUE
IM766394 | 3319CA | 01131_S_3319CA_IMBABA-4 | down due to power failure and dead batteries (M) | batt | Batteries | batt | Batteries | 355486 | IMBABA-4 | C2_3319CA_PH12 | (Rectifiers/Alarms reporting to the OMC/Rectifier alarms don't appear on the OMC) (Rectifiers/Alarms reporting to the OMC/Rectifier alarms don't appear on the OMC (battery fuse alarm)) | 2019-09-14 11:42 | 2019-06-26 | TRUE
IM766404 | 3489DE | 0461_S_DK-KFR-GHANNAM_3489DE | main power/stolen batteries /clear after power back | batt | Batteries | batt | Batteries | 325088 | DK-KFR-GHANNAM | C1-3489DE-PH13 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-14 10:23 | 2019-05-09 | TRUE
IM766406 | 0370UP | 1961_G_CAIRO-ASWAN-12_0370UP | Main power disconnection , stolen batteries , recovered | batt | Batteries | batt | Batteries | 304136 | 01_G_CAIRO-ASWAN-12_0370UP | C2_0370UP_PH8 | (Batteries/Item(s) stolen/ Batteries were stolen) | 2019-09-14 12:24 | 2019-02-07 | TRUE
IM766425 | 0801DE | 0351_G_DK-BARHANTOSH_0801DE | main power/Stolen batteries @BARHANTOSH_0801DE/clear on P.G,cant carry full loads | batt | Batteries | batt | Batteries | 325114 | DK-BARHANTOSH | C1_0801DE_PH9 | (Rectifiers/Alarms reporting to the OMC/Site has old power alarm) (Batteries/Some parts are (missing / stolen)/Battery string stolen) (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-14 11:33 | 2019-05-14 | TRUE
IM766433 | 3090UP | 2131_S_SG-FAZARA_3090UP | Due to H.T alarm , recovered | H.T | A/Cs | H.T | A/Cs | 356038 | 01_S_SG-FAZARA_3090UP | C2_3090UP_PH13 | (A/Cs Cooling / Free Cooling / Ventilation/Components faulty/2 A/c's not functioning) | 2019-09-14 12:34 | 2019-08-06 | TRUE
IM766434 | 3759UP | 0951_S_AT-AWLD-IBRHIM_3759UP | Commercial power cut off and site has weak backup batteries, recovered | backup batt | Batteries Batteries | backup batt | Batteries | 356232 | 01_S_AT-AWLD-IBRHIM_3759UP | C1_3759UP_PH15 | (Batteries/Some parts are (missing / stolen)/site batteries were stolen) | 2019-09-14 12:36 | 2019-09-05 | TRUE
IM766460 | 3290DE | 1171_D_MF-QATTA_3290DE | GN problem/batteries under investigation/clear on P.G | batt GN | Batteries Generator | GN | Generator | 355961 | MF-QATTA | C3_3290DE_PH12 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has leakage) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminals requried) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Cable need to be terminated well) | 2019-09-14 11:51 | 2019-08-03 | TRUE
IM766462 | 0595DE | 0281_G_DK-NISHA_0595DE | Main power / weak batteries | batt | Batteries | batt | Batteries | 324924 | DK-NISHAA | C1_0595DE_PH9 | (Batteries/Some parts are missing/cover) | 2019-09-14 12:11 | 2019-04-22 | TRUE
IM766467 | 3953DE | 0361_G_BH-MAARKA_3953DE | informed TT only @14:32//access ET/Main power/Stolen batteries | batt | Batteries | batt | Batteries | 304235 | BH-MAARKA | C1_3953DE_PH15 | (Batteries/Components faulty/Faulty battery and cable disconnected) | 2019-09-14 12:21 | 2019-02-14 | TRUE
IM766487 | 3318UP | 01_S_SG-TAL-ELZOKI_3318UP | Commercial power cut off and site has stolen backup batteries | backup batt | Batteries Batteries | backup batt | Batteries | 356366 | 01_O_SG-RYAYNA-HAGR_3744UP | C1_3744UP_PH16 | (Batteries/Item(s) stolen/site batteries were stolen) (Batteries/Some parts are (missing / stolen)/Site batteries were Stolen) | 2019-09-14 14:37 | 2019-09-18 | FALSE
IM766502 | 0962CA | 02148_S_0962CA_OM-BAYOMI-STH | down due to main power & weak batteries | batt | Batteries | batt | Batteries | 345370 | OM-BAYOMI-STH | C1_0962CA_PH9 | (Rectifiers/Alarms reporting to the OMC/Minor (high battery temp.) and major (faulty modules) alarms appear on the rectifier) (Batteries/Some parts are (missing / stolen)/Stolen batteries) | 2019-09-14 14:25 | 2019-06-18 | TRUE
IM766543 | 0882DE | 1091_D_GH-MHLA-BHR-ST_0882DE | GN problem @ GH-MHLA-BHR-ST_0882DE / batteries under check / connect PG / lock 2G | batt GN | Batteries Generator | GN | Generator | 324934 | GH-MHLA-BHR-ST | C6_0882DE_PH09 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check, clean) | 2019-09-14 15:00 | 2019-04-24 | TRUE
IM766585 | 0517DE | 1541_G_QL-TUKH-TRAIN_0517DE | Main power/week battery/clear after power back | batt | Batteries | batt | Batteries | 303890 | QL-TUKH-TRAIN BSC | C1_0517DE_PH8 | (Batteries/Item(s) stolen/stolen batteries) | 2019-09-14 19:03 | 2019-01-19 | TRUE
IM766608 | 0801DE | 0351_G_DK-BARHANTOSH_0801DE | Main power/stolen battery @ DK-BARHANTOSH/clear on P.G,can't carry full loads | batt | Batteries | batt | Batteries | 325114 | DK-BARHANTOSH | C1_0801DE_PH9 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-14 20:29 | 2019-05-14 | TRUE
IM766651 | 3438DE | 0411_S_DK-ABU-HUSEIN_3438DE | main power/Stolen batteries clear after power back | batt | Batteries | batt | Batteries | 325116 | DK-ABU-HUSEIN | C2-3438DE-PH13 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-14 23:27 | 2019-05-14 | TRUE
IM766676 | 3866DE | 2001_D_DK-SANBAKHT_3866DE | GN problem / stolen batteries | batt GN | Batteries Generator | GN | Generator | 304185 | DK-SANBAKHT | C3_3866DE_PH14 | (ATS / Engine/Components faulty/screen need repair) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/protect by tray ) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/protect) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check oil leakage ) | 2019-09-14 18:44 | 2019-02-07 | TRUE
IM766685 | 0608UP | 1071_D_MN-BANI-ROH_0608UP | Generator stopped due to radiator problem and site has weak backup batteries Site has guard access problem at night | backup batt Gen generator | Batteries Batteries Generator Generator | Gen generator | Generator | 356181 | 01_G_MN-BANI-ROH_0608UP | C1_0608UP_PH9 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage) (ATS / Engine/Components faulty/faulty battery) (ATS / Engine/Components faulty/need battery) (ATS / Engine/Wrong connection/remove wrong connection) | 2019-09-15 02:22 | 2019-08-28 | TRUE
IM766699 | 0180AL | 1081_S_WARDIAN_0180AL | Site Down After HT Alarm / No Access Refer To Soc Team / On Air After Solving HT Alarm | HT | A/Cs | HT | A/Cs | 324862 | S_WARDIAN_0180AL | C1_0180AL_PH3 | (A/Cs Cooling / Free Cooling / Ventilation/Components faulty/a/C1 has faulty IDU and isn't working.) | 2019-09-15 04:26 | 2019-04-16 | TRUE
IM766765 | 0638UP | 0491_G_QN-MOSALA_0638UP | Rented generator problem , Stolen batteries ; recovered after solving the generator problem | batt Gen generator | Batteries Generator Generator | batt Gen generator | Batteries Generator | 324745 | 01_G_QN-MOSALA_0638UP | C4_0638UP_PH9 | (Batteries/Item(s) stolen/Batteries were stolen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage beside enclosure by Vodafone ) | 2019-09-15 08:01 | 2019-04-04 | TRUE
IM766848 | 3495DE | 0181_S_SK-MAHDIYA_3495DE | Main power/ stolen battery/connect PG | batt | Batteries | batt | Batteries | 304144 | SK-MAHDIYA | C3_3495DE_PH13 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-15 09:30 | 2019-02-09 | TRUE
IM766863 | 3151UP | 1561_S_BS-QIMAN-AROS_3151UP | Commercial power cut off and site has weak backup batteries, PG connected | backup batt | Batteries Batteries | backup batt | Batteries | 355911 | 01_S_BS-QIMAN-AROS_3151UP | C2_3151UP_PH13 | (Rectifiers/Alarms reporting to the OMC/Loop on the minor alarm in DDF (Port 6)) (Rectifiers/Alarms reporting to the OMC/The power alarm is faulty (Always active on the rectifier and OMC)) | 2019-09-15 09:44 | 2019-07-28 | TRUE
IM766908 | 3275DE | 1151_S_QL-DEER-2_3275DE | main power @DEER-2_3275DE /weak battery/connect PG | batt | Batteries | batt | Batteries | 356318 | QL-DEER-2 | C1_3275DE_PH12 | (Rectifiers/Alarms reporting to the OMC/Alarm cable disconnected (Alarms not appear at OMC)) (Batteries/Components faulty/Faulty battaries) | 2019-09-15 10:27 | 2019-09-15 | TRUE
IM766924 | 3126DE | 0121_S_DK-HAGYZEYA_3126DE | main power/stolen batt/connect PG, | batt | Batteries | batt | Batteries | 355992 | DK-HAGYZEYA | C6-3126DE-PH12 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-15 09:52 | 2019-08-07 | TRUE
IM766925 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Main power / VF Share / Stolen batteries | batt | Batteries | batt | Batteries | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | (Batteries/Item(s) stolen/Stolen) | 2019-09-15 10:00 | 2019-03-25 | TRUE
IM766941 | 3445UP | 591_D_MN-TOKH_3445UP | Generator stopped due to LOP alarm and site has weak backup batteries | backup batt Gen generator | Batteries Batteries Generator Generator | Gen generator | Generator | 356182 | 01_G_MN-TOKH_3445UP | C1_3445UP_PH14 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage) (ATS / Engine/Components faulty/need battery) | 2019-09-15 11:18 | 2019-08-28 | TRUE
IM766944 | 3275DE | 1151_S_QL-DEER-2_3275DE | main power @DEER-2_3275DE /weak battery/connect PG | batt | Batteries | batt | Batteries | 356318 | QL-DEER-2 | C1_3275DE_PH12 | (Rectifiers/Alarms reporting to the OMC/Alarm cable disconnected (Alarms not appear at OMC)) (Batteries/Components faulty/Faulty battaries) | 2019-09-15 10:47 | 2019-09-15 | TRUE
IM766963 | 3385DE | 0671_S_BH-GHAZALA-VLG_3385DE | Main power / Batteries need check | batt | Batteries | batt | Batteries | 355780 | BH-GHAZALA-VLG | C2_3385DE_PH13 | (Rectifiers/Alarms reporting to the OMC/Site down due to power (Check alarms with OMC)) | 2019-09-15 11:14 | 2019-07-11 | TRUE
IM766978 | 0280DE | 0601_Q_BH-KOMHMADA-NTH_0280DE | GN problem @ BH-KOMHMADA-NTH_0280DE / Stolen batteries | batt GN | Batteries Generator | batt GN | Batteries Generator | 355878 | BH-KOMHMDA-NTH | C6_0280DE_PH3 | (Batteries/Some parts are (missing / stolen)/Stolen ) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Leakage) (ATS / Engine/Unit earth/Disconnected) | 2019-09-15 11:33 | 2019-07-21 | TRUE
IM767038 | 3272UP | 0791_G_QN-QENWYA-BHRY_3272UP | Main power disconnection , Weak batteries , P.G Connected | batt | Batteries | batt | Batteries | 355823 | 01_G_QN-QENWYA-BHRY_3272UP | C2_3272UP_PH14 | (Batteries/Some parts are (missing / stolen)/Some of Batteries were stolen) | 2019-09-15 12:10 | 2019-07-16 | TRUE
IM767058 | 0430AL | 00658_D_0430AL_TAMIR-EXIT | Generator problem/engine overhauling/Weak batteries/Connected PG/solved/Site restored | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 356072 | Tamir Exit | C2_0430AL_PH9 | (ATS / Engine/Unit earth/Disconnect generator earth.) (ATS / Engine/Components faulty/GCM Module need replacement.) (ATS / Engine/Wrong connection/Generator has bad condition and need overall.) | 2019-09-15 12:52 | 2019-08-20 | TRUE
IM767070 | 0983DE | 1771_S_DK-MIT-ANTAR_0983DE | Main power / Stolen batteries | batt | Batteries | batt | Batteries | 324896 | DK-MIT-ANTAR | C8_0983DE_PH11 | (Batteries/Item(s) stolen/stolen batteries) | 2019-09-15 12:46 | 2019-04-14 | TRUE
IM767078 | 3046UP | 0551_D_AT-BANI-FEEZ_3046UP | Generator stopped due to radiator problem and site has stolen backup batteries | backup batt Gen generator | Batteries Batteries Generator Generator | backup batt Gen generator | Batteries Generator | 303971 | 01_G_AT-BANI-FEEZ_3046UP | C4_3046UP_PH13 | (Batteries/Item(s) stolen/Site batteries were stolen) (ATS / Engine/Components faulty/Site need new battery) (ATS / Engine/Components faulty/Control panel button not working) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Power cables not protected and missing power gland) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM organization/Power cable not organized) (ATS / Engine/Panorama pictures for each system/Panorama) | 2019-09-15 13:07 | 2019-01-20 | TRUE
IM767152 | 3089UP | 2141_S_SG-GALAWEYA_3089UP | Main power disconnection , Stolen batteries , P.G Connected | batt | Batteries | batt | Batteries | 356371 | 01_S_SG-GALAWEYA_3089UP | C1_3089UP_PH13 | (Batteries/Some parts are (missing / stolen)/site batteries were Stolen) | 2019-09-15 13:21 | 2019-09-18 | FALSE
IM767195 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN prob@SK-MIT-GABIR_3833DE/stolen battery/tGNerator work | batt GN | Batteries Generator | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | (ATS / Engine/Wrong connection/Welding cables) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot) | 2019-09-15 14:01 | 2019-06-16 | TRUE
IM767197 | 0390UP | D_DAR-FOUAD_4712_S6_G | site cascade on site DAR-FOUAD and DAR-FOUAD down H.T and solved after fix A/C (MA) | A/C H.T | A/Cs A/Cs | A/C H.T | A/Cs | 356338 | DAR-FOUAD | C3_0390UP_PH8 | (A/Cs Cooling / Free Cooling / Ventilation/Some parts are (missing / stolen)/cover) | 2019-09-15 14:52 | 2019-09-19 | FALSE
IM767202 | 3245CA | 01973_S_3245CA_10th-RSD-6 | EC power outage /weak batteries / cleared after power restored | batt | Batteries | batt | Batteries | 356443 | 10TH-RSD-6 | C4_3245CA_PH11 | (Batteries/Some parts are (missing / stolen)/Battery string stolen) | 2019-09-15 14:58 | 2019-10-02 | FALSE
IM767238 | 0022SI | 03519_H_0022SI_IS-ABU-ATWA | EC power outage /stolen batteries / cleared after power restored | batt | Batteries | batt | Batteries | 325082 | 01_H_IS-ABU-ATWA_0022SI | C8_0022SI_PH1 | (Batteries/Item(s) stolen/Battery string stolen) | 2019-09-15 15:52 | 2019-05-04 | TRUE
IM767246 | 0711DE | 0701_S_GH-GOMHORIYAH_0711DE | Access TE / H.T alarm / BTS hanged | H.T | A/Cs | H.T | A/Cs | 335126 | GH-GOMHORIYAH | C2_0711DE_PH09 | (A/Cs Cooling / Free Cooling / Ventilation/Components faulty/Faulty ) (A/Cs Cooling / Free Cooling / Ventilation/Wrong connection/terminals in one slot) | 2019-09-15 14:54 | 2019-05-14 | TRUE
IM767302 | 3894CA | 02231_S_3894CA_REHAB-STAGE7 | down due to VF DG problem and stolen batteries and access VF problem (M) | batt DG | Batteries Generator | batt | Batteries | 356204 | REHAB-STAGE7 | C1_3894CA_PH17 | (Batteries/Some parts are (missing / stolen)/missing batteries) | 2019-09-15 17:52 | 2019-08-14 | TRUE
IM767330 | 3495DE | 0181_S_SK-MAHDIYA_3495DE | VF/main power/stolen battery/ PG (has problem will solved) | batt | Batteries | batt | Batteries | 304144 | SK-MAHDIYA | C3_3495DE_PH13 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-15 18:47 | 2019-02-09 | TRUE
IM767367 | 3495DE | 0181_S_SK-MAHDIYA_3495DE | access VF/VF PM need charge /Main power/Stolen batteries/clear after power back | batt | Batteries | batt | Batteries | 304144 | SK-MAHDIYA | C3_3495DE_PH13 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-15 19:45 | 2019-02-09 | TRUE
IM767381 | 0222RE | 03824_G_0222RE_RS-FLAMNCO-HTL | Site was down due to Gen Stoppage / stolen batteries / fuel theft case / cleared after refueled | batt Gen | Batteries Generator | Gen | Generator | 355690 | 01_G_RS-FLAMNCO-HTL_0222RE | C1_0222RE_PH09 | (ATS / Engine/Components faulty/need battery) | 2019-09-15 21:54 | 2019-01-20 | TRUE
IM767506 | 0028RE | 03477_N_0028RE_SZ-SUEZ8 | EC power outage / weak batteries / access PG problem / cleared after power restored | batt | Batteries | batt | Batteries | 345369 | 01_N_SZ-SUEZ8_0028RE | C2_0028RE_PH1 | (Batteries/Some parts are (missing / stolen)/Stolen battery string) | 2019-09-16 07:30 | 2019-06-17 | TRUE
IM767594 | 3955DE | 0731_S_SK-QRMT-SAHBRA_3955DE | Main power/stolen battery/clear after power back | batt | Batteries | batt | Batteries | 356230 | SK-QRMT-SAHBRA | C1_3955DE_PH15 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-16 09:14 | 2019-09-07 | TRUE
IM767647 | 3628DE | 0811_S_GH-QSR-BAGHDAD_3628DE | Main power / stolen batteries / PG connected | batt | Batteries | batt | Batteries | 324836 | GH-QSR-BAGHDAD | C2_3628DE_PH13 | (Batteries/Item(s) stolen/Stolen batteries) | 2019-09-16 09:50 | 2019-04-15 | TRUE
IM767648 | 0498RE | 03500_S_0498RE_SZ-SELIM-HAY | EC power outage / weak batteries / access PG problem / VF owner / cleared after power restored | batt | Batteries | batt | Batteries | 345366 | 01_S_SZ-SELIM-HAY_0498RE | C1_0498RE_PH17 | (Batteries/Some parts are (missing / stolen)/Stolen battery) | 2019-09-16 10:23 | 2019-06-17 | TRUE
IM767754 | 3361DE | 0441_S_KS-HAMUL-EST_3361DE | Share VF / Main power / stolen batteries | batt | Batteries | batt | Batteries | 355874 | KS-HAMUL-EST | C1_3361DE_PH12 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) | 2019-09-16 10:54 | 2019-07-22 | TRUE
IM767787 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Share VF / main power / stolen batteries | batt | Batteries | batt | Batteries | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | (Batteries/Item(s) stolen/Stolen) | 2019-09-16 11:20 | 2019-03-25 | TRUE
IM767789 | 0050DE | 0001_S_GH-SHABSHR-HAS_0050DE | Main power @ GH-SHABSHR-HAS_0050DE / batteries under check | batt | Batteries | batt | Batteries | 304298 | GH-SHABSHR-HAS | C1_0050DE_PH1 | (Batteries/Some parts are missing/cover) | 2019-09-16 11:22 | 2019-02-23 | TRUE
IM767793 | 3368DE | 0201_S_BH-ABO-SHIQAF_3368DE | Access VF / Main power / stolen batteries | batt | Batteries | batt | Batteries | 324904 | BH-ABO-SHIQAF | C1_3368DE_PH12 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-16 11:33 | 2019-04-17 | TRUE
IM767825 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN problem/stolen battery/clear after check GN | batt GN | Batteries Generator | batt GN | Batteries Generator | 324500 | SK-AZZAZI | C1_4029DE_PH15 | (Batteries/Item(s) stolen/No backup batteries.) (ATS / Engine/Wrong connection/Some cables are disconnected and need adjust.) (ATS / Engine/Panorama pictures for each system/Generator battery poles need cleaning, wax and covers.) (ATS / Engine/Panorama pictures for each system/Overview.) | 2019-09-16 12:21 | 2019-03-13 | TRUE
IM767836 | 0103RE | 00228_D_0103RE_RS-ST-ANTONIO | DG Stoppage / weak batteries / Fuel theft case / cleared after Gen restored | batt DG Gen | Batteries Generator Generator | batt DG Gen | Batteries Generator | 355830 | 01_G_RS-ST-ANTONIO_0103RE | C2_0103RE_PH3 | (Rectifiers/Alarms reporting to the OMC/Alarm on the rectifer module) (Batteries/Cables termination/lugs (AC side), lugs (DC side)/Loose in battery power cable) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Water leakage) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Genset Oil leakage) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Water leakage from the water pump ) (ATS / Engine/Unit earth/Stolen earth cables) (ATS / Engine/Components faulty/Defected genset battery) (ATS / Engine/Components faulty/Broken radiator fan plade ) (ATS / Engine/Wrong connection/Wrong connection , jumper on the genset main contactor ) (ATS / Engine/Wrong connection/Genset welded cables) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Bad genset contactor terminals ) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Unused genset ATS cables ) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Genset alarm cables , not fixed well , not terminated) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Charging system cables bad terminals) | 2019-09-16 12:42 | 2019-07-17 | TRUE
IM767864 | 0050DE | 0001_S_GH-SHABSHR-HAS_0050DE | Main power / batteries under check | batt | Batteries | batt | Batteries | 304298 | GH-SHABSHR-HAS | C1_0050DE_PH1 | (Batteries/Some parts are missing/cover) | 2019-09-16 12:51 | 2019-02-23 | TRUE
IM767875 | 3037DE | 0301_D_DK-BAGALAT_3037DE | Share ET / GN problem / stolen batteries | batt GN | Batteries Generator | batt GN | Batteries Generator | 345376 | DK-BAGALAT | C3_3037DE_PH11 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) (ATS / Engine/Components faulty/Control module has faulty buttons.) (ATS / Engine/Wrong connection/Cable has bad connections and need replacement.) | 2019-09-16 13:01 | 2019-06-19 | TRUE
IM767952 | 3394DE | 0011_S_B-SAFT-KHALED_3394DE | Share VF / Main power / weak batteries | batt | Batteries | batt | Batteries | 304033 | BH-SAFT-KHALED | C1_3394DE_PH13 | (Batteries/Components faulty/Faulty battery) | 2019-09-16 13:40 | 2019-01-24 | TRUE
IM767969 | 0435UP | 02_G_SG-GAZAZRA_0435UP | Main power disconnection , stolen batteries , recovered when EC power come back | batt | Batteries | batt | Batteries | 324744 | 01_G_QN-BAKHANES_3276UP | C4_3276UP_PH14 | (Batteries/Item(s) stolen/site batteries were stolen) (Batteries/Item(s) stolen/Batteries were stolen) | 2019-09-16 14:55 | 2019-04-04 | TRUE
IM767989 | 3778UP | 1291_S_AS-SABIL_3778UP_X | Main power disconnection , Stolen batteries , P.G connected | batt | Batteries | batt | Batteries | 356225 | 01_S_AS-SABIL_3778UP | C1_3778UP_PH15 | (Batteries/Some parts are (missing / stolen)/Batteries were stolen) | 2019-09-16 15:17 | 2019-09-04 | TRUE
IM768000 | 0096SI | 01_G_SS-MR-BLUE-BAY_0096SI | DG stoppage / weak batteries / Radiator problem / spare requested / cleared after power restored | batt DG | Batteries Generator | DG | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | (ATS / Engine/Unit earth/Genset unit earth cable not connected to main earth bar) (ATS / Engine/Components faulty/Defected genset battery) (ATS / Engine/Wrong connection/Wrong connection of the main ATS contactor , the coil fed by line power cable from the same contactor main contact) (ATS / Engine/Wrong connection/Welded cables ) (ATS / Engine/Wrong connection/Plastic bags used as isolation in the genset ATS panels) (ATS / Engine/Wrong connection/•Charge & dynamo cables welded bad status) (ATS / Engine/Wrong connection/Deep cycle battery used as genset starter) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Bad cables terminals) (ATS / Engine/Oil level & quality/Genset oil bad status) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure ) (ATS / Engine/Wrong connection/generator battery as used in the site and not suitable in High temp) | 2019-09-16 15:35 | 2019-07-01 | TRUE
IM768037 | 3740DE | 0521_S_KS-MNSHT-ABS_3740DE | Access TE / Main power / Stolen batteries | batt | Batteries | batt | Batteries | 324805 | KS-MNSHT-ABS | C1_3740DE_Ph14 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-16 15:40 | 2019-04-08 | TRUE
IM768038 | 3821DE | 1481_S_SK-HAJAJIYAH_3821DE | vf gn /stolen battery/VF checked gn | batt GN | Batteries Generator | batt | Batteries | 303842 | SK-HAJAJIYAH | C2-3821DE-PH14 | (Batteries/Item(s) stolen/BTS covers need fixation.) (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-16 15:42 | 2019-01-16 | TRUE
IM768076 | 3712DE | 0221_G_BH-QAMHA_3712DE | Main power problem @ BH-QAMHA_3712DE / SC GN in continous mode / BDT @ 07/01/2019 Is: 3.00 | GN | Generator | GN | Generator | 304258 | BH-QAMHA | C1_3712DE_PH14 | (ATS / Engine/Components faulty/Small generator not working // Site has history generator status alarm) | 2019-09-16 18:10 | 2019-02-19 | TRUE
IM768128 | 3821DE | 1481_S_SK-HAJAJIYAH_3821DE | VF GEN PROB/stolen battery/connect PG | batt Gen | Batteries Generator | batt | Batteries | 303842 | SK-HAJAJIYAH | C2-3821DE-PH14 | (Batteries/Item(s) stolen/BTS covers need fixation.) (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-16 21:35 | 2019-01-16 | TRUE
IM768134 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to DG Oil sensor problem and weak batteries(M) | batt DG | Batteries Generator | DG | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | (ATS / Engine/Wrong connection/wrong connections) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/floating hoses) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/unprotected cable) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage) | 2019-09-16 21:37 | 2019-03-26 | TRUE
IM768137 | 3178UP | 01_D_AT-BAQUR_3178UP | Generator stopped due to fuel shortage and site has weak backup batteries | backup batt Gen generator | Batteries Batteries Generator Generator | backup batt Gen generator | Batteries Generator | 324555 | 01_G_AT-BAQUR_3178UP | C2_3178UP_PH13 | (Batteries/Components faulty/site batteries were defected and to be changed) (ATS / Engine/Components faulty/Gen missing battery) (ATS / Engine/Wrong connection/Bad isolation for batteries cables) | 2019-09-16 20:36 | 2019-03-17 | TRUE
IM768185 | 3532DE | 0511_S_SK-NATORA_3532DE | VDF GEN problem/stolen battery/gen work | batt Gen | Batteries Generator | batt | Batteries | 356262 | SK-NATORA | C2_3532DE_PH13 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-17 03:02 | 2019-09-11 | TRUE
IM768221 | 3953DE | 0361_G_BH-MAARKA_3953DE | main power/weak battery/clear after power back | batt | Batteries | batt | Batteries | 304235 | BH-MAARKA | C1_3953DE_PH15 | (Batteries/Components faulty/Faulty battery and cable disconnected) | 2019-09-17 06:11 | 2019-02-14 | TRUE
IM768279 | 0581DE | 1571_S_SK-IKYAD-BHARIA_0581DE | main power/stolen batteries @SK-IKYAD-BHARIA_0581DE/clear on P.G | batt | Batteries | batt | Batteries | 324498 | SK-IKYAD-BHARIA | C1_0581DE_PH9 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-17 08:19 | 2019-03-13 | TRUE
IM768288 | 4021DE | 0181_S_BH-ABQAEEN_4021DE | Access VF / Main power / stolen batteries | batt | Batteries | batt | Batteries | 304224 | BH-ABQAEEN | C1_4021DE_PH15 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-16 11:33 | 2019-02-13 | TRUE
IM768337 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN problem/Stolen batteries @SK-MIT-GABIR_3833DE/clear on P.G | batt GN | Batteries Generator | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | (ATS / Engine/Wrong connection/Welding cables) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot) | 2019-09-17 09:05 | 2019-06-16 | TRUE
IM768357 | 3828DE | 0961_S_BH-GWAD-HUSNI_3828DE | Main power /stolen batteries | batt | Batteries | batt | Batteries | 356184 | BH-GWAD-HUSNI | C1_3828DE_PH14 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) | 2019-09-17 09:29 | 2019-09-02 | TRUE
IM768377 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Share VF / Main power / stolen batteries | batt | Batteries | batt | Batteries | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | (Batteries/Item(s) stolen/Stolen) | 2019-09-17 09:51 | 2019-03-25 | TRUE
IM768390 | 0735DE | 0711_G_GH-TANTA-HW2_0735DE | Main power @ GH-TANTA-HW2_0735DE / stolen batteries | batt | Batteries | batt | Batteries | 324537 | GH-TANTA-HW2 | C1_0735DE_PH9 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-17 10:19 | 2019-03-14 | TRUE
IM768394 | 3455UP | 0921_S_QN-ELNUGOU_3455UP | Main power disconnection ,batteries are suspected to be weak , P.G connected | batt | Batteries | batt | Batteries | 355996 | 01_S_QN-ELNUGOU_3455UP | C1_3455UP_PH14 | (Rectifiers/Alarms reporting to the OMC/Alarm was exists on rectifier control panel and appeared on the Omc to be cleared) (Batteries/Some parts are (missing / stolen)/Missing batteries poles covers) | 2019-09-17 09:09 | 2019-08-06 | TRUE
IM768395 | 3259DE | 0291_S_BH-ANAAM_3259DE | Share VF/ Main power / stolen batteries | batt | Batteries | batt | Batteries | 324534 | BH-ANAAM | C1_3259DE_PH12 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-17 10:18 | 2019-03-14 | TRUE
IM768401 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to commercial cut and no backup and access problem (MA) | backup | Batteries | backup | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | (Batteries/Some parts are (missing / stolen)/missing battereis) | 2019-09-17 11:01 | 2019-08-14 | TRUE
IM768440 | 3484DE | 0231_S_SK-MIT-BASHAR_3484DE | main power/stolen battery/power back | batt | Batteries | batt | Batteries | 356055 | SK-MIT-BASHAR | C2-3484DE-PH13 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) | 2019-09-17 10:21 | 2019-08-18 | TRUE
IM768468 | 3394DE | 0011_S_B-SAFT-KHALED_3394DE | Share VF / Main power / weak batteries | batt | Batteries | batt | Batteries | 304033 | BH-SAFT-KHALED | C1_3394DE_PH13 | (Batteries/Components faulty/Faulty battery) | 2019-09-17 11:15 | 2019-01-24 | TRUE
IM768489 | 0975UP | 0381_S_BS-MASID-ABYAD_0975UP_X | Commercial power cut off and site has stolen backup batteries, PG connected | backup batt | Batteries Batteries | backup batt | Batteries | 356360 | 01_S_BS-MASID-ABYAD_0975UP | C1_0975UP_PH12 | (Rectifiers/Alarms reporting to the OMC/Minor alarm doesn't appear on the OMC) (Batteries/Some parts are (missing / stolen)/Batteries and cables are stolen) | 2019-09-17 09:42 | 2019-09-17 | TRUE
IM768491 | 3414UP | 0401_S_BS-AHWA_3414UP_X | Commercial power cut off and site has weak backup batteries, PG connected | backup batt | Batteries Batteries | backup batt | Batteries | 356350 | 01_S_BS-AHWA_3414UP | C1_3414UP_PH14 | (Rectifiers/Alarms reporting to the OMC/Loop on the major alarm in DDF) (Batteries/Components faulty/Batteries are faulty and site is down after less than one hour of power disconnected) | 2019-09-17 10:33 | 2019-09-17 | TRUE
IM768527 | 0485SI | 01_S_SS-MOUSA-COAST_0485SI | EC power outage / weak batteries / cleared after power restored | batt | Batteries | batt | Batteries | 356428 | 01_S_SS-MOUSA-COAST_0485SI | C1_0485SI_PH13 | (Batteries/Components faulty/All battery string exploded & not work) | 2019-09-17 12:06 | 2019-09-30 | FALSE
IM768547 | 3924CA | U_S_3924CA_NC-YASMIN7 | down due to DG filter problem and stolen batteries @ 3924CA_NC-YASMIN7 | batt DG | Batteries Generator | DG | Generator | 356200 | NC-YASMIN7@U_S_3924CA_NC-YASMIN7 | 3924CA | (ATS / Engine/Unit earth/missing earth) | 2019-09-17 12:58 | 2019-08-07 | TRUE
IM768569 | 3779DE | 1021_S_GH-BASTAWISY_3779DE | Share VF / Main power / Stolen batteries | batt | Batteries | batt | Batteries | 355870 | GH-BASTAWISY | C1_3779DE_PH14 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) | 2019-09-17 12:44 | 2019-07-22 | TRUE
IM768603 | 3837DE | 0441_D_SK-BAKARISH_3837DE | access Guard/GN problem/Stolen batteries/clear after check GN | batt GN | Batteries Generator | batt GN | Batteries Generator | 345278 | SK-BAKARISH | C1-3837DE-PH14 | (Batteries/Some parts are (missing / stolen)/NO backup batteries.) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Cables and neutral bolts need proper terminals.) | 2019-09-17 13:12 | 2019-06-11 | TRUE
IM768694 | 3072DE | 291_Q_GH-AMIRA-MHALA_3072DE | New GN swap / connect PG | GN | Generator | GN | Generator | 324606 | Gh_Amria_Mahala | C1_3072DE_PH11 | (ATS / Engine/Components faulty/DG Disconnected) (ATS / Engine/Components faulty/Disconnected Cables) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Fix and protect) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Check leakage // hole) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) | 2019-09-17 16:05 | 2019-03-17 | TRUE
IM768746 | 3833DE | 0521_D_SK-MIT-GABIR_3833DE | GN problem/Stolen batteries@MIT-GABIR_3833DE/clear after check GN | batt GN | Batteries Generator | GN | Generator | 345384 | SK-MIT-GABIR | C5_3833DE_PH14 | (ATS / Engine/Wrong connection/Welding cables) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminals at 1 slot) | 2019-09-17 16:20 | 2019-06-16 | TRUE
IM768815 | 0407AL | G_ALEX-WST_48193_S2_S | Main power problem/Stolen batteries/Power backed/Autorecovered | batt | Batteries | batt | Batteries | 355458 | ALEX-WST ( Replacement) | C6_0407AL_PH09 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-17 20:13 | 2019-06-27 | TRUE
IM768847 | 4016CA | 02557_V_4016CA_BAHTIM4 | down due to power failure and weak batteries and auto restored (M) | batt | Batteries | batt | Batteries | 355762 | BAHTIM4 | C1_4016CA_PH17 | (Batteries/Some parts are (missing / stolen)/Two batteries are stolen) | 2019-09-18 00:35 | 2019-07-08 | TRUE
IM768857 | 3438DE | 0411_S_DK-ABU-HUSEIN_3438DE | one cell only/main power/stolen battery/clear on pg but it cannot carry all loads | batt | Batteries | batt | Batteries | 325116 | DK-ABU-HUSEIN | C2-3438DE-PH13 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-18 00:11 | 2019-05-14 | TRUE
IM768866 | 0581DE | 1571_S_SK-IKYAD-BHARIA_0581DE | main power/stolen batteries @SK-IKYAD-BHARIA_0581DE/clear on P.G | batt | Batteries | batt | Batteries | 324498 | SK-IKYAD-BHARIA | C1_0581DE_PH9 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-18 00:55 | 2019-03-13 | TRUE
IM768873 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Access VF " access blocked " / VF GN problem / Stolen batteries | batt GN | Batteries Generator | batt GN | Batteries Generator | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | (Batteries/Item(s) stolen/Stolen) (ATS / Engine/Item(s) stolen/missing battery) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) | 2019-09-18 01:22 | 2019-03-25 | TRUE
IM768874 | 3531DE | 1341_D_SK-MIT-EZZ_3531DE | GN. Problem / stolen batteries / clear after checking GN. | batt GN | Batteries Generator | batt GN | Batteries Generator | 303843 | SK-MIT-EZZ | C1-3531DE-PH13 | (Batteries/Item(s) stolen/No backup batteries.) (ATS / Engine/Wrong connection/Generator need proper water feeding and radiator need check.) | 2019-09-18 01:54 | 2019-01-16 | TRUE
IM768883 | 3067DE | 1301_D_DK-GAMMALIAH2_3067DE | GN problem / batteries under check | batt GN | Batteries Generator | GN | Generator | 304172 | DK-GAMMALIYAH2 | C5_3067DE_PH12 | (ATS / Engine/Wrong connection/Generator has bad radiator feeding.) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Neutral cables need proper fixation with neutral bar.) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Hole need cover.) | 2019-09-18 03:15 | 2019-02-11 | TRUE
IM768919 | 3720DE | 0651_D_MF-SK-KARADIS_3720DE | GN problem/stolen battery @-SK-KARADIS/ | batt GN | Batteries Generator | batt GN | Batteries Generator | 355737 | MF-SK-KARADIS | C2-3720DE-PH14 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Cables have bad connections, proper terminals and proper installtion are rerquired.) | 2019-09-18 06:15 | 2019-07-07 | TRUE
IM768945 | 0476DE | 0111_N_DK-BESHLA_0476DE | Main power/ battery under invistegation/clear after power back | batt | Batteries | batt | Batteries | 356100 | DK-BESHLA | C3_0476DE_PH7 | (Batteries/Some parts are (missing / stolen)/no batteries) | 2019-09-18 07:18 | 2019-08-25 | TRUE
IM768950 | 0055RE | 01_G_RS-MR44-16_0055RE | DG Stoppage / cleared on PG till Gen problem solved | DG Gen | Generator Generator | DG Gen | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure ) (ATS / Engine/Wrong connection/generator battery as used in the site and not suitable in High temp) | 2019-09-18 07:23 | 2019-07-01 | TRUE
IM768982 | 0324UP | 1421_S_MN-BARTABAT_0324UP | Commercial power cut off and site has stolen backup batteries | backup batt | Batteries Batteries | backup batt | Batteries | 324919 | 01_S_MN-BARTABAT_0324UP | C1_0324UP_PH8 | (Batteries/Item(s) stolen/Site batteries were stolen) | 2019-09-18 08:30 | 2019-04-20 | TRUE
IM769011 | 0605DE | 0041_S_DK-MAHMUDIYYA_0605DE | Main power @ DK-MAHMUDIYYA_0605DE / Stolen batteries | batt | Batteries | batt | Batteries | 304053 | DK-MAHMUDIYYA | C2_0605DE_PH9 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-18 09:10 | 2019-01-29 | TRUE
IM769016 | 0015RE | 00223_C_0015RE_SUKHNA-RD7 | DG stoppage / stolen batteries / dynamo problem / cleared after Gen restored | batt DG Gen | Batteries Generator Generator | batt DG Gen | Batteries Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | (Batteries/Some parts are (missing / stolen)/Battery string stolen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage) (ATS / Engine/Unit earth/Earth cable disconnected) (ATS / Engine/Components faulty/Generator indicator broken & not work) (ATS / Engine/Components faulty/Ventilation fan not work) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Power cable has no terminal) | 2019-09-18 09:31 | 2019-09-09 | TRUE
IM769036 | 0195RE | 03617_S_0195RE_RS-PRTO-COMPND | EC power outage / weak batteries / Access PG problem /cleared after power restored | batt | Batteries | batt | Batteries | 355604 | 01_S_RS-PRTO-COMPND_0195RE | C1_0195RE_PH9 | (Batteries/Components faulty/change battery) | 2019-09-18 09:36 | 2019-06-29 | TRUE
IM769053 | 3598CA | 01968_S_3598CA_10TH-RSD-16 | EC power outage / weak batteries / cleared after power restored | batt | Batteries | batt | Batteries | 356447 | 10TH-RSD-16 | C1_3598CA_PH14 | (Batteries/Some parts are (missing / stolen)/Missing battery pole cover) | 2019-09-18 10:12 | 2019-10-02 | FALSE
IM769096 | 3065AL | 03902_S_3065AL_MHWR-DABA-17 | Guard access problem / GN problem / stolen batteries / restored after solved Gn problem | batt GN | Batteries Generator | GN | Generator | 324550 | MHWR-DABA-17 | C1_3065AL_PH20 | (ATS / Engine/Wrong connection/Wrong connection (Joint cables)) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM organization/Cables needs organization) | 2019-09-18 09:07 | 2019-03-17 | TRUE
IM769123 | 3126DE | 0121_S_DK-HAGYZEYA_3126DE | Access ET. / Main Power / Stolen batteries / Clear on PG | batt | Batteries | batt | Batteries | 355992 | DK-HAGYZEYA | C6-3126DE-PH12 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-18 09:53 | 2019-08-07 | TRUE
IM769137 | 3971DE | 0511_S_GH-ABU-GENDI_3971DE | ET Share / Main power / Stolen batteries | batt | Batteries | batt | Batteries | 324794 | GH-ABU-GENDI | C1_3971DE_PH15 | (Batteries/Item(s) stolen/stolen batteries) | 2019-09-18 10:10 | 2019-04-10 | TRUE
IM769139 | 3344DE | 0681_S_BH-ELNEGILY_3344DE | VF Share / Main power / Stolen batteries | batt | Batteries | batt | Batteries | 304214 | BH-ELNEGILY | C3_3344DE_PH12 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-18 10:18 | 2019-02-12 | TRUE
IM769161 | 0329UP | 0791_S_MN-EBSHAK_0329UP | Commercial power cut off and site has weak backup batteries, PG connected | backup batt | Batteries Batteries | backup batt | Batteries | 325023 | 01_S_MN-EBSHAK_0329UP | C1_0329UP_PH8 | (Batteries/Item(s) stolen/stolen Battery) | 2019-09-18 11:30 | 2019-04-29 | TRUE
IM769189 | 0080UP | L_E_AS-WST_0080UP | Swap Rectifier AP# 357553 | rect | Rectifier | rect | Rectifier | 345348 | 01_S_AS-WST_0080UP | C3_0080UP_PH3 | (DC Boxes/Unit earth/ddf earth cable is missing) (DC Boxes/Unit earth/ddf earth cable is missing earth) | 2019-09-17 07:30 | 2019-06-13 | TRUE
IM769240 | 3394DE | 0011_S_B-SAFT-KHALED_3394DE | VF Share / Main power / Weak batteries | batt | Batteries | batt | Batteries | 304033 | BH-SAFT-KHALED | C1_3394DE_PH13 | (Batteries/Components faulty/Faulty battery) | 2019-09-18 11:53 | 2019-01-24 | TRUE
IM769271 | 3776UP | 02_D_SG-HARJA-QARAN_3776UP | Generator problem , weak batteries , guard access problem ,recovered. | batt Gen generator | Batteries Generator Generator | batt Gen generator | Batteries Generator | 355969 | 01_G_SG-HARJA-QARAN_3776UP | C1_3776UP_PH15 | (Rectifiers/Alarms reporting to the OMC/Rectifier minor alarm was looped at ddf ) (Batteries/Components faulty/Batteries were faulty ( exploded )) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage from etisalat Gen) (ATS / Engine/Unit earth/Gen enclosure earth cable is not connected) (ATS / Engine/Components faulty/ radiator is defected and connected with extranl water source) (ATS / Engine/Components faulty/Gen battey is defected and need new one) (ATS / Engine/Components faulty/ATS pressing keys and Knob were defected) (ATS / Engine/Wrong connection/Two cables inserted in one slot and not teminated can cause bad connections ) | 2019-09-14 18:59 | 2019-08-04 | TRUE
IM769287 | 0015RE | 00223_C_0015RE_SUKHNA-RD7 | DG stoppage / stolen batteries / dynamo problem / cleared after power restored | batt DG | Batteries Generator | batt DG | Batteries Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | (Batteries/Some parts are (missing / stolen)/Battery string stolen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage) (ATS / Engine/Unit earth/Earth cable disconnected) (ATS / Engine/Components faulty/Generator indicator broken & not work) (ATS / Engine/Components faulty/Ventilation fan not work) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Power cable has no terminal) | 2019-09-18 13:12 | 2019-09-09 | TRUE
IM769296 | 0013RE | 03428_Q_0013RE_SZ-HW33-9 | DG stoppage / weak batteries / Radiator problem / cleared after power restored | batt DG | Batteries Generator | DG | Generator | 345446 | 01_W_SZ-HW33-9_0013RE | C1_0013RE_PH1 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Genest unclean & oil leakage) (ATS / Engine/Unit earth/Loose in earth cable) (ATS / Engine/Components faulty/Genset radiator low water level ) (ATS / Engine/Components faulty/Genset radiator low water level & missing green water) (ATS / Engine/Components faulty/Hour meter gauage not work) (ATS / Engine/Wrong connection/ATS welded cables & bad connection) (ATS / Engine/Wrong connection/Non standard (From Orange ) DC/DC converter used & bad terminals) (ATS / Engine/Wrong connection/Misisng fuel tank indoor light & power cable should be dismantled) (ATS / Engine/Wrong connection/Stolen power from the site) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Remain power cable) | 2019-09-18 13:09 | 2019-06-25 | TRUE
IM769316 | 0498RE | 03500_S_0498RE_SZ-SELIM-HAY | EC power outage / Sharing VF / weak batteries / access PG problem / cleared after power restored | batt | Batteries | batt | Batteries | 345366 | 01_S_SZ-SELIM-HAY_0498RE | C1_0498RE_PH17 | (Batteries/Some parts are (missing / stolen)/Stolen battery) | 2019-09-18 13:43 | 2019-06-17 | TRUE
IM769334 | 0657CA | 01766_S_0657CA_BAGDAD-ST | down due to power failure and dead batteries | batt | Batteries | batt | Batteries | 345255 | BAGDAD-ST | C7_0657CA_PH8 | (Batteries/Some parts are missing/missing batteries/ stolen) | 2019-09-18 14:17 | 2019-05-22 | TRUE
IM769381 | 3445UP | 591_D_MN-TOKH_3445UP | Generator stopped due to LOP alarm and site has weak backup batteries Site has guard access problem | backup batt Gen generator | Batteries Batteries Generator Generator | Gen generator | Generator | 356182 | 01_G_MN-TOKH_3445UP | C1_3445UP_PH14 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check leakage) (ATS / Engine/Components faulty/need battery) | 2019-09-18 15:20 | 2019-08-28 | TRUE
IM769390 | 0013RE | 03428_Q_0013RE_SZ-HW33-9 | DG stoppage / weak batteries / cleared after power restored | batt DG | Batteries Generator | DG | Generator | 345446 | 01_W_SZ-HW33-9_0013RE | C1_0013RE_PH1 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Genest unclean & oil leakage) (ATS / Engine/Unit earth/Loose in earth cable) (ATS / Engine/Components faulty/Genset radiator low water level ) (ATS / Engine/Components faulty/Genset radiator low water level & missing green water) (ATS / Engine/Components faulty/Hour meter gauage not work) (ATS / Engine/Wrong connection/ATS welded cables & bad connection) (ATS / Engine/Wrong connection/Non standard (From Orange ) DC/DC converter used & bad terminals) (ATS / Engine/Wrong connection/Misisng fuel tank indoor light & power cable should be dismantled) (ATS / Engine/Wrong connection/Stolen power from the site) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Remain power cable) | 2019-09-18 15:40 | 2019-06-25 | TRUE
IM769433 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem and stolen batteries and VF access problem . | batt DG | Batteries Generator | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | (Batteries/Some parts are (missing / stolen)/missing battereis) | 2019-09-18 16:01 | 2019-08-14 | TRUE
IM769459 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to generator problem (filter air) and stolen batteries | batt Gen generator | Batteries Generator Generator | batt Gen generator | Batteries Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | (Batteries/Some parts are missing/missing batteries) (ATS / Engine/Wrong connection/wrong connection) | 2019-09-18 16:49 | 2019-02-26 | TRUE
IM769494 | 3185DE | 0171_D_MF-SANGALF_3185DE | GN Problem/ Stolen batteries / Clear after check GN | batt GN | Batteries Generator | batt | Batteries | 345324 | MF-SANGALF | C2-3185DE-PH12 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) | 2019-09-18 17:34 | 2019-06-11 | TRUE
IM769500 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to generator problem air filter and stolen batteries | batt Gen generator | Batteries Generator Generator | batt Gen generator | Batteries Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | (Batteries/Some parts are missing/missing batteries) (ATS / Engine/Wrong connection/wrong connection) | 2019-09-18 17:59 | 2019-02-26 | TRUE
IM769526 | 3290DE | 1171_D_MF-QATTA_3290DE | GEN failure/batteries under investigtion | batt Gen | Batteries Generator | Gen | Generator | 355961 | MF-QATTA | C3_3290DE_PH12 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has leakage) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminals requried) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Cable need to be terminated well) | 2019-09-18 18:26 | 2019-08-03 | TRUE
IM769549 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to generator problem (filter air) and stolen batteries | batt Gen generator | Batteries Generator Generator | batt Gen generator | Batteries Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | (Batteries/Some parts are missing/missing batteries) (ATS / Engine/Wrong connection/wrong connection) | 2019-09-18 20:33 | 2019-02-26 | TRUE
IM769578 | 3096DE | 02891_G_3096DE_OBOUR-DST6 | down due to DG problem and no battery install | batt DG | Batteries Generator | DG | Generator | 345263 | OBOUR-DST6 | C1_3096DE_PH12 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage) | 2019-09-18 21:32 | 2019-05-27 | TRUE
IM769622 | 3807UP | 0631_D_QN-MHAMID-QBLY_3807UP | Generator problem , batteries are suspected to be weak ,Guard night access problem , solved , Recovered after solvig the generator problem . | batt Gen generator | Batteries Generator Generator | batt Gen generator | Batteries Generator | 355794 | 01_G_QN-MHAMID-QBLY_3807UP | C1_3807UP_PH15 | (Rectifiers/Alarms reporting to the OMC/Rectifier minor alarm was looped at ddf) (ATS / Engine/Unit earth/Earth bar is missing) (ATS / Engine/Components faulty/Gen enclosure Screen press keys were defected) (ATS / Engine/Filters condition oil/fuel/air/Air Filter cover is not fixed) | 2019-09-19 00:28 | 2019-07-14 | TRUE
IM769634 | 4011CA | 02353_V_4011CA_MOSTORD-RD2 | down due to main power cut off and stolen batt. (I) | batt | Batteries | batt | Batteries | 355905 | MOSTORD-RD2 | C1_4011CA_PH17 | (Batteries/Some parts are (missing / stolen)/Batteries are stolen) | 2019-09-19 02:37 | 2019-07-25 | TRUE
IM769656 | 0709DE | 0181_D_GH-MIDO-PARK_0709DE | Access Owner / GN problem | GN | Generator | GN | Generator | 355834 | GH-MIDO-PARK | C3_0709DE_PH9 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check and clean) (ATS / Engine/Unit earth/not earthed) (ATS / Engine/Components faulty/faulty radiator) (ATS / Engine/Components faulty/faulty) (ATS / Engine/Components below/over rate (excluding main power feeder if not hot)/high rate) | 2019-09-19 03:49 | 2019-07-18 | TRUE
IM769689 | 3953DE | 0361_G_BH-MAARKA_3953DE | Access ET. / Main Power / Weak batteries / Clear on PG | batt | Batteries | batt | Batteries | 304235 | BH-MAARKA | C1_3953DE_PH15 | (Batteries/Components faulty/Faulty battery and cable disconnected) | 2019-09-19 06:35 | 2019-02-14 | TRUE
IM769690 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN peoblem/Stolen batteries/ | batt GN | Batteries Generator | batt GN | Batteries Generator | 324500 | SK-AZZAZI | C1_4029DE_PH15 | (Batteries/Item(s) stolen/No backup batteries.) (ATS / Engine/Wrong connection/Some cables are disconnected and need adjust.) (ATS / Engine/Panorama pictures for each system/Generator battery poles need cleaning, wax and covers.) (ATS / Engine/Panorama pictures for each system/Overview.) | 2019-09-19 06:41 | 2019-03-13 | TRUE
IM769696 | 3775DE | 0471_D_DK-DABBOS-VLG_3775DE | GN problem / batteries under check | batt GN | Batteries Generator | GN | Generator | 325073 | DK-DABBOS-VLG | C1_3775DE_PH14 | (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/bad terminals) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) | 2019-09-19 06:52 | 2019-05-07 | TRUE
IM769701 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to DG Dynamo problem and batt. stolen (I) | batt DG | Batteries Generator | batt DG | Batteries Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | (Batteries/Some parts are missing/missing batteries) (ATS / Engine/Wrong connection/wrong connection) | 2019-09-19 07:25 | 2019-02-26 | TRUE
IM769724 | 0102RE | 00086_S_0102RE_SZ-STLLADEMARE | EC power outage / weak batteries / access PG problem/ Hotel / cleared after power restored | batt | Batteries | batt | Batteries | 324988 | SZ-STLLADEMARE | C3_0102RE_PH3 | (Batteries/Item(s) stolen/Battery string stolen) | 2019-09-19 08:26 | 2019-05-01 | TRUE
IM769738 | 3844DE | 1841_S_BH-SAHALI_3844DE | Access Guard " 1786 " / H.T | H.T | A/Cs | H.T | A/Cs | 356089 | BH-SAHALI | C1_3844DE_PH14 | (A/Cs Cooling / Free Cooling / Ventilation/Components faulty/A/C has no proper cooling (Working only as a fan)) (A/Cs Cooling / Free Cooling / Ventilation/Components faulty/A/C has no proper cooling (Working only as a fan) // Burned cables) (A/Cs Cooling / Free Cooling / Ventilation/Wrong connection/Cancelling the control board and replacing it by temperature sensor) (A/Cs Cooling / Free Cooling / Ventilation/Cables termination/lugs (AC side), lugs (DC side)/Cables at 1 slot) (A/Cs Cooling / Free Cooling / Ventilation/Cables termination/lugs (AC side), lugs (DC side)/Cable need to be terminated well) | 2019-09-19 07:19 | 2019-08-20 | TRUE
IM769747 | 0411RE | 03870_S_0411RE_RS-BRAYKA-BAY | PM Generator / stolen batteries | batt Gen generator | Batteries Generator Generator | batt Gen generator | Batteries Generator | 356418 | 01_S_RS-BRAYKA-BAY_0411RE | C1_0411RE_PH15 | (Batteries/Some parts are (missing / stolen)/Batteries were stolen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Open gland in Gen enclosure need insulation) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Two cables inserted in one slot and not teminated can cause bad connections ) | 2019-09-19 09:01 | 2019-09-26 | FALSE
IM769876 | 0498RE | 03500_S_0498RE_SZ-SELIM-HAY | EC power outage / Sharing VF / weak batteries / access PG problem / cleared after power restored | batt | Batteries | batt | Batteries | 345366 | 01_S_SZ-SELIM-HAY_0498RE | C1_0498RE_PH17 | (Batteries/Some parts are (missing / stolen)/Stolen battery) | 2019-09-19 10:44 | 2019-06-17 | TRUE
IM769892 | 3272UP | 0791_G_QN-QENWYA-BHRY_3272UP | Main power disconnection ,batteries are suspected to be weak , recovered when EC power come back | batt | Batteries | batt | Batteries | 355823 | 01_G_QN-QENWYA-BHRY_3272UP | C2_3272UP_PH14 | (Batteries/Some parts are (missing / stolen)/Some of Batteries were stolen) | 2019-09-19 11:20 | 2019-07-16 | TRUE
IM769920 | 3628DE | 0811_S_GH-QSR-BAGHDAD_3628DE | Main power / stolen batteries | batt | Batteries | batt | Batteries | 324836 | GH-QSR-BAGHDAD | C2_3628DE_PH13 | (Batteries/Item(s) stolen/Stolen batteries) | 2019-09-19 10:59 | 2019-04-15 | TRUE
IM769927 | 0248UP | 0061_H_SG-MINSHAH-NTH_0248UP | Main power disconnection, batteries are suspected to be weak, Standby Generator was not worked due to fuel pump problem, recovere d when EC power come back | batt Gen generator | Batteries Generator Generator | batt Gen generator | Batteries Generator | 356519 | S_SG-MINSHAH-NTH_0248UP | C1_0248UP_PH06 | (Batteries/Some parts are (missing / stolen)/Batteries string were stolen) (ATS / Engine/Wrong connection/neutral cable inside ATS panel was Burnt) (ATS / Engine/Alarms on equipment (excluding ADM)/Gen has alarm ) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Bad teminated can cause bad connections) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Two cables inserted in one slot and bad teminated can cause bad connections) | 2019-09-19 12:01 | 2019-10-10 | FALSE
IM769948 | 0028RE | 03477_N_0028RE_SZ-SUEZ8 | EC power outage / weak batteries / access PG problem / cleared after power restored | batt | Batteries | batt | Batteries | 345369 | 01_N_SZ-SUEZ8_0028RE | C2_0028RE_PH1 | (Batteries/Some parts are (missing / stolen)/Stolen battery string) | 2019-09-19 12:39 | 2019-06-17 | TRUE
IM769954 | 3385DE | 0671_S_BH-GHAZALA-VLG_3385DE | Suspected main power / batteries under check | batt | Batteries | batt | Batteries | 355780 | BH-GHAZALA-VLG | C2_3385DE_PH13 | (Rectifiers/Alarms reporting to the OMC/Site down due to power (Check alarms with OMC)) | 2019-09-19 11:39 | 2019-07-11 | TRUE
IM769974 | 0102RE | 00086_S_0102RE_SZ-STLLADEMARE | EC power outage / weak batteries / access PG problem/ Hotel / cleared after power restored | batt | Batteries | batt | Batteries | 324988 | SZ-STLLADEMARE | C3_0102RE_PH3 | (Batteries/Item(s) stolen/Battery string stolen) | 2019-09-19 12:50 | 2019-05-01 | TRUE
IM769983 | 3394DE | 0011_S_B-SAFT-KHALED_3394DE | Share VF / Main power / weak batteries | batt | Batteries | batt | Batteries | 304033 | BH-SAFT-KHALED | C1_3394DE_PH13 | (Batteries/Components faulty/Faulty battery) | 2019-09-19 12:54 | 2019-01-24 | TRUE
IM769985 | 3333DE | 0181_S_BH-OM-SABER_3333DE | Access VF. / Main Power / Stolen batteries / Clear after power back | batt | Batteries | batt | Batteries | 304089 | BH-OM-SABER_SSS0 | C1_3333DE_PH12 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-19 13:05 | 2019-01-30 | TRUE
IM770053 | 0476DE | 0111_N_DK-BESHLA_0476DE | Main power/ batteries dismentle/clear after power back | batt | Batteries | batt | Batteries | 356100 | DK-BESHLA | C3_0476DE_PH7 | (Batteries/Some parts are (missing / stolen)/no batteries) | 2019-09-19 15:00 | 2019-08-25 | TRUE
IM770072 | 0443SI | 0481_G_SS-RING-RD2_0443SI | DG stoppage / weak batteries / cleared after power restored | batt DG | Batteries Generator | DG | Generator | 355554 | 01_G_SS-RING-RD2_0443SI | C1_0443SI_PH12 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage ) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage ) (ATS / Engine/Unit earth/earth cable not connected ) (ATS / Engine/Unit earth/earth bar not connected to main earth bar ) (ATS / Engine/Wrong connection/welded cable) (ATS / Engine/Wrong connection/welded neutral cable ) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/cable not terminated) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/cables not terminated) | 2019-09-19 15:21 | 2019-07-03 | TRUE
IM770148 | 0498RE | 03500_S_0498RE_SZ-SELIM-HAY | EC power outage / Sharing VF / weak batteries / access PG problem / cleared after power restored | batt | Batteries | batt | Batteries | 345366 | 01_S_SZ-SELIM-HAY_0498RE | C1_0498RE_PH17 | (Batteries/Some parts are (missing / stolen)/Stolen battery) | 2019-09-19 16:44 | 2019-06-17 | TRUE
IM770198 | 0613DE | 00167_D_0613DE_SANDORINI-CLUB | GN. Problem /batteries UNDER INVESTIGATION / clear after check GEN | batt Gen GN | Batteries Generator Generator | Gen GN | Generator | 303981 | Sandorini Country Club | C1_0613DE_PH9 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check and clean) | 2019-09-19 20:22 | 2019-01-22 | TRUE
IM770220 | 0540UP | 0071_G_AS-ENT_0540UP_X | Generator problem , batteries are suspected to be weak , Recovered after solvig the generator problem . | batt Gen generator | Batteries Generator Generator | batt Gen generator | Batteries Generator | 345343 | 01_G_AS-ENT_0540UP | C3_0540UP_PH9 | (Rectifiers/Alarms reporting to the OMC/Rectifer alarm not appeared on the omc ( Minor & major rectifier alarm looped at ddf )) (Batteries/Some parts are (missing / stolen)/One Batteries string was stolen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure) | 2019-09-19 21:01 | 2019-06-13 | TRUE
IM770244 | 0405RE | 03878_S_0405RE_RS-MRSA-NAKARI | ET DG Stoppage / stolen batteries / cleared after GEN restored | batt DG Gen | Batteries Generator Generator | batt | Batteries | 356420 | 01_S_RS-MRSA-NAKARI_0405RE | C1_0405RE_PH15 | (Batteries/Some parts are (missing / stolen)/Batteries were stolen) | 2019-09-19 23:39 | 2019-09-26 | FALSE
IM770291 | 3494DE | 1101_D_GH-ATWA-QIBLYA_3494DE | GN problem / Stolen batteries | batt GN | Batteries Generator | GN | Generator | 345242 | GH-ATWA-QIBLYA | C4_3494DE_PH13 | (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminal requried) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Cable need to be terminated well) (ATS / Engine/Filters condition oil/fuel/air/Missing protective cover) | 2019-09-20 04:45 | 2019-06-02 | TRUE
IM770311 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem and access VF problem and stolen batt. (I) | batt DG | Batteries Generator | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | (Batteries/Some parts are (missing / stolen)/missing battereis) | 2019-09-20 06:15 | 2019-08-14 | TRUE
IM770335 | 0485SI | 01_S_SS-MOUSA-COAST_0485SI | Outage power in area located site , dead batteries Once power restored , site recovered | batt | Batteries | batt | Batteries | 356428 | 01_S_SS-MOUSA-COAST_0485SI | C1_0485SI_PH13 | (Batteries/Components faulty/All battery string exploded & not work) | 2019-09-20 06:25 | 2019-09-30 | FALSE
IM770340 | 3892DE | 0171_S_BH-ZWIT-HUMOR_3892DE | Main power / Stolen batteries | batt | Batteries | batt | Batteries | 324905 | BH-ZWIT-HUMOR | C1_3892DE_PH14 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-20 07:49 | 2019-04-17 | TRUE
IM770341 | 0576DE | 1611_G_BH-WAFAIYYA_0576DE | Main power / Stolen batteries | batt | Batteries | batt | Batteries | 324440 | BH-WAFAIYYA | C2_0576DE_PH9 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-20 07:49 | 2019-03-07 | TRUE
IM770352 | 3844DE | 1841_S_BH-SAHALI_3844DE | H.T alarm / BTS hanged | H.T | A/Cs | H.T | A/Cs | 356089 | BH-SAHALI | C1_3844DE_PH14 | (A/Cs Cooling / Free Cooling / Ventilation/Components faulty/A/C has no proper cooling (Working only as a fan)) (A/Cs Cooling / Free Cooling / Ventilation/Components faulty/A/C has no proper cooling (Working only as a fan) // Burned cables) (A/Cs Cooling / Free Cooling / Ventilation/Wrong connection/Cancelling the control board and replacing it by temperature sensor) (A/Cs Cooling / Free Cooling / Ventilation/Cables termination/lugs (AC side), lugs (DC side)/Cables at 1 slot) (A/Cs Cooling / Free Cooling / Ventilation/Cables termination/lugs (AC side), lugs (DC side)/Cable need to be terminated well) | 2019-09-20 08:51 | 2019-08-20 | TRUE
IM770353 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Due to Generator problem , weak batteries, Recovered | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | (ATS / Engine/Components faulty/Gen battery was defected) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM organization/ATS Cables not organized) | 2019-09-20 07:28 | 2019-05-18 | TRUE
IM770365 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to DG oil sensor problem & stolen batteries (T) | batt DG | Batteries Generator | batt DG | Batteries Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | (Batteries/Some parts are missing/missing batteries) (ATS / Engine/Wrong connection/wrong connection) | 2019-09-20 09:12 | 2019-02-26 | TRUE
IM770375 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, solved . | Gen generator | Generator Generator | Gen generator | Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | (ATS / Engine/Wrong connection/external cable to the guard connected from gen and not protected) (ATS / Engine/Wrong connection/One Contactor turned on by setting wood inside it) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cables not protected in tube) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cables not protected) (ATS / Engine/Item(s) stolen/Gen battery is missing) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/ Fuel leakage inside Gen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage inside Gen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage beisde Gen enclosure area need cleaning) (ATS / Engine/Panorama pictures for each system/Open gland in Gen enclosure need insulation) (ATS / Engine/Panorama pictures for each system/Panorama site view in outside site) (ATS / Engine/Panorama pictures for each system/Last Gen hour meter at Audit G ( 31148 )) | 2019-09-20 10:35 | 2019-01-16 | TRUE
IM770392 | 0800CA | 01942_S_0800CA_RAMADAN-FCT | Outage power in factory located site access factory weekend / weak batteries /Nog. informed Once power restored site recovered | batt | Batteries | batt | Batteries | 356352 | RAMADAN-FCT | C1_0800CA_PH9 | (Rectifiers/Alarms reporting to the OMC/Power alarm not report the OMC due to loop on DDF) (Rectifiers/Alarms reporting to the OMC/Rectifier minor alarm not report the OMC due to loop on DDF) | 2019-09-20 11:15 | 2019-09-21 | FALSE
IM770405 | 0476DE | 0111_N_DK-BESHLA_0476DE | main power/batteries not installed /clear after power back | batt | Batteries | batt | Batteries | 356100 | DK-BESHLA | C3_0476DE_PH7 | (Batteries/Some parts are (missing / stolen)/no batteries) | 2019-09-20 12:40 | 2019-08-25 | TRUE
IM770463 | 3454DE | 1061_D_GH-MAHLT-MENOF_3454DE | share ET / GN problem / stolen batteries | batt GN | Batteries Generator | batt GN | Batteries Generator | 324838 | GH-MAHLT-MENOF | C2_3454DE_PH13 | (Batteries/Item(s) stolen/Stolen Batteries) (ATS / Engine/Item(s) stolen/stolen batteries) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) | 2019-09-20 15:43 | 2019-04-10 | TRUE
IM770534 | 0485SI | 01_S_SS-MOUSA-COAST_0485SI | Outage power in area located site , dead batteries Once power restored , site recovered | batt | Batteries | batt | Batteries | 356428 | 01_S_SS-MOUSA-COAST_0485SI | C1_0485SI_PH13 | (Batteries/Components faulty/All battery string exploded & not work) | 2019-09-20 16:54 | 2019-09-30 | FALSE
IM770542 | 3778UP | 1291_S_AS-SABIL_3778UP_X | Main power disconnection , stolen batteries , SCG defected , P.G Connected . | batt | Batteries | batt | Batteries | 356225 | 01_S_AS-SABIL_3778UP | C1_3778UP_PH15 | (Batteries/Some parts are (missing / stolen)/Batteries were stolen) | 2019-09-20 20:57 | 2019-09-04 | TRUE
IM770548 | 0899UP | 00352_S_0899UP_6OCT-ZAYED-1ST | down due to main power cut off and stolen batt. (I) | batt | Batteries | batt | Batteries | 356343 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | (Batteries/Some parts are (missing / stolen)/stolen batteries) | 2019-09-20 22:46 | 2019-09-15 | TRUE
IM770576 | 0405RE | 03878_S_0405RE_RS-MRSA-NAKARI | ET DG Stopped , stolen batteries , caused site Down once ET team fix DG Site recovered | batt DG | Batteries Generator | batt | Batteries | 356420 | 01_S_RS-MRSA-NAKARI_0405RE | C1_0405RE_PH15 | (Batteries/Some parts are (missing / stolen)/Batteries were stolen) | 2019-09-21 01:27 | 2019-09-26 | FALSE
IM770578 | 3916DE | 1191_S_BH-BAYDA-2_3916DE | Access guard / Main power / weak batteries | batt | Batteries | batt | Batteries | 355465 | BH-BAYDA-2 | C1_3916DE_PH14 | (Batteries/Components faulty/faulty) | 2019-09-21 00:50 | 2019-06-23 | TRUE
IM770579 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/stolen battery/clear after check GN | batt GN | Batteries Generator | batt GN | Batteries Generator | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | (Batteries/Some parts are missing/Battery cabinet need cleaning (from inside) and holes need sealing.) (Batteries/Some parts are missing/Batteries poles need have missing covers.) (ATS / Engine/Components faulty/Generator has bad performance and need overall.) (ATS / Engine/Panorama pictures for each system/Overview.) | 2019-09-21 01:02 | 2019-05-21 | TRUE
IM770593 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | VF GN / VF night access /stolen battery/clear after | batt GN | Batteries Generator | batt GN | Batteries Generator | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | (Batteries/Item(s) stolen/There is no battery for site) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cable has damaged protective isolation) | 2019-09-21 02:34 | 2019-05-09 | TRUE
IM770597 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem & access VF problem & stolen batt. (I) | batt DG | Batteries Generator | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | (Batteries/Some parts are (missing / stolen)/missing battereis) | 2019-09-21 03:35 | 2019-08-14 | TRUE
IM770612 | 3368DE | 0201_S_BH-ABO-SHIQAF_3368DE | Access VF / Main power / stolen batteries | batt | Batteries | batt | Batteries | 324904 | BH-ABO-SHIQAF | C1_3368DE_PH12 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-21 03:43 | 2019-04-17 | TRUE
IM770640 | 0595DE | 0281_G_DK-NISHA_0595DE | Main power / weak batteries | batt | Batteries | batt | Batteries | 324924 | DK-NISHAA | C1_0595DE_PH9 | (Batteries/Some parts are missing/cover) | 2019-09-21 06:26 | 2019-04-22 | TRUE
IM770661 | 3495DE | 0181_S_SK-MAHDIYA_3495DE | Main Power / Stolen batteries / Clear after power back | batt | Batteries | batt | Batteries | 304144 | SK-MAHDIYA | C3_3495DE_PH13 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-21 07:52 | 2019-02-09 | TRUE
IM770665 | 0476DE | 0111_N_DK-BESHLA_0476DE | Main power/batteries were dismanteled/ | batt | Batteries | batt | Batteries | 356100 | DK-BESHLA | C3_0476DE_PH7 | (Batteries/Some parts are (missing / stolen)/no batteries) | 2019-09-21 09:41 | 2019-08-25 | TRUE
IM770668 | 0364RE | U_S_0364RE_SZ-MALLAHA | Outage power in area located site , dead batteries , access PG Once power restored , site recovered | batt | Batteries | batt | Batteries | 356046 | SZ-MALLAHA | 0364RE | (Batteries/Some parts are (missing / stolen)/Missing battery pole cover) | 2019-09-21 09:45 | 2019-08-18 | TRUE
IM770676 | 0485DE | K_MF-BARAHIM_21106_1 | Main power /6074150/batteries under investigation@MF-BARAHIM_0485DE// | batt | Batteries | batt | Batteries | 304303 | MF-BARAHIM | C5_0485DE_PH7 | (Batteries/Some parts are missing/Battery without covers) | 2019-09-21 10:31 | 2019-02-21 | TRUE
IM770679 | 0587DE | 0221_S_DK-KFR-KURDI_0587DE | Share VF / main power / stolen batteries | batt | Batteries | batt | Batteries | 324791 | DK-KFR-KURDI | C9_0587DE_PH09 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-21 09:54 | 2019-04-10 | TRUE
IM770710 | 3403UP | 01_G_LU-QBLY-QAMOLA_3403UP | Main power disconnection ,batteries are suspected to be weak , P.G connected | batt | Batteries | batt | Batteries | 356289 | 01_G_LU-QBLY-QAMOLA_3403UP | C2_3403UP_PH14 | (Batteries/Components faulty/Backup batteries voltage drop too fast) | 2019-09-21 09:27 | 2019-09-11 | TRUE
IM770758 | 3394DE | 0011_S_B-SAFT-KHALED_3394DE | VF Share / Main power / Weak batteries | batt | Batteries | batt | Batteries | 304033 | BH-SAFT-KHALED | C1_3394DE_PH13 | (Batteries/Components faulty/Faulty battery) | 2019-09-21 12:05 | 2019-01-24 | TRUE
IM770869 | 3089UP | 2141_S_SG-GALAWEYA_3089UP | Main power disconnection , stolen batteries , recovered when EC power come back | batt | Batteries | batt | Batteries | 356371 | 01_S_SG-GALAWEYA_3089UP | C1_3089UP_PH13 | (Batteries/Some parts are (missing / stolen)/site batteries were Stolen) | 2019-09-21 13:45 | 2019-09-18 | TRUE
IM770885 | 0029SI | 01_G_SZ-HALIJAL-OYUN_0029SI | DG Stopped due alternator problem , dead batteries once team arrive and install PG Sites Recovered | batt DG | Batteries Generator | batt DG | Batteries Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | (Batteries/Item(s) stolen/Stolen battery string) (Batteries/Item(s) stolen/C.B's connected to the stolen battery string should be switched off) (ATS / Engine/Components faulty/Genset indicator notwork , voltage & temp) (ATS / Engine/Components faulty/Burnet main contactor) (ATS / Engine/Components faulty/Burnet ATS panel) (ATS / Engine/Wrong connection/Jumper on the main contactor) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Bad terminals of main contactor) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Disconnected ATS cable) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Hole in the genset container) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Genset oil leakage) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure ) (ATS / Engine/Wrong connection/generator battery as used in the site and not suitable in High temp) | 2019-09-21 14:39 | 2019-07-01 | TRUE
IM770894 | 3634DE | 1481_D_MF-DAMLIG_3634DE | Main power /batteries under investigation// Clear after power back | batt | Batteries | batt | Batteries | 303849 | MF-DAMLIG | C1-3634DE-PH13 | (Batteries/Components faulty/Faulty battery) | 2019-09-21 15:24 | 2019-01-15 | TRUE
IM771001 | 3943DE | 0921_S_SK-AKRASH_3943DE | Access ET. / ET. GN. Problem / stolen batteries @ 0921_S_SK-AKRASH_3943DE / Clear after checking GN. | batt GN | Batteries Generator | batt | Batteries | 303886 | SK-AKRASH | C1_3943DE_PH15 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-21 20:31 | 2019-01-19 | TRUE
IM771019 | 3867DE | 2101_S_GH-NAWYA_3867DE | Main power / weak batteries | batt | Batteries | batt | Batteries | 324418 | GH-NAWYA | C1_3867DE_PH14 | (Batteries/Item(s) stolen/stolen) | 2019-09-21 22:46 | 2019-03-04 | TRUE
IM771047 | 0578DE | 0801_G_SK-QSASIN-AZHR_0578DE | main power/stolen Batteries @QSASIN-AZHR_0578DE/clear after power back | batt | Batteries | batt | Batteries | 335150 | PS-KHADIGA | C2_3413DE_PH13 | (Batteries/Item(s) stolen/missing batteries) | 2019-09-22 00:51 | 2019-05-20 | TRUE
IM771070 | 0605DE | 0041_S_DK-MAHMUDIYYA_0605DE | Main power @DK-MAHMUDIYYA_0605DE / stolen batteries | batt | Batteries | batt | Batteries | 304053 | DK-MAHMUDIYYA | C2_0605DE_PH9 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-22 02:10 | 2019-01-29 | TRUE
IM771115 | 0405RE | 03878_S_0405RE_RS-MRSA-NAKARI | ET DG Stopped , stolen batteries recovered once VDF DG fixed | batt DG | Batteries Generator | batt | Batteries | 356420 | 01_S_RS-MRSA-NAKARI_0405RE | C1_0405RE_PH15 | (Batteries/Some parts are (missing / stolen)/Batteries were stolen) | 2019-09-22 05:33 | 2019-09-26 | FALSE
IM771123 | 0242CA | 01963_S_0242CA_10TH-RSD2 | Outage power in factory located site , access PG , weak Backup Recovered once power restored | backup | Batteries | backup | Batteries | 356353 | 10TH-RSD2 | C4_0242CA_PH2 | (Batteries/Some parts are (missing / stolen)/Battery string stolen) | 2019-09-22 06:03 | 2019-09-21 | TRUE
IM771131 | 3429UP | 0901_D_QN-BELAD-ELMAL_3429UP | Due to PM generator with AP# C358757 , weak batteries , Recovered . | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 356495 | 01_G_QN-BELAD-ELMAL_3429UP | C1_3429UP_PH14 | (ATS / Engine/Unit earth/Gen enclosure earth cable is missing) (ATS / Engine/Components faulty/fuel level sensor not working and faulty (checked with zte team and it is not working )) (ATS / Engine/Components faulty/Gen enclosure battery is faulty) (ATS / Engine/Components faulty/ATS pressing keys were faulty and screen glass was broken) | 2019-09-22 07:07 | 2019-10-07 | FALSE
IM771153 | 3975DE | 0301_D_MF-SUKKARIYA_3975DE | Access VF Guard/VF GN problem/Stolen batteries/clear on P.G | batt GN | Batteries Generator | batt GN | Batteries Generator | 325093 | MF-SUKKARIYA | C2_3975DE_PH15 | (Batteries/Item(s) stolen/There is no battery for site) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cable has damaged protective isolation) | 2019-09-22 07:26 | 2019-05-09 | TRUE
IM771160 | 3594DE | 1241_S_BH-TAYRIYA_3594DE | main power/stolen Batteries /clear after power back | batt | Batteries | batt | Batteries | 325119 | BH-TAYRIYA | C1-3594DE-PH13 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-22 08:18 | 2019-05-12 | TRUE
IM771199 | 4021DE | 0181_S_BH-ABQAEEN_4021DE | Access VF / Main power / stolen batteries | batt | Batteries | batt | Batteries | 304224 | BH-ABQAEEN | C1_4021DE_PH15 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-21 03:43 | 2019-02-13 | TRUE
IM771216 | 4021DE | 0181_S_BH-ABQAEEN_4021DE | Access VF / Main power / stolen batteries | batt | Batteries | batt | Batteries | 304224 | BH-ABQAEEN | C1_4021DE_PH15 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-21 09:55 | 2019-02-13 | TRUE
IM771218 | 3368DE | 0201_S_BH-ABO-SHIQAF_3368DE | Access VF / Main power / stolen batteries | batt | Batteries | batt | Batteries | 324904 | BH-ABO-SHIQAF | C1_3368DE_PH12 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-21 09:55 | 2019-04-17 | TRUE
IM771275 | 3953DE | 0361_G_BH-MAARKA_3953DE | access ET/Main power/weak batteries clear on P.G | batt | Batteries | batt | Batteries | 304235 | BH-MAARKA | C1_3953DE_PH15 | (Batteries/Components faulty/Faulty battery and cable disconnected) | 2019-09-22 09:48 | 2019-02-14 | TRUE
IM771305 | 0070SI | 01_S_SS-SAINT-CATRN_0070SI | Power outage site has weak batteries and access PG problem recovered once power restored | batt | Batteries | batt | Batteries | 356151 | 01_S_SS-SAINT-CATRN_0070SI | C2_0070SI_PH2 | (Rectifiers/Alarms reporting to the OMC/rectifier major alarm appears ) | 2019-09-22 10:40 | 2019-08-27 | TRUE
IM771319 | 3199UP | 0641_S_AT-GANADLAH_3199UP | Due to EC power cutoff , stolen batteries , Recovered | batt | Batteries | batt | Batteries | 303847 | 01_S_AT-GANADLAH_3199UP | C2_3199UP_PH13 | (Batteries/Item(s) stolen/site Batteries were Stolen) | 2019-09-22 11:15 | 2019-01-15 | TRUE
IM771395 | 0405RE | 03878_S_0405RE_RS-MRSA-NAKARI | ET DG Stopped , New site without Backup recovered once VDF DG fixed | backup DG | Batteries Generator | backup | Batteries | 356420 | 01_S_RS-MRSA-NAKARI_0405RE | C1_0405RE_PH15 | (Batteries/Some parts are (missing / stolen)/Batteries were stolen) | 2019-09-22 12:47 | 2019-09-26 | FALSE
IM771418 | 3628DE | 0811_S_GH-QSR-BAGHDAD_3628DE | Main power / stolen batteries | batt | Batteries | batt | Batteries | 324836 | GH-QSR-BAGHDAD | C2_3628DE_PH13 | (Batteries/Item(s) stolen/Stolen batteries) | 2019-09-22 11:36 | 2019-04-15 | TRUE
IM771434 | 0459SI | 01_G_SS-RIVIERA_0459SI | DG Stopped , weak batteries caused site Down once DG Fix site recovered | batt DG | Batteries Generator | DG | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure ) (ATS / Engine/Wrong connection/generator battery as used in the site and not suitable in High temp) | 2019-09-22 12:55 | 2019-07-01 | TRUE
IM771444 | 0452AL | 2001_S_MIAMI-SBWY-RD2_0452AL | Main Power Problem / Weak Batteries / Auto Recovered | batt | Batteries | batt | Batteries | 303998 | S_MIAMI-SBWY-RD2_0452AL | C1_0452AL_PH9 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-22 12:19 | 2019-01-22 | TRUE
IM771455 | 3548DE | 1391_S_GH-SANADID_3548DE | main power problem /Stolen batteries/handel shatanouf west,,batanoun,birkit esab north ,denshway/clear on P.F | batt | Batteries | batt | Batteries | 325091 | GH-SANADID | C2_3548DE_PH16 | (Batteries/Item(s) stolen/No battery for site) | 2019-09-22 12:42 | 2019-05-09 | TRUE
IM771521 | 3534DE | 1641_D_SK-SANGAHA_3534DE | main power/weak batteries /clear on P.G | batt | Batteries | batt | Batteries | 335160 | SK-SANGAHA | C1-3534DE-PH13 | (Batteries/Components faulty/batteries are ballooned and have cracked.) (Batteries/Some parts are missing/batteries poles need cover.) | 2019-09-22 14:24 | 2019-05-21 | TRUE
IM771629 | 3037DE | 0301_D_DK-BAGALAT_3037DE | GN problem / Stolen batteries | batt GN | Batteries Generator | batt GN | Batteries Generator | 345376 | DK-BAGALAT | C3_3037DE_PH11 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) (ATS / Engine/Components faulty/Control module has faulty buttons.) (ATS / Engine/Wrong connection/Cable has bad connections and need replacement.) | 2019-09-22 17:32 | 2019-06-19 | TRUE
IM771631 | 3949DE | 0721_S_SK-ABO-ARABY_3949DE | access ET/ET owner/Guard switch MCB OFF/stolen batteries | batt | Batteries | batt | Batteries | 355738 | SK-ABO-ARABY | C01_3949DE_PH15 | (Batteries/Components faulty/Batteries can't carry site.) | 2019-09-22 17:53 | 2019-07-07 | TRUE
IM771654 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | VF Share / Main power / Stolen batteries | batt | Batteries | batt | Batteries | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | (Batteries/Item(s) stolen/Stolen) | 2019-09-22 21:35 | 2019-03-25 | TRUE
IM771675 | 0605DE | 0041_S_DK-MAHMUDIYYA_0605DE | Main power @DK-MAHMUDIYYA_0605DE / stolen batteries | batt | Batteries | batt | Batteries | 304053 | DK-MAHMUDIYYA | C2_0605DE_PH9 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-23 00:08 | 2019-01-29 | TRUE
IM771676 | 3400DE | 0731_S_GH-GHAZL-MAHLA_3400DE | Share VF / Main power / stolen batteries | batt | Batteries | batt | Batteries | 325111 | GH-GHAZL-MAHLA | C1_3400DE_PH12 | (Batteries/Item(s) stolen/Stolen Batteries) | 2019-09-23 00:08 | 2019-05-14 | TRUE
IM771697 | 3577UP | 2261_E_SG-NAZLET-ALI_3577UP | Generator problem, weak Batteries, solved. | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 304210 | 01_S_SG-NAZLET-ALI_3577UP | C1_3577UP_PH14 | (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Power cable not protected and missing power gland) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Battery cable not isolated) (ATS / Engine/Item(s) stolen/Gen Missing battery) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage around gen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage from gen) (ATS / Engine/Panorama pictures for each system/Panorama) | 2019-09-23 01:13 | 2019-02-13 | TRUE
IM771717 | 0490SI | 03534_S_0490SI_IS-NASR | Power outage site has weak batteries and access PG problem recovered once power restored | batt | Batteries | batt | Batteries | 356007 | 01_S_IS-NASR_0490SI | C2_0490SI_PH14 | (Rectifiers/Alarms reporting to the OMC/Rectifier alarm , A/C & door not apear on CAP) (Batteries/Components faulty/Battery voltag reading drop to 46 volt after we disconnect th rectifier C.B (Check the batteries)) | 2019-09-23 03:47 | 2019-08-07 | TRUE
IM771738 | 3664DE | 1741_E_GH-KFR-HASHAD_3664DE | GN problem / weak batteries | batt GN | Batteries Generator | batt | Batteries | 355453 | N_MILK-COMPANY_0251AL | C2_0251AL_PH3 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-23 04:02 | 2019-06-26 | TRUE
IM771755 | 3684UP | 0471_G_SG-KOUM-ELARAB_3684UP | Due to EC power cutoff, weak batteries , Recovered | batt | Batteries | batt | Batteries | 324483 | 01_G_SG-KOUM-ELARAB_3684UP | C1_3684UP_PH15 | (Batteries/Item(s) stolen/site batteries were Stolen) | 2019-09-23 07:28 | 2019-03-10 | TRUE
IM771842 | 0975UP | 0381_S_BS-MASID-ABYAD_0975UP_X | Due to EC power cutoff , Stolen batteries , Recovered | batt | Batteries | batt | Batteries | 356360 | 01_S_BS-MASID-ABYAD_0975UP | C1_0975UP_PH12 | (Rectifiers/Alarms reporting to the OMC/Minor alarm doesn't appear on the OMC) (Batteries/Some parts are (missing / stolen)/Batteries and cables are stolen) | 2019-09-23 08:52 | 2019-09-17 | TRUE
IM771844 | 0587DE | 0221_S_DK-KFR-KURDI_0587DE | share VF / Main power / stolen batteries | batt | Batteries | batt | Batteries | 324791 | DK-KFR-KURDI | C9_0587DE_PH09 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-23 09:13 | 2019-04-10 | TRUE
IM771849 | 3784DE | 0661_S_KS-DAQLIT_3784DE | share VF / Main power / weak batteries | batt | Batteries | batt | Batteries | 335221 | KS-DAQLIT | C3_3784DE_PH14 | (Batteries/Components faulty/Faulty battery (battearies are ballooned)) | 2019-09-23 09:19 | 2019-05-26 | TRUE
IM771895 | 3259DE | 0291_S_BH-ANAAM_3259DE | share VF / Main power / stolen batteries | batt | Batteries | batt | Batteries | 324534 | BH-ANAAM | C1_3259DE_PH12 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-23 10:36 | 2019-03-14 | TRUE
IM771896 | 0015RE | 00223_J_0015RE_SUKHNA-RD7 | DG Stopped , stolen batteries , recovered | batt DG | Batteries Generator | batt DG | Batteries Generator | 356250 | SUKHNA-RD7 | C2_0015RE_PH1 | (Batteries/Some parts are (missing / stolen)/Battery string stolen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage) (ATS / Engine/Unit earth/Earth cable disconnected) (ATS / Engine/Components faulty/Generator indicator broken & not work) (ATS / Engine/Components faulty/Ventilation fan not work) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Power cable has no terminal) | 2019-09-23 10:59 | 2019-09-09 | TRUE
IM771897 | 0906DE | 691_S_KS-ANTRA-BAIDA_0906DE | main power / weak batteries | batt | Batteries | batt | Batteries | 324828 | LU-GZRT-BAIRAT | C1_4211UP_PH19 | (Batteries/Item(s) stolen/Batteries were stolen) | 2019-09-23 10:34 | 2019-04-14 | TRUE
IM771902 | 0305UP | 01_S_AT-DEIR-MEHARA_0305UP | Due to EC power cutoff , weak batteries , PG Connected | batt | Batteries | batt | Batteries | 335158 | 01_S_AT-DEIR-MEHARA_0305UP | C1_0305UP_PH8 | (Batteries/Components faulty/Fire panel was switched off) | 2019-09-23 10:03 | 2019-05-18 | TRUE
IM771976 | 0498RE | 03500_S_0498RE_SZ-SELIM-HAY | VFE power outage , dead batteries , recovered once power restored | batt | Batteries | batt | Batteries | 345366 | 01_S_SZ-SELIM-HAY_0498RE | C1_0498RE_PH17 | (Batteries/Some parts are (missing / stolen)/Stolen battery) | 2019-09-23 11:27 | 2019-06-17 | TRUE
IM771992 | 3411UP | 0171_S_BS-DABAANA_3411UP_X | Due to EC power cutoff , weak batteries , PG Connected | batt | Batteries | batt | Batteries | 356314 | 01_S_BS-DABAANA_3411UP | C1_3411UP_PH14 | (Rectifiers/Alarms reporting to the OMC/Loop on the minor alarm in DDF) | 2019-09-23 11:15 | 2019-09-16 | TRUE
IM772046 | 0673DE | 0871_H_MF-SEDOD_0673DE | Power/battery under investigation/connect P.G | batt | Batteries | batt | Batteries | 304302 | MF-SEDOD | C1_0673DE_PH9 | (Batteries/Some parts are missing/Battery racks are placed directly under A/C IDU) | 2019-09-23 11:40 | 2019-02-21 | TRUE
IM772110 | 3830DE | 1311_S_BH-MHLT-KYL_3830DE | share VF / Main power / stolen batteries / PG handle another sites ( BH-KOM-DAFSHO_3803DE & BH-BARSIQ_3342DE ) | batt | Batteries | batt | Batteries | 356185 | BH-MHLT-KYL | C1_3830DE_PH14 | (Batteries/Some parts are (missing / stolen)/No battery for site) | 2019-09-23 12:47 | 2019-09-02 | TRUE
IM772115 | 0127DE | 0061_H_GH-MRO4-QUTUR_0127DE | Main power @ GH-MRO4-QUTUR_0127DE / stolen batteries / PG connected | batt | Batteries | batt | Batteries | 304205 | 9_S_GH-MR04-QUTUR_0127DE_SS00 | C4_0127DE_PH2 | (Batteries/Item(s) stolen/stolen batteries) | 2019-09-23 13:11 | 2019-02-14 | TRUE
IM772119 | 3394DE | 0011_S_B-SAFT-KHALED_3394DE | share VF / Main power / weak batteries | batt | Batteries | batt | Batteries | 304033 | BH-SAFT-KHALED | C1_3394DE_PH13 | (Batteries/Components faulty/Faulty battery) | 2019-09-23 12:56 | 2019-01-24 | TRUE
IM772197 | 3431DE | 0001_D_DM-NEW-DUMYAT6_3431DE | ET GN problem / batteries under check / connect PG | batt GN | Batteries Generator | batt GN | Batteries Generator | 335138 | DM-NEW-DUMYAT6 | C1_3431DE_PH13 | (Batteries/Some parts are missing/covers) (ATS / Engine/Components faulty/check genset) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) | 2019-09-23 14:22 | 2019-05-19 | TRUE
IM772205 | 0305UP | 01_S_AT-DEIR-MEHARA_0305UP | Due to EC power cutoff , weak batteries, PG Connected | batt | Batteries | batt | Batteries | 335158 | 01_S_AT-DEIR-MEHARA_0305UP | C1_0305UP_PH8 | (Batteries/Components faulty/Fire panel was switched off) | 2019-09-23 14:35 | 2019-05-18 | TRUE
IM772253 | 0037SI | 01_H_SS-LIBEIRIQ_0037SI | DG Stopped , weak batteries caused site Down once DG Fix site recovered | batt DG | Batteries Generator | DG | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | (ATS / Engine/Components faulty/Burnet ATS terminals) (ATS / Engine/Components faulty/Defected genset battery) (ATS / Engine/Components faulty/Broken control panel screen) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Bad fixation of fuel hose) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Bad termination of ATS panel) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Bad termination of charging system) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Genset oil & fuel leakage) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure ) (ATS / Engine/Wrong connection/generator battery as used in the site and not suitable in High temp) | 2019-09-23 16:01 | 2019-07-01 | TRUE
IM772272 | 0498RE | 03500_S_0498RE_SZ-SELIM-HAY | VFE power outage , dead batteries , recovered once power restored | batt | Batteries | batt | Batteries | 345366 | 01_S_SZ-SELIM-HAY_0498RE | C1_0498RE_PH17 | (Batteries/Some parts are (missing / stolen)/Stolen battery) | 2019-09-23 16:11 | 2019-06-17 | TRUE
IM772279 | 0278CA | 02185_N_0278CA_ABBOUD | down due to power probelm @ 0278CA_ABBOUD and battery weak | batt | Batteries | batt | Batteries | 304055 | ABBOUD | C1_0278CA_PH3 | (Batteries/Item(s) stolen/Batteries and cables are stolen) | 2019-09-23 16:13 | 2019-01-29 | TRUE
IM772288 | 3499UP | 1871_S_AS-GAFAR-SADK_3499UP_X | Main Power Disconenction,Stolen Batteries, Autorecovered. | batt | Batteries | batt | Batteries | 356189 | 01_S_AS-GAFAR-SADK_3499UP | C1_3499UP_PH14 | (Batteries/Some parts are (missing / stolen)/Site Batteries were stolen) | 2019-09-23 16:12 | 2019-09-03 | TRUE
IM772313 | 3181DE | 03323_D_3181DE_QL-QALIUB-RLWY | GN problem/battery under invistigation/clear after check GN | batt GN | Batteries Generator | batt GN | Batteries Generator | 303916 | QL_QALIUB_RLWY _3181DE_SSS0 | C1_3181DE_PH12 | (Batteries/Item(s) stolen/stolen batteries) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM organization/arrange) | 2019-09-23 17:23 | 2019-01-20 | TRUE
IM772336 | 0734DE | 0441_D_MF-TANTA-HW1_0734DE | GN problem / Stolen batteries | batt GN | Batteries Generator | batt GN | Batteries Generator | 356142 | MF-TANTA-HW1 | C1_0734DE_PH9 | (Rectifiers/Alarms reporting to the OMC/Site has fake power alarm) (Batteries/Some parts are (missing / stolen)/There is no battery for site) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has leakage) | 2019-09-23 17:23 | 2019-08-27 | TRUE
IM772352 | 3275DE | 1151_S_QL-DEER-2_3275DE | Main power/weak battery@ QL-DEER-2_3275DE/clear after power back | batt | Batteries | batt | Batteries | 356318 | QL-DEER-2 | C1_3275DE_PH12 | (Rectifiers/Alarms reporting to the OMC/Alarm cable disconnected (Alarms not appear at OMC)) (Batteries/Components faulty/Faulty battaries) | 2019-09-23 18:46 | 2019-09-15 | TRUE
IM772363 | 3555CA | 00042_L_3555CA_SAMA-TOWER | down due to DG problem and no backup (MA) | backup DG | Batteries Generator | backup DG | Batteries Generator | 345256 | SAMA-TOWER | C2_3555CA_PH13 | (Batteries/Some parts are missing/missing batteries) (ATS / Engine/Wrong connection/welded cables) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage) | 2019-09-23 20:01 | 2019-05-25 | TRUE
IM772476 | 0581DE | 1571_S_SK-IKYAD-BHARIA_0581DE | Main power/stolen battery@SK-IKYAD-BHARIA_0581DE/clear on P.G | batt | Batteries | batt | Batteries | 324498 | SK-IKYAD-BHARIA | C1_0581DE_PH9 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-24 08:33 | 2019-03-13 | TRUE
IM772479 | 3489DE | 0461_S_DK-KFR-GHANNAM_3489DE | Main power/stolen battery/clear after power back | batt | Batteries | batt | Batteries | 325088 | DK-KFR-GHANNAM | C1-3489DE-PH13 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-24 08:35 | 2019-05-09 | TRUE
IM772492 | 3499UP | 1871_S_AS-GAFAR-SADK_3499UP_X | Main Power Disconnection, weak batteries, PG Connected. | batt | Batteries | batt | Batteries | 356189 | 01_S_AS-GAFAR-SADK_3499UP | C1_3499UP_PH14 | (Batteries/Some parts are (missing / stolen)/Site Batteries were stolen) | 2019-09-24 07:31 | 2019-09-03 | TRUE
IM772520 | 3895DE | 0401_S_BH-KFR-ZYADA_3895DE | Share VF / VG GN problem / stolen batteries | batt GN | Batteries Generator | batt | Batteries | 324442 | BH-KFR-ZYADA | C1_3895DE_PH14 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-24 09:37 | 2019-03-07 | TRUE
IM772531 | 0156UP | 01_J_GIZA-LUXOR-25_0156UP | Generator problem, weak Batteries, solved. | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | (ATS / Engine/Components faulty/Gen enclosure battery was faulty) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM organization/ATS cables need organization) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Loose neutral cable) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Two cables inserted in one slot and not teminated can cause bad connections) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage inside Gen enclosure) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage) (ATS / Engine/Panorama pictures for each system/Last gen hour meter at Audit G ( 6762 )) (ATS / Engine/Panorama pictures for each system/Panorama site view in outside site) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure ) (ATS / Engine/Wrong connection/generator battery as used in the site and not suitable in High temp) | 2019-09-24 09:02 | 2019-07-01 | TRUE
IM772563 | 3628DE | 0811_S_GH-QSR-BAGHDAD_3628DE | main power / stolen batteries / PG connected | batt | Batteries | batt | Batteries | 324836 | GH-QSR-BAGHDAD | C2_3628DE_PH13 | (Batteries/Item(s) stolen/Stolen batteries) | 2019-09-24 09:51 | 2019-04-15 | TRUE
IM772564 | 3124UP | 1761_S_AS-SILWA-BHRY_3124UP_X | Main Power Disconnection, Stolen Batteries, Autorecovered. | batt | Batteries | batt | Batteries | 355937 | 01_S_AS-SILWA-BHRY_3124UP | C1_3124UP_PH13 | (Rectifiers/Alarms reporting to the OMC/Rectifer minor alarm is not appeared on the omc and looped) | 2019-09-24 10:06 | 2019-08-01 | TRUE
IM772575 | 3394DE | 0011_S_B-SAFT-KHALED_3394DE | Share VF / main power / weak batteries / PG connected | batt | Batteries | batt | Batteries | 304033 | BH-SAFT-KHALED | C1_3394DE_PH13 | (Batteries/Components faulty/Faulty battery) | 2019-09-24 10:24 | 2019-01-24 | TRUE
IM772605 | 0391RE | 03496_S_0391RE_SZ-AAMER | Power outage site has weak batteries and access PG problem recovered once power restored | batt | Batteries | batt | Batteries | 356056 | 01_S_SZ-AAMER_0391RE | C1_0391RE_PH15 | (Rectifiers/Alarms reporting to the OMC/Rectifier major alarm not report the OMC & Cable looped in DDF) | 2019-09-24 11:23 | 2019-08-19 | TRUE
IM772619 | 0238RE | 03882_S_0238RE_RS-RSRT-GHALEB | Power outage site has weak batteries and access PG problem recovered once power restored | batt | Batteries | batt | Batteries | 355503 | 01_S_RS-RSRT-GHALEB_0238RE | C2_0238RE_PH9 | (Rectifiers/Alarms reporting to the OMC/Rectifer alarm not appeared on the omc ( looped at ddf rack alarm not connected at ddf )) (Rectifiers/Alarms reporting to the OMC/Rectifer alarm not appeared on the omc ( looped at ddf rack alarm not connected at ddf )) (Batteries/Components faulty/Batteries were faulty ( explosion )) | 2019-09-24 11:11 | 2019-06-26 | TRUE
IM772623 | 0638UP | 0491_G_QN-MOSALA_0638UP | Genertaor problem, stolen Batteries, solved. | batt Gen | Batteries Generator | batt Gen | Batteries Generator | 324745 | 01_G_QN-MOSALA_0638UP | C4_0638UP_PH9 | (Batteries/Item(s) stolen/Batteries were stolen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage beside enclosure by Vodafone ) | 2019-09-24 11:10 | 2019-04-04 | TRUE
IM772653 | 3076DE | 0321_S_DK-MIT-ASEM_3076DE | Share VF / Main power / stolen batteries | batt | Batteries | batt | Batteries | 324790 | DK_Mit_Asem | C1_3076DE_PH11 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-24 10:59 | 2019-04-10 | TRUE
IM772658 | 0576DE | 1611_G_BH-WAFAIYYA_0576DE | Main power / stolen batteries | batt | Batteries | batt | Batteries | 324440 | BH-WAFAIYYA | C2_0576DE_PH9 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-24 11:15 | 2019-03-07 | TRUE
IM772660 | 3344DE | 0681_S_BH-ELNEGILY_3344DE | Access VF / Main power /VF Guard switched off MCB / stolen batteries | batt | Batteries | batt | Batteries | 304214 | BH-ELNEGILY | C3_3344DE_PH12 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-24 11:29 | 2019-02-12 | TRUE
IM772690 | 0305UP | 01_S_AT-DEIR-MEHARA_0305UP | Due to EC power cutoff , weak batteries , PG Connected | batt | Batteries | batt | Batteries | 335158 | 01_S_AT-DEIR-MEHARA_0305UP | C1_0305UP_PH8 | (Batteries/Components faulty/Fire panel was switched off) | 2019-09-24 11:53 | 2019-05-18 | TRUE
IM772692 | 3873UP | 671_S_LU-TIBA-CITY-2_3873UP | Generator problem, weak Batteries, solved. | batt Gen generator | Batteries Generator Generator | batt Gen generator | Batteries Generator | 324438 | LU-TIBA-CITY-2 | C1_3873UP_PH15 | (Batteries/Item(s) stolen/Batteries were stolen) (Batteries/Item(s) stolen/Batteries were stolen ( missing )) (ATS / Engine/Wrong connection/Main cables were welded inside ATS panel) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM wrong penetration/Wrong penetration for power cables) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Two cables inserted in one slot can cause bad connections) (ATS / Engine/Item(s) stolen/Gen Battery is missing) (ATS / Engine/Panorama pictures for each system/Last Gen hour meter at hour meter at Audit G ( 5751 )) (ATS / Engine/Panorama pictures for each system/Panorama site view in outside site) | 2019-09-24 12:12 | 2019-03-07 | TRUE
IM772780 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | batt Gen generator | Batteries Generator Generator | batt Gen generator | Batteries Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | (Batteries/Item(s) stolen/Batteries were stolen) (ATS / Engine/Wrong connection/external cable to the guard connected from gen and not protected) (ATS / Engine/Wrong connection/One Contactor turned on by setting wood inside it) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cables not protected in tube) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cables not protected) (ATS / Engine/Item(s) stolen/Gen battery is missing) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/ Fuel leakage inside Gen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage inside Gen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage beisde Gen enclosure area need cleaning) (ATS / Engine/Panorama pictures for each system/Open gland in Gen enclosure need insulation) (ATS / Engine/Panorama pictures for each system/Panorama site view in outside site) (ATS / Engine/Panorama pictures for each system/Last Gen hour meter at Audit G ( 31148 )) | 2019-09-24 13:14 | 2019-01-16 | TRUE
IM772813 | 0736CA | 02118_D_0736CA_PETROL-PIPELINS | down due to DG filter problem and stolen batteries | batt DG | Batteries Generator | batt DG | Batteries Generator | 356154 | PETROL-PIPELINS | C2_0736CA_PH9 | (Batteries/Some parts are (missing / stolen)/Batteries and cables are stolen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Signs of oil and fuel leakage arround the genset) (ATS / Engine/Unit earth/Stolen earth connections of the ATS panel) (ATS / Engine/Components faulty/White exhaust of the engine) (ATS / Engine/Wrong connection/Wrong connections of cables connected to the ATS trans.) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Missing terminals of power cables connected to the ATS contactors) | 2019-09-24 14:23 | 2019-08-26 | TRUE
IM772869 | 0421DE | 0721_H_MF-MANSH-SOLTN_0421DE | Main power/battery under investigation/clear after power back | batt | Batteries | batt | Batteries | 304300 | MF-MANSH-SOLTN | C1_0421DE_PH4 | (Batteries/Some parts are missing/Battery racks are placed directly under A/C IDU) | 2019-09-24 15:15 | 2019-02-21 | TRUE
IM772910 | 3548DE | 1391_S_GH-SANADID_3548DE | Main power/stolen battery/clear on P.G | batt | Batteries | batt | Batteries | 325091 | GH-SANADID | C2_3548DE_PH16 | (Batteries/Item(s) stolen/No battery for site) | 2019-09-24 15:54 | 2019-05-09 | TRUE
IM772960 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN problem/stolen battery/clear after check GN | batt GN | Batteries Generator | batt GN | Batteries Generator | 324500 | SK-AZZAZI | C1_4029DE_PH15 | (Batteries/Item(s) stolen/No backup batteries.) (ATS / Engine/Wrong connection/Some cables are disconnected and need adjust.) (ATS / Engine/Panorama pictures for each system/Generator battery poles need cleaning, wax and covers.) (ATS / Engine/Panorama pictures for each system/Overview.) | 2019-09-24 18:35 | 2019-03-13 | TRUE
IM772962 | 3037DE | 0301_D_DK-BAGALAT_3037DE | ET Share / GN stopped / Stolen batteries | batt GN | Batteries Generator | batt GN | Batteries Generator | 345376 | DK-BAGALAT | C3_3037DE_PH11 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) (ATS / Engine/Components faulty/Control module has faulty buttons.) (ATS / Engine/Wrong connection/Cable has bad connections and need replacement.) | 2019-09-24 18:48 | 2019-06-19 | TRUE
IM772997 | 3955DE | 0731_S_SK-QRMT-SAHBRA_3955DE | access ET/ET GN problem/Stolen batteries | batt GN | Batteries Generator | batt | Batteries | 356230 | SK-QRMT-SAHBRA | C1_3955DE_PH15 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-24 22:49 | 2019-09-07 | TRUE
IM773002 | 0615AL | 1381_S_NZHA-TERMINAL_0615AL | Down Due To Main Power Cutoff / Weak Batteries / On Air After Main Power Auto Recovered | batt | Batteries | batt | Batteries | 356028 | MF-TELYA | C4_0674DE_PH09 | (Rectifiers/Alarms reporting to the OMC/Site down due to power during visite (Check alarms with OMC with capture)) | 2019-09-24 23:29 | 2019-08-06 | TRUE
IM773004 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/stolen battery/clear after check GN | batt GN | Batteries Generator | batt GN | Batteries Generator | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | (Batteries/Some parts are missing/Battery cabinet need cleaning (from inside) and holes need sealing.) (Batteries/Some parts are missing/Batteries poles need have missing covers.) (ATS / Engine/Components faulty/Generator has bad performance and need overall.) (ATS / Engine/Panorama pictures for each system/Overview.) | 2019-09-25 00:14 | 2019-05-21 | TRUE
IM773030 | 0070SI | 01_S_SS-SAINT-CATRN_0070SI | Power outage site has weak batteries and access PG problem recovered once power restored | batt | Batteries | batt | Batteries | 356151 | 01_S_SS-SAINT-CATRN_0070SI | C2_0070SI_PH2 | (Rectifiers/Alarms reporting to the OMC/rectifier major alarm appears ) | 2019-09-25 05:04 | 2019-08-27 | TRUE
IM773054 | 0509SI | U_S_0509SI_IS-NEW-MAHSAMA | Power outage , site has weak batteries must replace with another new team moved with PG , before arrive site recovered once power restored | batt | Batteries | batt | Batteries | 356269 | 01_S_IS-NEW-MAHSAMA_0509SI | C1_0509SI_PH15 | (Batteries/Some parts are (missing / stolen)/Battery string stolen) | 2019-09-25 06:02 | 2019-09-11 | TRUE
IM773103 | 0983DE | 1771_S_DK-MIT-ANTAR_0983DE | H.T alarm / BTS hanging | H.T | A/Cs | H.T | A/Cs | 324896 | DK-MIT-ANTAR | C8_0983DE_PH11 | (A/Cs Cooling / Free Cooling / Ventilation/Components faulty/faulty , need to rest it control each time to work) | 2019-09-25 06:39 | 2019-04-14 | TRUE
IM773105 | 0498CA | 01846_S_0498CA_GHAMRA | down due to power failure and weak batteries and auto restored(M) | batt | Batteries | batt | Batteries | 324428 | GHAMRA | C2_0498CA_PH4 | (Batteries/Some parts are missing/Missing hoods of batteries) | 2019-09-25 07:02 | 2019-03-07 | TRUE
IM773125 | 3594DE | 1241_S_BH-TAYRIYA_3594DE | main power/Stolen batteries/clear on PG | batt | Batteries | batt | Batteries | 325119 | BH-TAYRIYA | C1-3594DE-PH13 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-25 07:10 | 2019-05-12 | TRUE
IM773198 | 0070UP | 01_J_QN-HAMMADI-NTH_0070UP | Generator problem, weak Batteries, TV station access problem | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure ) (ATS / Engine/Wrong connection/generator battery as used in the site and not suitable in High temp) | 2019-09-25 09:08 | 2019-07-01 | TRUE
IM773204 | 0456UP | 02_S_QN-TOWAYRAT_0456UP | Main power disconnection ,batteries are suspected to be weak , P.G connected | batt | Batteries | batt | Batteries | 356277 | 01_S_QN-TOWAYRAT_0456UP | C1_0456UP_PH9 | (Rectifiers/Alarms reporting to the OMC/Alarm was exists on rectifier control panel and appeared on the Omc to) | 2019-09-25 09:15 | 2019-09-11 | TRUE
IM773335 | 3368DE | 0201_S_BH-ABO-SHIQAF_3368DE | Access VF / Main power / stolen batteries / PG handle anther sites ( BH-ABO-REESH_3064DE & BH-SHUBRA-NUNA_0048DE ) | batt | Batteries | batt | Batteries | 324904 | BH-ABO-SHIQAF | C1_3368DE_PH12 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-25 10:38 | 2019-04-17 | TRUE
IM773351 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Main power / stolen batteries | batt | Batteries | batt | Batteries | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | (Batteries/Item(s) stolen/Stolen) | 2019-09-25 10:55 | 2019-03-25 | TRUE
IM773442 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem and battery stolen and PG access | batt DG | Batteries Generator | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | (Batteries/Some parts are (missing / stolen)/missing battereis) | 2019-09-25 13:40 | 2019-08-14 | TRUE
IM773470 | 3110DE | 1681_D_GH-SHUBRA-RIS_3110DE | Share VF / VF GN problem @ GH-SHUBRA-RIS_3110DE / weak batteries | batt GN | Batteries Generator | GN | Generator | 324613 | GH-SHUBRA-RIS | C1_3110DE_PH12 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) | 2019-09-25 13:32 | 2019-03-25 | TRUE
IM773472 | 0350DE | 1271_Q_BH-BADR_0350DE | access guard/GN problem/batteries under investigation@BH-BADR_0350DE | batt GN | Batteries Generator | GN | Generator | 304087 | BH-BADR | C3_0350DE_PH4 | (ATS / Engine/Components below rate (excluding main power feeder if not hot)/Generator voltage is high) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM organization/Disconnected cables) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM wrong penetration/CB need fixation) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminals requried) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Burned terminal // Terminals at 1 slot) | 2019-09-25 13:39 | 2019-01-30 | TRUE
IM773522 | 3492CA | 00879_D_3492CA_REHAB-G17 | down due to DG problem and battery stolen and PG accessed | batt DG | Batteries Generator | batt DG | Batteries Generator | 314391 | REHAB-G17 | C1_3492CA_PH13 | (Batteries/Some parts are missing/missing batteries) (ATS / Engine/Wrong connection/wrong connection) | 2019-09-25 15:40 | 2019-02-26 | TRUE
IM773561 | 0993UP | 0041_S_AT-ELOUNA_0993UP | Due to EC power cutoff , Weak batteries , PG Connected | batt | Batteries | batt | Batteries | 355474 | 01_S_AT-ELOUNA_0993UP | C1_0993UP_PH12 | (Rectifiers/Alarms reporting to the OMC/Power alarm not appeared on the omc) | 2019-09-25 15:44 | 2019-06-26 | TRUE
IM773630 | 3575DE | 1701_S_BH-NKHLA-BHRYA_3575DE | Main power / batteries under check | batt | Batteries | batt | Batteries | 356088 | BH-NKHLA-BHRYA | C1_3575DE_PH13 | (Batteries/Components faulty/Battery CBs off) | 2019-09-25 20:04 | 2019-08-20 | TRUE
IM773769 | 3290DE | 1171_D_MF-QATTA_3290DE | acess Guard/GN problem /Good batteries/clear after check GN | batt GN | Batteries Generator | GN | Generator | 355961 | MF-QATTA | C3_3290DE_PH12 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has leakage) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminals requried) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Cable need to be terminated well) | 2019-09-26 05:39 | 2019-08-03 | TRUE
IM773787 | 0633AL | B_ALEX-WST-1_1_33866_G | gen problem / stolen batteries / solved . | batt Gen | Batteries Generator | batt Gen | Batteries Generator | 355459 | ALEX-WST-1 | C1_0633AL_PH13 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator and its area has a lot of leakage.) | 2019-09-25 17:37 | 2019-06-27 | TRUE
IM773799 | 3436UP | 1071_S_MN-MYANA-WAQF_3436UP | Due to Generator problem , weak batteries , Recovered | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 324959 | 01_S_MN-MYANA-WAQF_3436UP | C2_3436UP_PH14 | (ATS / Engine/Wrong connection/Gen working without control and protection) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Battery cables not isolated) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage around Gen set from ET) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage from oil filler cap) | 2019-09-26 06:36 | 2019-04-25 | TRUE
IM773831 | 0673DE | 0871_H_MF-SEDOD_0673DE | main power/Batteries under investigation/clear after connect P.G | batt | Batteries | batt | Batteries | 304302 | MF-SEDOD | C1_0673DE_PH9 | (Batteries/Some parts are missing/Battery racks are placed directly under A/C IDU) | 2019-09-26 07:38 | 2019-02-21 | TRUE
IM773855 | 4021DE | 0181_S_BH-ABQAEEN_4021DE | Access VF / Main power / stolen batteries / PG handle anther sites ( BH-ABO-REESH_3064DE & BH-SHUBRA-NUNA_0048DE ) | batt | Batteries | batt | Batteries | 304224 | BH-ABQAEEN | C1_4021DE_PH15 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-25 10:38 | 2019-02-13 | TRUE
IM773880 | 3628DE | 0811_S_GH-QSR-BAGHDAD_3628DE | BTS problem / Down after AP 358492 / O&M disconnected / then Main power / Stolen batteries / PG connected | batt | Batteries | batt | Batteries | 324836 | GH-QSR-BAGHDAD | C2_3628DE_PH13 | (Batteries/Item(s) stolen/Stolen batteries) | 2019-09-26 08:00 | 2019-04-15 | TRUE
IM773912 | 3955DE | 0731_S_SK-QRMT-SAHBRA_3955DE | Access ET. / ET. GN. Problem / stolen batteries / clear after checking ET. GN. | batt GN | Batteries Generator | batt | Batteries | 356230 | SK-QRMT-SAHBRA | C1_3955DE_PH15 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-26 08:46 | 2019-09-07 | TRUE
IM773916 | 0456UP | 02_S_QN-TOWAYRAT_0456UP | main Power Disconnection, weak Batteries, PG Connected. | batt | Batteries | batt | Batteries | 356277 | 01_S_QN-TOWAYRAT_0456UP | C1_0456UP_PH9 | (Rectifiers/Alarms reporting to the OMC/Alarm was exists on rectifier control panel and appeared on the Omc to) | 2019-09-26 09:02 | 2019-09-11 | TRUE
IM773934 | 0975UP | 0381_S_BS-MASID-ABYAD_0975UP_X | Due to EC power cutoff , Stolen batteries , PG Connected | batt | Batteries | batt | Batteries | 356360 | 01_S_BS-MASID-ABYAD_0975UP | C1_0975UP_PH12 | (Rectifiers/Alarms reporting to the OMC/Minor alarm doesn't appear on the OMC) (Batteries/Some parts are (missing / stolen)/Batteries and cables are stolen) | 2019-09-26 09:38 | 2019-09-17 | TRUE
IM773939 | 3895DE | 0401_S_BH-KFR-ZYADA_3895DE | Share VF / VF GN problem / stolen batteries | batt GN | Batteries Generator | batt | Batteries | 324442 | BH-KFR-ZYADA | C1_3895DE_PH14 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-26 09:06 | 2019-03-07 | TRUE
IM773940 | 0674DE | 1381_S_MF-TELYA_0674DE | Access VF. / main power/ batteries under investigation @ L_G_MF-TELYA_0674DE/ clear on PG. | batt | Batteries | batt | Batteries | 356028 | MF-TELYA | C4_0674DE_PH09 | (Rectifiers/Alarms reporting to the OMC/Site down due to power during visite (Check alarms with OMC with capture)) | 2019-09-26 09:17 | 2019-08-06 | TRUE
IM773987 | 4081DE | 0521_D_GH-KAFR-DIMA_4081DE | Share VF / VF GN problem / stolen batteries | batt GN | Batteries Generator | batt GN | Batteries Generator | 324614 | GH-KAFR-DIMA | C2_4081DE_PH15 | (Batteries/Item(s) stolen/Stolen) (ATS / Engine/Item(s) stolen/missing battery) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/leakage) | 2019-09-26 10:17 | 2019-03-25 | TRUE
IM773993 | 3414UP | 0401_S_BS-AHWA_3414UP_X | Due to EC power cutoff , weak batteries , PG Connected | batt | Batteries | batt | Batteries | 356350 | 01_S_BS-AHWA_3414UP | C1_3414UP_PH14 | (Rectifiers/Alarms reporting to the OMC/Loop on the major alarm in DDF) (Batteries/Components faulty/Batteries are faulty and site is down after less than one hour of power disconnected) | 2019-09-26 10:31 | 2019-09-17 | TRUE
IM773995 | 3836DE | 0661_S_SK-HAGARSA_3836DE | Main Power / Stolen batteries @ 0661_S_SK-HAGARSA_3836DE / Clear after Power back | batt | Batteries | batt | Batteries | 345237 | SK-HAGARSA | C1-3836DE-PH14 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-26 10:38 | 2019-06-03 | TRUE
IM774051 | 4029DE | 0451_D_SK-AZZAZI_4029DE | GN. problem / stolen batteries / clear after checking GN. | batt GN | Batteries Generator | batt GN | Batteries Generator | 324500 | SK-AZZAZI | C1_4029DE_PH15 | (Batteries/Item(s) stolen/No backup batteries.) (ATS / Engine/Wrong connection/Some cables are disconnected and need adjust.) (ATS / Engine/Panorama pictures for each system/Generator battery poles need cleaning, wax and covers.) (ATS / Engine/Panorama pictures for each system/Overview.) | 2019-09-26 11:08 | 2019-03-13 | TRUE
IM774065 | 3044CA | 02884_I_3044CA_MASAKEN-ALEX2 | down due to DG relay problem & weak batteries (T) | batt DG | Batteries Generator | DG | Generator | 324659 | MASAKEN-ALEX2 | C1_3044CA_PH09 | (ATS / Engine/Wrong connection/wrong connections) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/floating hoses) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/unprotected cable) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage) | 2019-09-26 11:56 | 2019-03-26 | TRUE
IM774069 | 3096DE | 02891_G_3096DE_OBOUR-DST6 | down due to DG fuel filter problem & no backup (T) | backup DG | Batteries Generator | DG | Generator | 345263 | OBOUR-DST6 | C1_3096DE_PH12 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage) | 2019-09-26 11:46 | 2019-05-27 | TRUE
IM774090 | 4211UP | 691_OO_LU-GZRT-BAIRAT_4211UP | main Power Disconnection, weak Batteries, Autorcovered. | batt | Batteries | batt | Batteries | 324828 | LU-GZRT-BAIRAT | C1_4211UP_PH19 | (Batteries/Item(s) stolen/Batteries were stolen) | 2019-09-26 12:25 | 2019-04-14 | TRUE
IM774120 | 0371SI | 01_G_SS-RAMADA-SEDR_0371SI | DG Stopped , weak batteries caused site Down once DG Fix site recovered | batt DG | Batteries Generator | batt DG | Batteries Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | (Batteries/Some parts are (missing / stolen)/Battery string stolen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage) (ATS / Engine/Components faulty/Generator battery defected) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure ) (ATS / Engine/Wrong connection/generator battery as used in the site and not suitable in High temp) | 2019-09-26 12:57 | 2019-07-01 | TRUE
IM774138 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem & no backup & access VF (T) | backup DG | Batteries Generator | backup | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | (Batteries/Some parts are (missing / stolen)/missing battereis) | 2019-09-26 13:16 | 2019-08-14 | TRUE
IM774152 | 0587DE | 0221_S_DK-KFR-KURDI_0587DE | VF Share / Main power / Stolen batteries | batt | Batteries | batt | Batteries | 324791 | DK-KFR-KURDI | C9_0587DE_PH09 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-26 12:38 | 2019-04-10 | TRUE
IM774163 | 0305UP | 01_S_AT-DEIR-MEHARA_0305UP | Due to EC power cutoff , weak batteries , PG Connected | batt | Batteries | batt | Batteries | 335158 | 01_S_AT-DEIR-MEHARA_0305UP | C1_0305UP_PH8 | (Batteries/Components faulty/Fire panel was switched off) | 2019-09-26 13:40 | 2019-05-18 | TRUE
IM774164 | 3867DE | 2101_S_GH-NAWYA_3867DE | Main power / Weak batteries / BDT @ 22/05/2019 Is: 0.00 | batt | Batteries | batt | Batteries | 324418 | GH-NAWYA | C1_3867DE_PH14 | (Batteries/Item(s) stolen/stolen) | 2019-09-26 13:23 | 2019-03-04 | TRUE
IM774166 | 0305UP | 01_S_AT-DEIR-MEHARA_0305UP | Due to EC power cutoff , weak batteries , PG Connected | batt | Batteries | batt | Batteries | 335158 | 01_S_AT-DEIR-MEHARA_0305UP | C1_0305UP_PH8 | (Batteries/Components faulty/Fire panel was switched off) | 2019-09-26 13:40 | 2019-05-18 | TRUE
IM774183 | 3794UP | 02_E_QN-ELQUBIBAH_3794UP | Generator problem, weak Batteries, MW E/// hanged after restore power, MMU reset HW and replaced Ethernet Cable between Link&BTS. | batt Gen generator | Batteries Generator Generator | batt Gen generator | Batteries Generator | 356303 | 01_S_QN-ELQUBIBAH_3794UP | C4_3794UP_PH15 | (Rectifiers/Alarms reporting to the OMC/Rectifier minor alarm was looped at ddf ) (Batteries/Components faulty/Batteries were faulty ( exploded )) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage from etisalat Gen) (ATS / Engine/Unit earth/Gen enclosure earth cable is not connected) (ATS / Engine/Components faulty/ radiator is defected and connected with extranl water source) (ATS / Engine/Components faulty/Gen battey is defected and need new one) (ATS / Engine/Components faulty/ATS pressing keys and Knob were defected) (ATS / Engine/Wrong connection/Two cables inserted in one slot and not teminated can cause bad connections ) (Batteries/Some parts are (missing / stolen)/One of Batteries string was stolen) (ATS / Engine/Unit earth/Gen enclosure earth cable is missing) (ATS / Engine/Components faulty/Gen battery is faulty) (ATS / Engine/Components faulty/Gen battery is faulty) (ATS / Engine/Alarms on equipment (excluding ADM)/Gen has alarm) | 2019-09-25 18:25 | 2019-09-12 | TRUE
IM774221 | 0648DE | 0381_S_BH-IZ-HUSNI_0648DE | Main power / Stolen batteries | batt | Batteries | batt | Batteries | 355857 | BH-IZ-HUSNI | C1_0648DE_PH9 | (Batteries/Some parts are (missing / stolen)/stolen batteries) | 2019-09-26 14:06 | 2019-07-22 | TRUE
IM774244 | 0081SI | 01_H_SS-TABA-MARINA-BR_0081SI | Power outage site has weak batteries and access PG problem recovered once power restored | batt | Batteries | batt | Batteries | 324756 | 01_H_SS-TABA-MARINA-BR_0081SI | C2_0081SI_PH2 | (Batteries/Components faulty/defected battery ( string not connected )) | 2019-09-26 14:36 | 2019-04-07 | TRUE
IM774265 | 3894CA | 02231_S_3894CA_REHAB-STAGE7 | down due to VF DG problem & stolen batteries & access VF (T) | batt DG | Batteries Generator | batt | Batteries | 356204 | REHAB-STAGE7 | C1_3894CA_PH17 | (Batteries/Some parts are (missing / stolen)/missing batteries) | 2019-09-26 15:40 | 2019-08-14 | TRUE
IM774306 | 0967DE | 0111_D_MF-MAWKEF-2_0967DE | access owner/GN problem/weak batteries | batt GN | Batteries Generator | GN | Generator | 335176 | MF-MAWKEF-2 | C2_0967DE_PH11 | (ATS / Engine/Wrong connection/Wrong connection (Cables uninstalled inside CB)) | 2019-09-26 17:56 | 2019-05-19 | TRUE
IM774359 | 3755DE | 0951_Q_SK-SHARSHIMA_3755DE | GN problem/ batteries under investigation@SK-SHARSHIMA_3755DE/ | batt GN | Batteries Generator | GN | Generator | 304145 | SK-SHARSHIMA | C6_3755DE_PH14 | (ATS / Engine/Components faulty/Generator has alarm (although it is working)) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has oil leakage and its oil seal need adjust and repair.) (ATS / Engine/Panorama pictures for each system/Overview.) | 2019-09-26 23:48 | 2019-02-09 | TRUE
IM774394 | 3755DE | 0951_Q_SK-SHARSHIMA_3755DE | GN problem/ batteries under investigation@SK-SHARSHIMA_3755DE/clear on pg but it cannot carry all loads | batt GN | Batteries Generator | GN | Generator | 304145 | SK-SHARSHIMA | C6_3755DE_PH14 | (ATS / Engine/Components faulty/Generator has alarm (although it is working)) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Generator has oil leakage and its oil seal need adjust and repair.) (ATS / Engine/Panorama pictures for each system/Overview.) | 2019-09-27 04:53 | 2019-02-09 | TRUE
IM774400 | 3299DE | 0541_S_KS-ZAAFRAN_3299DE | Share VF / Main power / weak batteries | batt | Batteries | batt | Batteries | 355873 | KS-ZAAFRAN | C1_3299DE_PH12 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) | 2019-09-27 05:42 | 2019-07-22 | TRUE
IM774403 | 0165UP | 0381_B_AS-APT_0165UP_X | Generator problem,weak Batteries, solved. | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 345342 | 01_V_AS-APT_0165UP | C4_0165UP_PH03 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage beside gen enclosure) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage beside gen enclosure ( Huge fuel leakage )) (ATS / Engine/Components faulty/external water supply connected to radiator) | 2019-09-27 06:06 | 2019-06-12 | TRUE
IM774408 | 0574UP | 02_S_QN-GARAGOUS_0574UP | main Power Disconnection, weak Batteries, PG Connected. | batt | Batteries | batt | Batteries | 304201 | 01_S_QN-GARAGOUS_0574UP | C3_0574UP_PH9 | (Batteries/Item(s) stolen/Batteries were stolen) | 2019-09-27 06:32 | 2019-02-12 | TRUE
IM774429 | 3221UP | 2021_S_SG-AWLAD-NOSIR_3221UP | main Power Disconnection, weak Batteries, PG Connected. | batt | Batteries | batt | Batteries | 345420 | 01_S_SG-AWLAD-NOSIR_3221UP | C1_3221UP_PH13 | (Batteries/Some parts are (missing / stolen)/one string battery was stolen) | 2019-09-27 05:38 | 2019-06-20 | TRUE
IM774438 | 0165UP | 0381_B_AS-APT_0165UP_X | Generator problem,weak Batteries, solved. | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 345342 | 01_V_AS-APT_0165UP | C4_0165UP_PH03 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage beside gen enclosure) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage beside gen enclosure ( Huge fuel leakage )) (ATS / Engine/Components faulty/external water supply connected to radiator) | 2019-09-27 07:49 | 2019-06-12 | TRUE
IM774451 | 0964UP | 0181_S_SG-SALLA_0964UP | main Power Disconnection, weak Batteries, PG Connected. | batt | Batteries | batt | Batteries | 345407 | SG-SALLA | C2_0964UP_PH12 | (Batteries/Some parts are (missing / stolen)/site Batteries were stolen) | 2019-09-27 09:01 | 2019-06-19 | TRUE
IM774504 | 0045SI | 01_G_SS-MR66-ABYAD_0045SI | DG Stoppage / weak batteries / access Guard problem / cleared after Gen restored | batt DG Gen | Batteries Generator Generator | DG Gen | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure ) (ATS / Engine/Wrong connection/generator battery as used in the site and not suitable in High temp) | 2019-09-27 11:25 | 2019-07-01 | TRUE
IM774541 | 3903DE | 0501_D_GH-MHLT-MISIR_3903DE | GN problem / stolen batteries | batt GN | Batteries Generator | batt GN | Batteries Generator | 335219 | GH-MHLT-MISIR | C4_3903DE_PH15 | (Batteries/Item(s) stolen/There is no battery for site) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM wrong penetration/CB need proper fixation) | 2019-09-27 13:24 | 2019-05-26 | TRUE
IM774545 | 3793DE | 0821_D_SK-SHARQAYA_3793DE | GN problem/Batteries under investigation/clear after replace GN | batt GN | Batteries Generator | GN | Generator | 356263 | SK-SHARQAYA | C1-3793DE-PH14 | (ATS / Engine/Components faulty/Faulty module.) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/ATS cables need proper terminals.) | 2019-09-27 13:59 | 2019-09-11 | TRUE
IM774624 | 0219RE | 1691_Q_MARSA-EDFU16_0219RE_X | Generator problem, weak Batteries, solved. | batt Gen generator | Batteries Generator Generator | batt Gen generator | Batteries Generator | 303875 | 01_H_MARSA-EDFU16_0219RE | C1_0219RE_PH9 | (Batteries/Item(s) stolen/Batteries were stolen) (ATS / Engine/Wrong connection/external cable to the guard connected from gen and not protected) (ATS / Engine/Wrong connection/One Contactor turned on by setting wood inside it) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cables not protected in tube) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Cables not protected) (ATS / Engine/Item(s) stolen/Gen battery is missing) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/ Fuel leakage inside Gen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage inside Gen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage beisde Gen enclosure area need cleaning) (ATS / Engine/Panorama pictures for each system/Open gland in Gen enclosure need insulation) (ATS / Engine/Panorama pictures for each system/Panorama site view in outside site) (ATS / Engine/Panorama pictures for each system/Last Gen hour meter at Audit G ( 31148 )) | 2019-09-27 19:27 | 2019-01-16 | TRUE
IM774636 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/stolen batteries/clear after check GN | batt GN | Batteries Generator | batt GN | Batteries Generator | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | (Batteries/Some parts are missing/Battery cabinet need cleaning (from inside) and holes need sealing.) (Batteries/Some parts are missing/Batteries poles need have missing covers.) (ATS / Engine/Components faulty/Generator has bad performance and need overall.) (ATS / Engine/Panorama pictures for each system/Overview.) | 2019-09-27 19:29 | 2019-05-21 | TRUE
IM774642 | 0500RE | 03461_S_0500RE_SZ-REHAB | VF EC power problem / stolen batteries / access PG problem /cleared after power restored | batt | Batteries | batt | Batteries | 356059 | 01_S_SZ-REHAB_0500RE | 0500RE | (Batteries/Some parts are (missing / stolen)/Battery string stolen) | 2019-09-27 22:12 | 2019-08-19 | TRUE
IM774648 | 0352UP | 01_J_ASYUT-KHARGA-6-NR_0352UP | Due to Generator problem , Weak batteries , Recovered | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 355715 | 01_S_RS-ABO-RAMAD-BR_0512RE | 0512RE | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/fuel leakage inside Gen enclosure ) (ATS / Engine/Wrong connection/generator battery as used in the site and not suitable in High temp) | 2019-09-27 22:48 | 2019-07-01 | TRUE
IM774658 | 0003UP | 0311_N_AS-TROMBAT-AS_0003UP | main Power Disconnection, weak Batteries,Autorecovered. | batt | Batteries | batt | Batteries | 345338 | 01_N_AS-TROMBAT-AS_0003UP | C1_0003UP_PH0 | (Batteries/Some parts are (missing / stolen)/one Batteries string was stolen) | 2019-09-27 23:32 | 2019-06-12 | TRUE
IM774664 | 0548UP | 01_D_WG-BHAGWAYAT_0548UP | Generator stopped due to LOP alarm as engine need overhauling action Site has weak backup batteries | backup batt Gen generator | Batteries Batteries Generator Generator | backup batt Gen generator | Batteries Generator | 325009 | 01_D_WG-BHAGWAYAT_0548UP | C1_0548UP_PH9 | (Batteries/Item(s) stolen/One of batteries string was stolen) (ATS / Engine/Components faulty/Gen battery is defected) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/Gen battery cables not isolated well) (ATS / Engine/Panorama pictures for each system/Open gland in Gen enclosure need insulation) (ATS / Engine/Panorama pictures for each system/Panorama site view in outside site) (ATS / Engine/Panorama pictures for each system/Last Gen hour meter at Auidt G ( 661 )) | 2019-09-28 00:57 | 2019-05-02 | TRUE
IM774676 | 3349CA | 01126_S_3349CA_IMBABA-6 | down due to main power & weak batteries (T) | batt | Batteries | batt | Batteries | 303961 | IMBABA-6 | C2_3349CA_PH12 | (Batteries/Components faulty/Batteries are in a very bad condition (DC voltage dropped to 42.7V. after 1 min of power disconnecting)) | 2019-09-27 10:24 | 2019-01-21 | TRUE
IM774683 | 3002CA | 00926_S_3002CA_BASHTEL1 | down due to main power & stolen batteries at 3002CA_BASHTEL1 (T) | batt | Batteries | batt | Batteries | 304247 | BASHTEL1 | C1_3002CA_PH9 | (Batteries/Item(s) stolen/Stolen batteries and cables) | 2019-09-27 14:21 | 2019-02-17 | TRUE
IM774718 | 0011RE | 03426_G_0011RE_SZ-HW33-7 | DG stoppage / stolen batteries / fuel pump problem/ PG connected till gen restored | batt DG Gen | Batteries Generator Generator | batt DG Gen | Batteries Generator | 356077 | 01_G_SZ-HW33-7_0011RE | C1_0011RE_PH1 | (Batteries/Some parts are (missing / stolen)/Battery string stolen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage) (ATS / Engine/Wrong connection/Power cable has no terminal & worng connection , the two cables should be in one terminal) | 2019-09-28 04:33 | 2019-08-22 | TRUE
IM774728 | 3065UP | 0641_S_QN-ELARAKI_3065UP | main Power Disconnection, weak Batteries, PG Connected. | batt | Batteries | batt | Batteries | 356496 | 01_S_QN-ELARAKI_3065UP | C1_3065UP_PH13 | (Batteries/Some parts are (missing / stolen)/Batteries were stolen) | 2019-09-28 04:15 | 2019-10-07 | FALSE
IM774750 | 3529UP | 1041_E_QN-HISHA_3529UP | Generator problem, weak Batteries, solved. | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 355814 | 01_S_QN-HISHA_3529UP | C1_3529UP_PH14 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/old fuel leakage beisde Gen enclosure ) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Fuel leakage inside Gen enclosure ) (ATS / Engine/Unit earth/Gen earth cable is missing) | 2019-09-28 07:08 | 2019-07-16 | TRUE
IM774758 | 0011RE | 03426_D_0011RE_SZ-HW33-7 | DG stoppage / stolen batteries / fuel pump problem/ PG connected till gen restored | batt DG Gen | Batteries Generator Generator | batt DG Gen | Batteries Generator | 356077 | 01_G_SZ-HW33-7_0011RE | C1_0011RE_PH1 | (Batteries/Some parts are (missing / stolen)/Battery string stolen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage) (ATS / Engine/Wrong connection/Power cable has no terminal & worng connection , the two cables should be in one terminal) | 2019-09-28 07:33 | 2019-08-22 | TRUE
IM774820 | 2123DE | 0631_S_DM-M-EZBT-BRG2_2123DE | Main power / Micro / Access PG / Weak batteries | batt | Batteries | batt | Batteries | 355943 | DM-M-EZBT-BRG2 | C1_2123DE_PH17 | (Rectifiers/Alarms reporting to the OMC/alarm door is not reported) (Batteries/Some parts are (missing / stolen)/poles covers ) | 2019-09-28 09:12 | 2019-08-03 | TRUE
IM774821 | 0954UP | 01_G_MN-DAHMARU_0954UP | VF shared power meter was our of charge and recharged Site has stolen backup batteries | backup batt | Batteries Batteries | backup batt | Batteries | 324946 | 01_G_MN-DAHMARU_0954UP | C1_0954UP_PH12 | (Batteries/Item(s) stolen/site baateries were stolen) | 2019-09-28 09:51 | 2019-04-25 | TRUE
IM774831 | 0629CA | 01134_S_0629CA_KAWMYA-ARABYA | down due to main power & weak batteries (T) | batt | Batteries | batt | Batteries | 304038 | KAWMYA-ARABYA | C2_0629CA_PH8 | (Batteries/Item(s) stolen/Battery cables are stolen) | 2019-09-28 10:44 | 2019-01-27 | TRUE
IM774832 | 3178UP | 01_D_AT-BAQUR_3178UP | Generator stopped due to fuel theft problem and site powered on P.G till refuling the generator site has weak backup batteries | backup batt Gen generator | Batteries Batteries Generator Generator | backup batt Gen generator | Batteries Generator | 324555 | 01_G_AT-BAQUR_3178UP | C2_3178UP_PH13 | (Batteries/Components faulty/site batteries were defected and to be changed) (ATS / Engine/Components faulty/Gen missing battery) (ATS / Engine/Wrong connection/Bad isolation for batteries cables) | 2019-09-28 10:50 | 2019-03-17 | TRUE
IM774843 | 3740DE | 0521_S_KS-MNSHT-ABS_3740DE | Access TE / Main power / Stolen batteries | batt | Batteries | batt | Batteries | 324805 | KS-MNSHT-ABS | C1_3740DE_Ph14 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-28 10:14 | 2019-04-08 | TRUE
IM774845 | 0479DE | 0591_S_DK-MNS-FRSKOR1_0479DE | Main power @ DK-MNS-FRSKOR1_0479DE / Stolen batteries / Access road problem / PG connected | batt | Batteries | batt | Batteries | 356389 | DK-MNS-FRSKOR1 | C3_0479DE_PH7 | (Batteries/Some parts are (missing / stolen)/stolen batteries) | 2019-09-28 10:15 | 2019-09-24 | TRUE
IM774847 | 3368DE | 0201_S_BH-ABO-SHIQAF_3368DE | Share VF / Main power / stolen batteries | batt | Batteries | batt | Batteries | 324904 | BH-ABO-SHIQAF | C1_3368DE_PH12 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-28 10:16 | 2019-04-17 | TRUE
IM774864 | 3344DE | 0681_S_BH-ELNEGILY_3344DE | VF Share / Main power / Stolen batteries | batt | Batteries | batt | Batteries | 304214 | BH-ELNEGILY | C3_3344DE_PH12 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-28 10:54 | 2019-02-12 | TRUE
IM774933 | 0413SI | 0451_D_SS-SHRM-CRS-RD_0413SI | DG stoppage / weak batteries / fuel filter problem/ cleared after replaced | batt DG | Batteries Generator | DG | Generator | 355555 | SS-SHRM-CRS-RD | C1_0413SI_PH14 | (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/OIL & fuel leakage ) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/oil leakage ) (ATS / Engine/Unit earth/alternator not earthed) (ATS / Engine/Unit earth/earth bar not connected to main earth bar ) (ATS / Engine/Unit earth/earth cable not connected ) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/cable not terminated ) | 2019-09-28 13:31 | 2019-07-03 | TRUE
IM774958 | 3065AL | 03902_S_3065AL_MHWR-DABA-17 | GN problem/ stolen batteries/ restored after solve GN problem | batt GN | Batteries Generator | GN | Generator | 324550 | MHWR-DABA-17 | C1_3065AL_PH20 | (ATS / Engine/Wrong connection/Wrong connection (Joint cables)) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM organization/Cables needs organization) | 2019-09-28 14:07 | 2019-03-17 | TRUE
IM775050 | 0011RE | 03426_G_0011RE_SZ-HW33-7 | DG stoppage / stolen batteries / fuel pump problem/ PG connected till gen restored | batt DG Gen | Batteries Generator Generator | batt DG Gen | Batteries Generator | 356077 | 01_G_SZ-HW33-7_0011RE | C1_0011RE_PH1 | (Batteries/Some parts are (missing / stolen)/Battery string stolen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage) (ATS / Engine/Wrong connection/Power cable has no terminal & worng connection , the two cables should be in one terminal) | 2019-09-28 20:39 | 2019-08-22 | TRUE
IM775051 | 0001SI | 03504_I_0001SI_IS-GEDAM | DG stoppage / weak batteries / dynamo problem/ cleared | batt DG | Batteries Generator | batt | Batteries | 355761 | 01_W_IS-GEDAM_0001SI | C2_0001SI_PH0 | (Rectifiers/Alarms reporting to the OMC/Rectifier minor & major alarm not report the OMC) | 2019-09-28 20:48 | 2019-07-08 | TRUE
IM775078 | 0329RE | 03838_S_0329RE_RS-SENTIDO-DRM | ET Gen stoppage / weak batteries / cleared after Gen restored | batt Gen | Batteries Generator | Gen | Generator | 304289 | 01_S_RS-SENTIDO-DRM_0329RE | C1_0329RE_PH12 | (ATS / Engine/Panorama pictures for each system/Panorama site view in outside site) | 2019-09-29 00:09 | 2019-02-19 | TRUE
IM775080 | 3130CA | K_BASHTEL-ST_2_11319-2_S | was down cascaded 3130CA_BASHTEL-ST which down due to power and stolen batt. (I) | batt | Batteries | batt | Batteries | 345403 | BASHTEL-ST | C3_3130CA_PH9 | (Rectifiers/Alarms reporting to the OMC/Minor alarm due to temprature measurement doesn't appear on the OMC (Loop in DDF)) (Batteries/Some parts are (missing / stolen)/All batteries are stolen) | 2019-09-29 00:45 | 2019-06-19 | TRUE
IM775092 | 3953DE | 0361_G_BH-MAARKA_3953DE | access ET/main power/weak batteries/clear after power back | batt | Batteries | batt | Batteries | 304235 | BH-MAARKA | C1_3953DE_PH15 | (Batteries/Components faulty/Faulty battery and cable disconnected) | 2019-09-29 02:36 | 2019-02-14 | TRUE
IM775115 | 0576DE | 1611_G_BH-WAFAIYYA_0576DE | Main Power / Stolen batteries | batt | Batteries | batt | Batteries | 324440 | BH-WAFAIYYA | C2_0576DE_PH9 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-29 05:20 | 2019-03-07 | TRUE
IM775121 | 0971DE | 1931_D_KS-DISOQ-COURT_0971DE | Share ET / Gen problem / Stolen Batteries / Team in site | batt Gen | Batteries Generator | batt Gen | Batteries Generator | 314424 | KS-DISOQ-COURT | C4_0971DE_PH11 | (Batteries/Item(s) stolen/No battery for site) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Cables at 1 slot) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Terminal requried) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Cable need to be terminated well) | 2019-09-29 05:59 | 2019-03-05 | TRUE
IM775172 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/Stolen batteries/clear on P.G | batt GN | Batteries Generator | batt GN | Batteries Generator | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | (Batteries/Some parts are missing/Battery cabinet need cleaning (from inside) and holes need sealing.) (Batteries/Some parts are missing/Batteries poles need have missing covers.) (ATS / Engine/Components faulty/Generator has bad performance and need overall.) (ATS / Engine/Panorama pictures for each system/Overview.) | 2019-09-29 08:26 | 2019-05-21 | TRUE
IM775175 | 3499UP | 1871_S_AS-GAFAR-SADK_3499UP_X | Main Power Disconenction, weak Batteries, Recovered. | batt | Batteries | batt | Batteries | 356189 | 01_S_AS-GAFAR-SADK_3499UP | C1_3499UP_PH14 | (Batteries/Some parts are (missing / stolen)/Site Batteries were stolen) | 2019-09-29 08:54 | 2019-09-03 | TRUE
IM775181 | 0086RE | 03821_C_0086RE_RS-MR44-LASIFA | DG Stoppage / weak batteries / cleared after restored | batt DG | Batteries Generator | DG | Generator | 355695 | 01_C_RS-MR44-LASIFA_0086RE | C2_0086RE_PH3 | (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/add terminals) | 2019-09-29 09:00 | 2019-01-22 | TRUE
IM775212 | 3361DE | 0441_S_KS-HAMUL-EST_3361DE | Share VF / Main power / Stolen batteries | batt | Batteries | batt | Batteries | 355874 | KS-HAMUL-EST | C1_3361DE_PH12 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) | 2019-09-28 09:54 | 2019-07-22 | TRUE
IM775218 | 4021DE | 0181_S_BH-ABQAEEN_4021DE | Share VF / Main power / Stolen batteries | batt | Batteries | batt | Batteries | 304224 | BH-ABQAEEN | C1_4021DE_PH15 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-28 10:16 | 2019-02-13 | TRUE
IM775267 | 3126DE | 0121_S_DK-HAGYZEYA_3126DE | access VF/main power/Stolen batteries/handel husiynia 2 //manshit amer//hwamida | batt | Batteries | batt | Batteries | 355992 | DK-HAGYZEYA | C6-3126DE-PH12 | (Batteries/Some parts are (missing / stolen)/No backup batteries.) | 2019-09-29 10:05 | 2019-08-07 | TRUE
IM775285 | 0596DE | 1691_G_GH-TIRA_0596DE | Main power @ GH-TIRA_0596DE / stolen batteries | batt | Batteries | batt | Batteries | 324921 | GH-TIRA | C1_0596DE_PH9 | (Batteries/Item(s) stolen/stolen batteries) | 2019-09-29 10:31 | 2019-04-22 | TRUE
IM775309 | 3991UP | 891_E_AT-DIR-MEHRAA2_3991UP | Generator replacment action and site has weak backup batteries , P.G connected | backup batt Gen generator | Batteries Batteries Generator Generator | Gen generator | Generator | 335156 | 01_S_AT-DIR-MEHRAA2_3991UP | C1_3991UP_PH16 | (ATS / Engine/Components faulty/Gen battery was defected) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM organization/ATS Cables not organized) | 2019-09-29 10:55 | 2019-05-18 | TRUE
IM775339 | 3346DE | 0701_S_BH-KOMOMBO_3346DE | Share VF / Main power / batteries under check | batt | Batteries | batt | Batteries | 355803 | BH-KOMOMBO | C1_3346DE_PH12 | (Rectifiers/Alarms reporting to the OMC/Site has fake power alarm) | 2019-09-29 11:21 | 2019-07-14 | TRUE
IM775494 | 4031DE | 1271_D_QL-NAMOL_4031DE | access Guard/GN problem/Stolen batteries/clear after check GN | batt GN | Batteries Generator | batt GN | Batteries Generator | 345429 | QL-NAMOL | C1_4031DE_PH15 | (Batteries/Some parts are (missing / stolen)/There is no battery for site) (ATS / Engine/Cables termination/lugs (AC side), lugs (DC side)/Cable need to be terminated well) | 2019-09-29 13:38 | 2019-06-23 | TRUE
IM775703 | 3178UP | 01_D_AT-BAQUR_3178UP | Generator stopped due to fuel shortage problem and solved site has weak backup batteries | backup batt Gen generator | Batteries Batteries Generator Generator | backup batt Gen generator | Batteries Generator | 324555 | 01_G_AT-BAQUR_3178UP | C2_3178UP_PH13 | (Batteries/Components faulty/site batteries were defected and to be changed) (ATS / Engine/Components faulty/Gen missing battery) (ATS / Engine/Wrong connection/Bad isolation for batteries cables) | 2019-09-29 16:52 | 2019-03-17 | TRUE
IM775837 | 3866DE | 2001_D_DK-SANBAKHT_3866DE | Generator problem / Stolen Batteries | batt Gen generator | Batteries Generator Generator | Gen generator | Generator | 304185 | DK-SANBAKHT | C3_3866DE_PH14 | (ATS / Engine/Components faulty/screen need repair) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/protect by tray ) (ATS / Engine/Cables/Jumpers/Coaxial/FO/PCM protection (e.g. floating/[sharp edges in trays/ducts/conduits])/protect) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/check oil leakage ) | 2019-09-30 05:39 | 2019-02-07 | TRUE
IM775866 | 3495DE | 0181_S_SK-MAHDIYA_3495DE | Main power/ stolen battery/connect PG | batt | Batteries | batt | Batteries | 304144 | SK-MAHDIYA | C3_3495DE_PH13 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-30 06:26 | 2019-02-09 | TRUE
IM775868 | 3394DE | 0011_S_B-SAFT-KHALED_3394DE | Share VF / Main Power / Weak Batteries / PG connected | batt | Batteries | batt | Batteries | 304033 | BH-SAFT-KHALED | C1_3394DE_PH13 | (Batteries/Components faulty/Faulty battery) | 2019-09-30 06:46 | 2019-01-24 | TRUE
IM775974 | 0955UP | 0551_S_QN-SHRQI-SMHUD_0955UP | main power Disconnection,weak batteries, PG Connected . | batt | Batteries | batt | Batteries | 355972 | 01_S_QN-SHRQI-SHMHUD_0955UP | C1_0955UP_PH12 | (Rectifiers/Alarms reporting to the OMC/High Temp Alarm was exists on rectifier and appeared on the Omc) | 2019-09-30 08:50 | 2019-08-05 | TRUE
IM776012 | 0587DE | 0221_S_DK-KFR-KURDI_0587DE | Share VF / Main Power / stolen Batteries / PG handle another sites ( DK-MNS-FRSKOR1_0479DE & Baramoun & DK-DEMYANA-PS_0731DE ) | batt | Batteries | batt | Batteries | 324791 | DK-KFR-KURDI | C9_0587DE_PH09 | (Batteries/Item(s) stolen/No backup batteries.) | 2019-09-30 09:20 | 2019-04-10 | TRUE
IM776051 | 3669UP | 0281_N_BS-NAEM-VLG_3669UP_X | Commercial power cutoff and weak backup batteries PLVD disconencted the site loads to save the linked sites P.G connected and site back on air | backup batt PLVD | Batteries Batteries Rectifier | backup batt | Batteries | 355953 | 01_N_BS-NAEM-VLG_3669UP | C1_3669UP_PH15 | (Batteries/Components faulty/The DC voltage dropped to 47.97 V. after 1 min. of disconnecting the power) | 2019-09-30 10:28 | 2019-07-29 | TRUE
IM776082 | 3344DE | 0681_S_BH-ELNEGILY_3344DE | Share VF / Main Power / stolen Batteries / PG handle another sites ( BH-SAHALI_3844DE & BH-MNSHT-HLBWI_3710DE ) | batt | Batteries | batt | Batteries | 304214 | BH-ELNEGILY | C3_3344DE_PH12 | (Batteries/Item(s) stolen/There is no battery for site) | 2019-09-30 09:39 | 2019-02-12 | TRUE
IM776085 | 0479DE | 0591_S_DK-MNS-FRSKOR1_0479DE | Main Power @ DK-MNS-FRSKOR1_0479DE / Stolen batteries / PG connected | batt | Batteries | batt | Batteries | 356389 | DK-MNS-FRSKOR1 | C3_0479DE_PH7 | (Batteries/Some parts are (missing / stolen)/stolen batteries) | 2019-09-30 09:48 | 2019-09-24 | TRUE
IM776122 | 3628DE | 0811_S_GH-QSR-BAGHDAD_3628DE | Main power / stolen batteries / PG handle another sites ( GH-GASTA_0833DE & GH-SHBRA-NAMLA_3354DE ) / PG connected | batt | Batteries | batt | Batteries | 324836 | GH-QSR-BAGHDAD | C2_3628DE_PH13 | (Batteries/Item(s) stolen/Stolen batteries) | 2019-09-30 09:53 | 2019-04-15 | TRUE
IM776150 | 0673CA | 02654_S_0673CA_ASMA-FAHMY | down due to power probelm @ 0673CA_ASMA-FAHMY and battery weak | batt | Batteries | batt | Batteries | 356212 | ASMA-FAHMY | C1_0673CA_PH8 | (Batteries/Some parts are (missing / stolen)/missing batteries) | 2019-09-30 11:32 | 2019-08-19 | TRUE
IM776189 | 0011RE | 03426_G_0011RE_SZ-HW33-7 | DG stoppage / stolen batteries / cleared after Gen restored | batt DG Gen | Batteries Generator Generator | batt DG Gen | Batteries Generator | 356077 | 01_G_SZ-HW33-7_0011RE | C1_0011RE_PH1 | (Batteries/Some parts are (missing / stolen)/Battery string stolen) (ATS / Engine/Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…)/Oil leakage) (ATS / Engine/Wrong connection/Power cable has no terminal & worng connection , the two cables should be in one terminal) | 2019-09-30 11:42 | 2019-08-22 | TRUE
IM776202 | 0479DE | 0591_S_DK-MNS-FRSKOR1_0479DE | Main Power @ DK-MNS-FRSKOR1_0479DE / Stolen batteries / PG connected | batt | Batteries | batt | Batteries | 356389 | DK-MNS-FRSKOR1 | C3_0479DE_PH7 | (Batteries/Some parts are (missing / stolen)/stolen batteries) | 2019-09-30 11:51 | 2019-09-24 | TRUE
IM776421 | 3528DE | 1691_D_SK-HAWAMIDA_3528DE | GN problem/stolen battery/clear after check Gn | batt GN | Batteries Generator | batt GN | Batteries Generator | 335161 | SK-HAWAMIDA | C2-3528DE-PH14 | (Batteries/Some parts are missing/Battery cabinet need cleaning (from inside) and holes need sealing.) (Batteries/Some parts are missing/Batteries poles need have missing covers.) (ATS / Engine/Components faulty/Generator has bad performance and need overall.) (ATS / Engine/Panorama pictures for each system/Overview.) | 2019-09-30 14:12 | 2019-05-21 | TRUE
IM776434 | 0553CA | 02127_N_0553CA_SATA | down due to power problem and battery weak | batt | Batteries | batt | Batteries | 345282 | SATA | C1_0553CA_PH5 | (Rectifiers/Alarms reporting to the OMC/Major alarm is active on the rectifier) (Batteries/Components faulty/DC voltage dropped to 47.6 V. after 10 seconds of power disconnecting) (Batteries/Some parts are (missing / stolen)/Stolen cables of battery string 1) | 2019-09-30 14:34 | 2019-06-10 | TRUE
IM776448 | 0657CA | 01766_S_0657CA_BAGDAD-ST | down due to power failure and dead batteries | batt | Batteries | batt | Batteries | 345255 | BAGDAD-ST | C7_0657CA_PH8 | (Batteries/Some parts are missing/missing batteries/ stolen) | 2019-09-30 14:51 | 2019-05-22 | TRUE
IM776477 | 3659CA | 599_G_3659CA_NEW-CA-VGK | down due to VF DG problem and access VF problem and stolen batt | batt DG | Batteries Generator | batt | Batteries | 356205 | NEW-CA-VGK | C1_3659CA_PH15 | (Batteries/Some parts are (missing / stolen)/missing battereis) | 2019-09-30 15:41 | 2019-08-14 | TRUE
IM776482 | 3394DE | 0011_S_B-SAFT-KHALED_3394DE | Share VF / Main Power / Weak Batteries / PG connected | batt | Batteries | batt | Batteries | 304033 | BH-SAFT-KHALED | C1_3394DE_PH13 | (Batteries/Components faulty/Faulty battery) | 2019-09-30 15:26 | 2019-01-24 | TRUE
IM776483 | 0983DE | 1771_S_DK-MIT-ANTAR_0983DE | Main power / stolen batteries / PG handle another sites ( DK-MNS-FRSKOR1_0479DE & Baramoun & DK-DEMYANA-PS_0731DE ) | batt | Batteries | batt | Batteries | 324896 | DK-MIT-ANTAR | C8_0983DE_PH11 | (Batteries/Item(s) stolen/stolen batteries) | 2019-09-30 15:49 | 2019-04-14 | TRUE
IM776540 | 0050DE | 0001_S_GH-SHABSHR-HAS_0050DE | Main power @ GH-SHABSHR-HAS_0050DE / batteries under check | batt | Batteries | batt | Batteries | 304298 | GH-SHABSHR-HAS | C1_0050DE_PH1 | (Batteries/Some parts are missing/cover) | 2019-09-30 17:33 | 2019-02-23 | TRUE
IM776640 | 3511DE | 1181_D_DK-NUZUL_3511DE | GN problem / weak batteries | batt GN | Batteries Generator | GN | Generator | 345377 | DK-NUZUL | C6_3511DE_PH13 | (ATS / Engine/Components faulty/Faulty module.) (ATS / Engine/Wrong connection/Radiator has bad water feeding.) | 2019-09-30 23:05 | 2019-06-19 | TRUE