## Tables&Charts
Table #0:
NSQI
Before | General | Converged Run | New Sites
Absolute NSQI | 0% | 0% | 0%
Average NSQI | 45.31% | 44.5% | 81%
Total sites | 45 | 44 | 1
Total sites above 90% | 0 | 0 | 0
Number of Criticals | 421 | 419 | 2
Number of Majors | 241 | 240 | 1
Number of Minors | 295 | 294 | 1
Total Reserves | 957 | 953 | 4
Contractor Performance Indicator (CPI)
Before | General
Absolute | 0%
Average | 52.02%
Table #1:
Sample Breakdown
Site Type | Required | Orange | Sectra | Total
BSC | 5 | 0 | 2 | 2
Whitelist | 5 | 1 | 4 | 5
Nodal/VIP | 10 | 3 | 6 | 9
Old Sites (Before 2018) | 10 | 7 | 12 | 19
New Sites (After 2018) | 10 | 0 | 1 | 1
LTE | 5 | 9 | 0 | 9
| 45 | 20 | 25 | 45
Table #2:
Sample Per Areas
HGLI | 20
AGLI | 13
NGLI | 12
45
Table #3:
Absolute NSQI Trend
Year | Week | General | Converged Run | New Sites
2016 | W1 | 2.899% | 2.899% | 56.52%
| W4 | 0% | 2.362% | 53.54%
| W5 | 0.3413% | 1.706% | 34.47%
| W6 | 0% | 7.317% | 29.27%
| W7 | 0% | 0% | 59.72%
| W8 | 0% | 3.704% | 59.26%
| W9 | 5.128% | 12.82% | 61.54%
| W10 | 0.7692% | 0.7692% | 33.85%
| W16 | 0% | 0% | 76.92%
| W18 | 1.01% | 1.01% | 52.02%
| W20 | 0% | 0% | 55%
| W28 | 0% | 2.5% | 45%
| W30 | 0% | 0% | 67.5%
| W32 | 0% | 0% | 35%
| W42 | 2.5% | 2.5% | 67.5%
| W44 | 0% | 0% | 50%
| W46 | 0% | 0% | 90%
| W46 | 0% | 0% | 90%
| W50 | 0% | 0% | 32.5%
| W52 | 0% | 0% | 77.5%
2017 | W4 | 5% | 10% | 40%
| W8 | 0% | 0% | 57.5%
| W10 | 0% | 4.444% | 73.33%
| W12 | 4.444% | 6.667% | 66.67%
| W14 | 0% | 0% | 37.78%
| W16 | 0% | 8.889% | 51.11%
| W18 | 0% | 2.222% | 53.33%
| W20 | 10.87% | 13.04% | 50%
| W22 | 10.87% | 13.04% | 50%
| W24 | 0% | 4.444% | 33.33%
| W26 | 0% | 11.11% | 31.11%
| W28 | 11.11% | 15.56% | 48.89%
| W30 | 0% | 4.444% | 42.22%
| W32 | 2.222% | 8.889% | 35.56%
| W34 | 4.444% | 8.889% | 44.44%
| W36 | 0% | 11.11% | 42.22%
| W38 | 6.667% | 17.78% | 46.67%
| W40 | 4.444% | 6.667% | 42.22%
| W42 | 6.667% | 8.889% | 37.78%
| W44 | 2.222% | 4.444% | 37.78%
| W46 | 4.444% | 11.11% | 42.22%
| W48 | 4.444% | 6.667% | 40%
| W50 | 2.222% | 4.444% | 42.22%
| W52 | 0% | 11.11% | 33.33%
2018 | W4 | 0% | 6.667% | 48.89%
| W6 | 2.222% | 6.667% | 51.11%
| W8 | 2.222% | 6.667% | 57.78%
| W10 | 6.667% | 13.33% | 55.56%
| W12 | 0% | 11.11% | 48.89%
| W14 | 2.222% | 11.11% | 40%
| W16 | 2.222% | 11.11% | 53.33%
| W18 | 2.222% | 6.667% | 42.22%
| W20 | 6.667% | 8.889% | 40%
| W22 | 2.222% | 15.56% | 40%
| W24 | 4.444% | 6.667% | 37.78%
| W26 | 11.11% | 17.78% | 51.11%
| W28 | 6.667% | 24.44% | 53.33%
| W30 | 11.11% | 20% | 37.78%
| W32 | 0% | 0% | 37.78%
| W34 | 0% | 4.444% | 55.56%
| W36 | 2.222% | 4.444% | 42.22%
| W38 | 2.222% | 4.444% | 42.22%
| W40 | 0% | 4.444% | 42.22%
| W42 | 4.444% | 17.78% | 53.33%
| W44 | 8.889% | 13.33% | 48.89%
| W46 | 20% | 7.143% | 0%
| W48 | 15.56% | 16.67% | 0%
| W50 | 4.444% | 4.444% | N/A
| W52 | 6.667% | 7.143% | 0%
2019 | W02 | 4.444% | 4.444% | N/A
| W04 | 4.444% | 4.444% | N/A
| W06 | 20% | 20% | N/A
| W08 | 17.78% | 13.95% | 100%
| W10 | 8.889% | 9.302% | 0%
| W12 | 2.222% | 0% | 9.091%
| W14 | 8.889% | 5% | 40%
| W16 | 4.444% | 2.381% | 33.33%
| W18 | 2.222% | 2.222% | N/A
| W20 | 2.222% | 2.381% | 0%
| W22 | 6.667% | 7.143% | 0%
| W24 | 2.222% | 2.222% | N/A
| W26 | 2.222% | 2.381% | 0%
| W28 | 0% | 0% | N/A
| W30 | 0% | 0% | N/A
| W32 | 2.222% | 2.222% | N/A
| W34 | 0% | 0% | N/A
| W36 | 2.222% | 2.381% | 0%
| W38 | 0% | 0% | 0%
Table #4:
Average NSQI Trend
Year | Week | General | Converged Run | New Sites
2016 | W20 | 39.9% | 47.43% | 78.63%
| W28 | 40.63% | 46.85% | 81.67%
| W30 | 39.67% | 42.95% | 87.12%
| W32 | 39.23% | 41.13% | 91.3%
| W42 | 54.1% | 56.9% | 92.6%
| W44 | 39% | 44.73% | 84.4%
| W46 | 41.15% | 43.5% | 95.15%
| W48 | 42.53% | 48.48% | 86.03%
| W50 | 41.3% | 50.1% | 81.48%
| W52 | 46.03% | 49.3% | 93.18%
2017 | W4 | 60.95% | 70.75% | 84.78%
| W8 | 49.02% | 65.92% | 80.25%
| W10 | 51.33% | 53.93% | 93.4%
| W12 | 61.59% | 66.12% | 91.69%
| W14 | 60.11% | 67.04% | 84.71%
| W16 | 63.31% | 71.44% | 86.95%
| W18 | 64.56% | 71.2% | 88.42%
| W20 | 64.6% | 72.8% | 87.38%
| W22 | 61.29% | 68.25% | 84.26%
| W24 | 61.52% | 70.85% | 83.83%
| W26 | 59.54% | 68.96% | 84.02%
| W28 | 59.54% | 68.96% | 84.02%
| W30 | 62.23% | 68.19% | 86.04%
| W32 | 59.12% | 67.17% | 84.96%
| W34 | 58.32% | 68.22% | 83.4%
| W36 | 60.19% | 69.84% | 85.54%
| W38 | 57.69% | 65.88% | 85.21%
| W40 | 63.73% | 71.41% | 87.62%
| W42 | 58.22% | 66.47% | 82.76%
| W44 | 56.74% | 63.4% | 82.97%
| W46 | 57.7% | 67.93% | 82.47%
| W48 | 62.86% | 71.36% | 85.66%
| W50 | 55.12% | 64.23% | 83.09%
| W52 | 58.16% | 66.9% | 84.69%
2018 | W4 | 62.1% | 71.73% | 81.9%
| W6 | 61.53% | 70.36% | 85.36%
| W8 | 61.86% | 69.09% | 86.03%
| W10 | 61.86% | 69.09% | 86.03%
| W12 | 60.51% | 69.4% | 86.38%
| W14 | 61.6% | 69.53% | 85.09%
| W16 | 61.86% | 67.96% | 86.91%
| W18 | 59.87% | 68.01% | 85.81%
| W20 | 58.51% | 66.91% | 83.52%
| W22 | 61.61% | 69.93% | 84.74%
| W24 | 55.36% | 65.4% | 79.78%
| W26 | 65.54% | 73.18% | 87.74%
| W28 | 65.59% | 74.54% | 86.01%
| W30 | 61.08% | 70.79% | 82.44%
| W32 | 52.96% | 60.84% | 82.81%
| W34 | 62.7% | 70.42% | 86.53%
| W36 | 61.76% | 70.18% | 85.75%
| W38 | 60.19% | 68.54% | 84.03%
| W40 | 58.91% | 66.99% | 84.03%
| W42 | 61.47% | 69.16% | 85.3%
| W44 | 61.69% | 68.44% | 87.89%
| W46 | 65.54% | 65.39% | 67.67%
| W48 | 65.16% | 65.99% | 53.56%
| W50 | 63.2% | 63.2% | N/A
| W52 | 61.82% | 61.53% | 65.89%
2019 | W02 | 55.84% | 55.84% | N/A
| W04 | 55.04% | 55.04% | N/A
| W06 | 67.55% | 67.55% | N/A
| W08 | 62.44% | 61.13% | 90.5%
| W10 | 57.78% | 57.43% | 65.33%
| W12 | 59.86% | 54.98% | 74.94%
| W14 | 53.14% | 50.23% | 76.4%
| W16 | 58.36% | 56.91% | 78.67%
| W18 | 61.63% | 61.63% | N/A
| W20 | 52.27% | 50.59% | 75.78%
| W22 | 57.65% | 56.35% | 75.83%
| W24 | 54.39% | 54.39% | N/A
| W26 | 55.47% | 54.41% | 70.33%
| W28 | 55.42% | 55.42% | N/A
| W30 | 48.88% | 48.88% | N/A
| W32 | 55.98% | 55.98% | N/A
| W34 | 52% | 52% | N/A
| W36 | 58.01% | 56.54% | 78.67%
| W38 | 45.31% | 44.5% | 81%
Table #5:
Reserves Per Offender
Aging | 326
Contractor | 390
Converged Run | 105
Electricity Company | 9
ET | 5
Guard | 17
New Sites | 3
Owner | 0
Sabotage | 6
Stealth | 94
Transmission Solutions | 0
VF | 2
957
Table #6:
Reserves Per Class
Civil | 309
Power System | 335
Cooling System | 119
Equipment and DDF | 104
Fire System | 53
Generator | 37
957
Table #7:
No. of Reserves Per Class Per Areas
System | HGLI | AGLI | NGLI
Power System | 174 | 50 | 111
Cooling System | 53 | 29 | 37
Equipment and DDF | 60 | 16 | 28
Fire System | 33 | 11 | 9
Civil | 190 | 64 | 55
Generator | 18 | 7 | 12
| 528 | 177 | 252
Table #8:
Sabotage & Stealth
Power System | 34
Cooling System | 11
Equipment and DDF | 14
Fire System | 4
Civil | 33
Generator | 4
100
Table #9:
Aging Breakdown
Power System | 118
Cooling System | 47
Equipment and DDF | 30
Fire System | 10
Civil | 113
Generator | 8
326
Table #10:
Civil | Shelter Body / Main Enclosure
Most Common Civil Aging Breakdown (Shelter Body / Main Enclosure)
Unit rust (else trays) | 7
Door/frame fixation that affects door from open easily or close firmly | 6
Lights operation | 5
Earth plates cleaned, waxed, covered with foil | 4
Door lock/handle that affects door from open easily or close firmly | 3
25
Table #11:
Civil | Antenna Support
Most Common Civil Aging Breakdown (Pylon / Palm Tree / Monopole / Masts / Side Arms)
Climbing safety wire | 8
Unit rust (else trays) | 8
Feeders unfixed/unorganized on the vertical path | 5
Beacon light function | 5
Unit unfixed/not installed well | 4
30
Table #12:
Civil | Fence / Roof
Most Common Civil Aging Breakdown (Fence / Roof)
Flammable junk/trash inside/outside (e.g. plastics, papers, cartoon boxes, etc…) | 8
Unit rust (else trays) | 6
Door lock/handle that affects door from open easily or close firmly | 2
Non-flammable junk/trash inside/outside (e.g. metals, woods, etc… ) | 2
Lights operation | 2
20

## Trend Year
Absolute NSQI Trend
Year | Week | General | Converged Run | New Sites | Absolute NSQI | General | Converged Run | New Sites
2016 | W1 | 2.899% | 2.899% | 56.52% | 2016 (Average) | 0.6% | 1.9% | 53.9%
| W4 | 0% | 2.362% | 53.54% | 2017 (Average) | 3.3% | 8.1% | 45%
| W5 | 0.3413% | 1.706% | 34.47% | 2018 (Average) | 5% | 10% | 40.8%
| W6 | 0% | 7.317% | 29.27% | W02-2019 | 4.444% | 4.444% | N/A
| W7 | 0% | 0% | 59.72% | W04-2019 | 4.444% | 4.444% | N/A
| W8 | 0% | 3.704% | 59.26% | W06-2019 | 20% | 20% | N/A
| W9 | 5.128% | 12.82% | 61.54% | W08-2019 | 17.78% | 13.95% | 100%
| W10 | 0.7692% | 0.7692% | 33.85% | W10-2019 | 8.889% | 9.302% | 0%
| W16 | 0% | 0% | 76.92% | W12-2019 | 2.222% | 0% | 9.091%
| W18 | 1.01% | 1.01% | 52.02% | W14-2019 | 8.889% | 5% | 40%
| W20 | 0% | 0% | 55% | W16-2019 | 4.444% | 2.381% | 33.33%
| W28 | 0% | 2.5% | 45% | W18-2019 | 2.222% | 2.222% | N/A
| W30 | 0% | 0% | 67.5% | W20-2019 | 2.222% | 2.381% | 0%
| W32 | 0% | 0% | 35% | W22-2019 | 6.667% | 7.143% | 0%
| W42 | 2.5% | 2.5% | 67.5% | W24-2019 | 2.222% | 2.222% | N/A
| W44 | 0% | 0% | 50% | W26-2019 | 2.222% | 2.381% | 0%
| W46 | 0% | 0% | 90% | W28-2019 | 0% | 0% | N/A
| W48 | 0% | 0% | 40% | W30-2019 | 0% | 0% | N/A
| W50 | 0% | 0% | 32.5% | W32-2019 | 2.222% | 2.222% | N/A
| W52 | 0% | 0% | 77.5% | W34-2019 | 0% | 0% | N/A
2017 | W4 | 5% | 10% | 40% | W36-2019 | 2.222% | 2.381% | 0%
| W8 | 0% | 0% | 57.5% | W38-2019 | 0% | 0% | 0%
| W10 | 0% | 4.444% | 73.33%
| W12 | 4.444% | 6.667% | 66.67%
| W14 | 0% | 0% | 37.78%
| W16 | 0% | 8.889% | 51.11%
| W18 | 0% | 2.222% | 53.33%
| W20 | 10.87% | 13.04% | 50%
| W22 | 10.87% | 13.04% | 50%
| W24 | 0% | 4.444% | 33.33%
| W26 | 0% | 11.11% | 31.11%
| W28 | 11.11% | 15.56% | 48.89%
| W30 | 0% | 4.444% | 42.22%
| W32 | 2.222% | 8.889% | 35.56%
| W34 | 4.444% | 8.889% | 44.44%
| W36 | 0% | 11.11% | 42.22%
| W38 | 6.667% | 17.78% | 46.67%
| W40 | 4.444% | 6.667% | 42.22%
| W42 | 6.667% | 8.889% | 37.78%
| W44 | 2.222% | 4.444% | 37.78%
| W46 | 4.444% | 11.11% | 42.22%
| W48 | 4.444% | 6.667% | 40%
| W50 | 2.222% | 4.444% | 42.22%
| W52 | 0% | 11.11% | 33.33%
2018 | W4 | 0% | 6.667% | 48.89%
| W6 | 2.222% | 6.667% | 51.11%
| W8 | 2.222% | 6.667% | 57.78%
| W10 | 6.667% | 13.33% | 55.56%
| W12 | 0% | 11.11% | 48.89%
| W14 | 2.222% | 11.11% | 40%
| W16 | 2.222% | 11.11% | 53.33%
| W18 | 2.222% | 6.667% | 42.22%
| W20 | 6.667% | 8.889% | 40%
| W22 | 2.222% | 15.56% | 40%
| W24 | 4.444% | 6.667% | 37.78%
| W26 | 11.11% | 17.78% | 51.11%
| W28 | 6.667% | 24.44% | 53.33%
| W30 | 11.11% | 20% | 37.78%
| W32 | 0% | 0% | 37.78%
| W34 | 0% | 4.444% | 55.56%
| W36 | 2.222% | 4.444% | 42.22%
| W38 | 2.222% | 4.444% | 42.22%
| W40 | 0% | 4.444% | 42.22%
| W42 | 4.444% | 17.78% | 53.33%
| W44 | 8.889% | 13.33% | 48.89%
| W46 | 20% | 7.143% | 0%
| W48 | 15.56% | 16.67% | 0%
| W50 | 4.444% | 4.444% | N/A
| W52 | 6.667% | 7.143% | 0%
2019 | W02 | 4.444% | 4.444% | N/A
| W04 | 4.444% | 4.444% | N/A
| W06 | 20% | 20% | N/A
| W08 | 17.78% | 13.95% | 100%
| W10 | 8.889% | 9.302% | 0%
| W12 | 2.222% | 0% | 9.091%
| W14 | 8.889% | 5% | 40%
| W16 | 4.444% | 2.381% | 33.33%
| W18 | 2.222% | 2.222% | N/A
| W20 | 2.222% | 2.381% | 0%
| W22 | 6.667% | 7.143% | 0%
| W24 | 2.222% | 2.222% | N/A
| W26 | 2.222% | 2.381% | 0%
| W28 | 0% | 0% | N/A
| W30 | 0% | 0% | N/A
| W32 | 2.222% | 2.222% | N/A
| W34 | 0% | 0% | N/A
| W36 | 2.222% | 2.381% | 0%
| W38 | 0% | 0% | 0%
Average NSQI Trend
Year | Week | General | Converged Run | New Sites | Average NSQI | General | Converged Run | New Sites
2016 | W20 | 39.9% | 47.43% | 78.63% | 2016 (Average) | 42.4% | 47.1% | 87.2%
| W28 | 40.63% | 46.85% | 81.67% | 2017 (Average) | 59.5% | 67.8% | 85.3%
| W30 | 39.67% | 42.95% | 87.12% | 2018 (Average) | 61.4% | 68.3% | 82.1%
| W32 | 39.23% | 41.13% | 91.3% | W02-2019 | 55.84% | 55.84% | N/A
| W42 | 54.1% | 56.9% | 92.6% | W04-2019 | 55.04% | 55.04% | N/A
| W44 | 39% | 44.73% | 84.4% | W06-2019 | 67.55% | 67.55% | N/A
| W46 | 41.15% | 43.5% | 95.15% | W08-2019 | 62.44% | 61.13% | 90.5%
| W48 | 42.53% | 48.48% | 86.03% | W10-2019 | 57.78% | 57.43% | 65.33%
| W50 | 41.3% | 50.1% | 81.48% | W12-2019 | 59.86% | 54.98% | 74.94%
| W52 | 46.03% | 49.3% | 93.18% | W14-2019 | 53.14% | 50.23% | 76.4%
2017 | W4 | 60.95% | 70.75% | 84.78% | W16-2019 | 58.36% | 56.91% | 78.67%
| W8 | 49.02% | 65.92% | 80.25% | W18-2019 | 61.63% | 61.63% | N/A
| W10 | 51.33% | 53.93% | 93.4% | W20-2019 | 52.27% | 50.59% | 75.78%
| W12 | 61.59% | 66.12% | 91.69% | W22-2019 | 57.65% | 56.35% | 75.83%
| W14 | 60.11% | 67.04% | 84.71% | W24-2019 | 54.39% | 54.39% | N/A
| W16 | 63.31% | 71.44% | 86.95% | W26-2019 | 55.47% | 54.41% | 70.33%
| W18 | 64.56% | 71.2% | 88.42% | W28-2019 | 55.42% | 55.42% | N/A
| W20 | 64.6% | 72.8% | 87.38% | W30-2019 | 48.88% | 48.88% | N/A
| W22 | 61.29% | 68.25% | 84.26% | W32-2019 | 55.98% | 55.98% | N/A
| W24 | 61.52% | 70.85% | 83.83% | W34-2019 | 52% | 52% | N/A
| W26 | 59.54% | 68.96% | 84.02% | W36-2019 | 58.01% | 56.54% | 78.67%
| W28 | 59.54% | 68.96% | 84.02% | W38-2019 | 45.31% | 44.5% | 81%
| W30 | 62.23% | 68.19% | 86.04%
| W32 | 59.12% | 67.17% | 84.96%
| W34 | 58.32% | 68.22% | 83.4%
| W36 | 60.19% | 69.84% | 85.54%
| W38 | 57.69% | 65.88% | 85.21%
| W40 | 63.73% | 71.41% | 87.62%
| W42 | 58.22% | 66.47% | 82.76%
| W44 | 56.74% | 63.4% | 82.97%
| W46 | 57.7% | 67.93% | 82.47%
| W48 | 62.86% | 71.36% | 85.66%
| W50 | 55.12% | 64.23% | 83.09%
| W52 | 58.16% | 66.9% | 84.69%
2018 | W4 | 62.1% | 71.73% | 81.9%
| W6 | 61.53% | 70.36% | 85.36%
| W8 | 61.86% | 69.09% | 86.03%
| W10 | 61.86% | 69.09% | 86.03%
| W12 | 60.51% | 69.4% | 86.38%
| W14 | 61.6% | 69.53% | 85.09%
| W16 | 61.86% | 67.96% | 86.91%
| W18 | 59.87% | 68.01% | 85.81%
| W20 | 58.51% | 66.91% | 83.52%
| W22 | 61.61% | 69.93% | 84.74%
| W24 | 55.36% | 65.4% | 79.78%
| W26 | 65.54% | 73.18% | 87.74%
| W28 | 65.59% | 74.54% | 86.01%
| W30 | 61.08% | 70.79% | 82.44%
| W32 | 52.96% | 60.84% | 82.81%
| W34 | 62.7% | 70.42% | 86.53%
| W36 | 61.76% | 70.18% | 85.75%
| W38 | 60.19% | 68.54% | 84.03%
| W40 | 58.91% | 66.99% | 84.03%
| W42 | 61.47% | 69.16% | 85.3%
| W44 | 61.69% | 68.44% | 87.89%
| W46 | 65.54% | 65.39% | 67.67%
| W48 | 65.16% | 65.99% | 53.56%
| W50 | 63.2% | 63.2% | N/A
| W50 | 63.2% | 63.2% | N/A
2019 | W02 | 55.84% | 55.84% | N/A
| W04 | 55.04% | 55.04% | N/A
| W06 | 67.55% | 67.55% | N/A
| W08 | 62.44% | 61.13% | 90.5%
| W10 | 57.78% | 57.43% | 65.33%
| W12 | 59.86% | 54.98% | 74.94%
| W14 | 53.14% | 50.23% | 76.4%
| W16 | 58.36% | 56.91% | 78.67%
| W18 | 61.63% | 61.63% | N/A
| W20 | 52.27% | 50.59% | 75.78%
| W22 | 54.1% | 56.9% | 92.6%
| W24 | 54.39% | 54.39% | N/A
| W26 | 55.47% | 54.41% | 70.33%
| W28 | 55.42% | 55.42% | N/A
| W30 | 48.88% | 48.88% | N/A
| W32 | 55.98% | 55.98% | N/A
| W34 | 52% | 52% | N/A
| W36 | 58.01% | 56.54% | 78.67%
| W38 | 45.31% | 44.5% | 81%

## Dashboard
Physical Quality Weekly Dashboard (W38-2019)
| Old Sites |  |  | 19
| VIP |  |  | 0
| Nodal |  |  | 9
| LTE Sites |  |  | 9
| BSCs |  |  | 2
| New Sites |  |  | 1
W22 | 57.65% | 56.35% | 75.83%
421
241
295
0%
45.31%
Week 4 NSQI
Average
Absolute
Reserves
957
Sabotage Reserves
Per Offender
Reserves classification
CRI
MAJ
MIN
Aging Breakdown
45 Sites

## Details
ReportID | ReserveID | Site Name | Site Code | Site Severity | Site Category | Responsible | Auditor | Auditor Company | Audit Date | Maintenance Office | Contractor | Contractor Area | Contractor Office | Version | Reference | Class | Sub-Class | Item | Severity | Before Comment | Offender | Assigned Team | Default Accountable | Modified Accountable | Vendor | Equipment | Item Score (Gen.) | Sub-Class Score (Gen.) | Site Score (Gen.)
356414 | 1144788 | I-CTYSTR-COM_BBU1 | C01_1142CA_PH17 | Bronze | Old Sites (Before 2015) | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | faulty A/C | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 10% | 61.5%
356414 | 1144787 | I-CTYSTR-COM_BBU1 | C01_1142CA_PH17 | Bronze | Old Sites (Before 2015) | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | B-17 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Wrong connection | Critical | loop over HT alarm | Sabotage | Contractor | M/D | Converged Run | - | - | 5% | 10% | 61.5%
356414 | 1144793 | I-CTYSTR-COM_BBU1 | C01_1142CA_PH17 | Bronze | Old Sites (Before 2015) | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | C-15 | Fire System | Fire Alarm and Fighting System | Components faulty | Critical | faulty FP | Contractor | Contractor | M/D | Converged Run | - | - | 2.5% | 10% | 61.5%
356414 | 1144786 | I-CTYSTR-COM_BBU1 | C01_1142CA_PH17 | Bronze | Old Sites (Before 2015) | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | C-17 | Fire System | Fire Alarm and Fighting System | Wrong connection | Critical | loop over fire alarm | Sabotage | Contractor | M/D | Converged Run | - | - | 2.5% | 10% | 61.5%
356414 | 1144782 | I-CTYSTR-COM_BBU1 | C01_1142CA_PH17 | Bronze | Old Sites (Before 2015) | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | C-60 | Fire System | Fire Alarm and Fighting System | Fire extinguisher missing/empty/expired/(safety seal) | Critical | expired | Contractor | Contractor | M/D | Converged Run | - | - | 2.5% | 10% | 61.5%
356414 | 1144794 | I-CTYSTR-COM_BBU1 | C01_1142CA_PH17 | Bronze | Old Sites (Before 2015) | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | C-7 | Fire System | Fire Alarm and Fighting System | Unit unfixed/not installed well | Critical | Fire panel unfixed | Aging | Contractor | M/D | Converged Run | - | - | 2.5% | 10% | 61.5%
356414 | 1144795 | I-CTYSTR-COM_BBU1 | C01_1142CA_PH17 | Bronze | Old Sites (Before 2015) | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | D-7 | Equipment and DDF | Equipment and DDF | Unit unfixed/not installed well | Critical | rack unfixed | Aging | Contractor | M/D | Converged Run | - | - | 3.5% | 7% | 61.5%
356413 | 1144774 | GOLDEN-PYRAMDS | C1_0531CA_PH4 | Silver | Nodal/VIP | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | faulty A/c | Aging | Contractor | M/D | Converged Run | - | - | 6% | 12% | 62%
356413 | 1144773 | GOLDEN-PYRAMDS | C1_0531CA_PH4 | Silver | Nodal/VIP | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | B-7 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Unit unfixed/not installed well | Critical | sensor unfixed | Aging | Contractor | M/D | Converged Run | - | - | 6% | 12% | 62%
356413 | 1144765 | GOLDEN-PYRAMDS | C1_0531CA_PH4 | Silver | Nodal/VIP | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | C-60 | Fire System | Fire Alarm and Fighting System | Fire extinguisher missing/empty/expired/(safety seal) | Critical | expired | Contractor | Contractor | M/D | Converged Run | - | - | 10% | 10% | 62%
356412 | 1144752 | M-ANDREA | C1_1154CA_PH8 | Bronze | Old Sites (Before 2015) | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | C-60 | Fire System | Fire Alarm and Fighting System | Fire extinguisher missing/empty/expired/(safety seal) | Critical | expired | Contractor | Contractor | M/D | Converged Run | - | - | 10% | 10% | 76%
356411 | 1144740 | I-MARIOT-MRAGE_BBU1 | C01_1118CA_PH05 | Silver | Nodal/VIP | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | B-17 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Wrong connection | Critical | loop over A/C fail alarm | Sabotage | Contractor | M/D | Converged Run | - | - | 10% | 10% | 71%
356411 | 1144739 | I-MARIOT-MRAGE_BBU1 | C01_1118CA_PH05 | Silver | Nodal/VIP | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | C-60 | Fire System | Fire Alarm and Fighting System | Fire extinguisher missing/empty/expired/(safety seal) | Critical | expired | Contractor | Contractor | M/D | Converged Run | - | - | 10% | 10% | 71%
356411 | 1144744 | I-MARIOT-MRAGE_BBU1 | C01_1118CA_PH05 | Silver | Nodal/VIP | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | E-1-33 | Civil | Shelter Body / Main Enclosure | Trays covers missing/unfixed (if laid on the ground only) | Critical | covers unfixed/missing | Converged Run | Contractor | M/D | Converged Run | - | - | 2.25% | 9% | 71%
356411 | 1144743 | I-MARIOT-MRAGE_BBU1 | C01_1118CA_PH05 | Silver | Nodal/VIP | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | E-1-8 | Civil | Shelter Body / Main Enclosure | Door/frame fixation that affects door from open easily or close firmly | Critical | door frame to be fixed | Aging | Contractor | M/D | Converged Run | - | - | 2.25% | 9% | 71%
356391 | 1143603 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-1-12 | Power System | Power Meter & Main Breaker | Unit earth | Critical | Stolen earth connections of the MFP | Stealth | Contractor | M/D | Converged Run | - | - | 2.5% | 5% | 20%
356391 | 1143632 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-1-20 | Power System | Power Meter & Main Breaker | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Critical | Main power cable isn't protected (Broken conduits) | Aging | Contractor | M/D | Converged Run | - | - | 2.5% | 5% | 20%
356391 | 1143608 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-3-12 | Power System | GEDP | Unit earth | Critical | Stolen earth connections of the GEDP | Stealth | Contractor | M/D | Converged Run | - | - | 2% | 7.5% | 20%
356391 | 1143609 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-3-23 | Power System | GEDP | Cables termination/lugs (AC side), lugs (DC side) | Critical | Two cables are connected to same slots of CBs and missing terminals | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 7.5% | 20%
356391 | 1143613 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-4-12 | Power System | Surge Arrestor | Unit earth | Critical | Stolen earth connections of the surge arrestors | Stealth | Contractor | M/D | Converged Run | - | - | 2% | 5.833% | 20%
356391 | 1143618 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-6-19 | Power System | Rectifiers | Alarms reporting to the OMC | Critical | Major and minor alarms don't appear on the OMC (Loop in DDF) | Sabotage | Contractor | M/D | Converged Run | - | - | 2% | 8% | 20%
356391 | 1143622 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-7-41 | Power System | Batteries | Some parts are (missing / stolen) | Critical | Batteries and cables are stolen | Stealth | Converged Run | M/D | Converged Run | - | - | 2.5% | 2.5% | 20%
356391 | 1143631 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | B-12 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Unit earth | Critical | Stolen earth connections of the ODU | Stealth | Contractor | M/D | Converged Run | - | - | 1.714% | 12% | 20%
356391 | 1143626 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | B-23 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Cables termination/lugs (AC side), lugs (DC side) | Critical | Missing terminals of cables inside IDU and ODU | Contractor | Contractor | M/D | Converged Run | - | - | 1.714% | 12% | 20%
356391 | 1143604 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | B-41 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Some parts are (missing / stolen) | Critical | A/C2 is stolen | Stealth | Contractor | M/D | Converged Run | - | - | 1.714% | 12% | 20%
356391 | 1143633 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | C-15 | Fire System | Fire Alarm and Fighting System | Components faulty | Critical | The fire panel is faulty | Aging | Contractor | M/D | Converged Run | - | - | 3.333% | 10% | 20%
356391 | 1143636 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | C-60 | Fire System | Fire Alarm and Fighting System | Fire extinguisher missing/empty/expired/(safety seal) | Critical | Expired date of the fire extinguisher | Contractor | Contractor | M/D | Converged Run | - | - | 3.333% | 10% | 20%
356391 | 1143645 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | E-1-19 | Civil | Shelter Body / Main Enclosure | Alarms reporting to the OMC | Critical | Loop on the HTalarm in DDF | Sabotage | Contractor | M/D | Converged Run | - | - | 3% | 9% | 20%
356391 | 1143654 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | E-3-66 | Civil | Fence / Roof | Flammable junk/trash inside/outside (e.g. plastics, papers, cartoon boxes, etc…) | Critical | Flammable materials arround the shelter | Guard | Converged Run | M/D | Converged Run | - | - | 7% | 7% | 20%
356365 | 1142906 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-17 | Power System | Power Meter & Main Breaker | Wrong connection | Critical | wrong connections | Guard | Converged Run | M/D | Converged Run | - | - | 5% | 5% | 20.33%
356365 | 1142864 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-22 | Power System | GEDP | Cables/Feeders/Jumpers/Coaxial/FO/PCM connection tightness | Critical | loose blue cables connections | Contractor | Contractor | M/D | Converged Run | - | - | 10% | 10.67% | 20.33%
356365 | 1142899 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-5-7 | Power System | DC Boxes | Unit unfixed/not installed well | Critical | fix | Aging | Contractor | M/D | Converged Run | - | - | 2% | 4% | 20.33%
356365 | 1142897 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-51 | Power System | Rectifiers | Batteries charging current unlimited per the manufacturer specs | Critical | adjust | Contractor | Contractor | M/D | Converged Run | - | - | 1.6% | 8% | 20.33%
356365 | 1142895 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-7 | Power System | Rectifiers | Unit unfixed/not installed well | Critical | fix | Aging | Contractor | M/D | Converged Run | - | - | 1.6% | 8% | 20.33%
356365 | 1142916 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | B-12 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Unit earth | Critical | not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 20.33%
356365 | 1142903 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | faulty A/C and fix cover | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 20.33%
356365 | 1142912 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | B-7 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Unit unfixed/not installed well | Critical | fix | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 20.33%
356365 | 1142880 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-10 | Civil | Shelter Body / Main Enclosure | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…) | Critical | seal | Converged Run | Contractor | M/D | Converged Run | - | - | 1.5% | 9% | 20.33%
356365 | 1142902 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-19 | Civil | Shelter Body / Main Enclosure | Alarms reporting to the OMC | Critical | fix door sensor | Aging | Contractor | M/D | Converged Run | - | - | 1.5% | 9% | 20.33%
356365 | 1142965 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-66 | Civil | Shelter Body / Main Enclosure | Flammable junk/trash inside/outside (e.g. plastics, papers, cartoon boxes, etc…) | Critical | clean | Contractor | Contractor | M/D | Converged Run | - | - | 1.5% | 9% | 20.33%
356365 | 1142868 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-15 | Civil | Antenna Support | Components faulty | Critical | ZTE camera is not working | Aging | Contractor | M/D | Converged Run | - | - | 1% | 7% | 20.33%
356365 | 1142946 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-77 | Civil | Antenna Support | Climbing safety wire | Critical | arrange from cables and attach to its supports | Converged Run | Contractor | M/D | Converged Run | - | - | 1% | 7% | 20.33%
356365 | 1142938 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-78 | Civil | Antenna Support | Earth connected to antennas & MW ODU | Critical | not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 1% | 7% | 20.33%
356365 | 1142910 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-66 | Civil | Fence / Roof | Flammable junk/trash inside/outside (e.g. plastics, papers, cartoon boxes, etc…) | Critical | remove | Contractor | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 20.33%
356365 | 1142959 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | F-12 | Generator | ATS / Engine | Unit earth | Critical | not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 2% | 10% | 20.33%
356365 | 1142960 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | F-41 | Generator | ATS / Engine | Some parts are (missing / stolen) | Critical | stolen battery | Stealth | Contractor | M/D | Converged Run | - | - | 2% | 10% | 20.33%
356364 | 1142798 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-20 | Power System | Power Meter & Main Breaker | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Critical | protect | Contractor | Contractor | M/D | Converged Run | - | - | 1.667% | 5% | 13.64%
356364 | 1142807 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-31 | Power System | Power Meter & Main Breaker | Trays/ducts/conduits unfixed | Critical | fix | Contractor | Contractor | M/D | Converged Run | - | - | 1.667% | 5% | 13.64%
356364 | 1142796 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-12 | Power System | GEDP | Unit earth | Critical | not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 3% | 12% | 13.64%
356364 | 1142795 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-16 | Power System | GEDP | Components below/over rate (excluding main power feeder if not hot) | Critical | high rate | Contractor | Contractor | M/D | Converged Run | - | - | 3% | 12% | 13.64%
356364 | 1142753 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-17 | Power System | GEDP | Wrong connection | Critical | two cables in one slote | Contractor | Contractor | M/D | Converged Run | - | - | 3% | 12% | 13.64%
356364 | 1142805 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-4-15 | Power System | Surge Arrestor | Components faulty | Critical | replace cable | Aging | Contractor | M/D | Converged Run | - | - | 2.5% | 7.833% | 13.64%
356364 | 1142804 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-4-7 | Power System | Surge Arrestor | Unit unfixed/not installed well | Critical | turn on RCCB | Contractor | Contractor | M/D | Converged Run | - | - | 3.333% | 7.833% | 13.64%
356364 | 1142838 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-5-7 | Power System | DC Boxes | Unit unfixed/not installed well | Critical | fix | Aging | Contractor | M/D | Converged Run | - | - | 1.333% | 4% | 13.64%
356364 | 1142764 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-12 | Power System | Rectifiers | Unit earth | Critical | not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 1.6% | 8% | 13.64%
356364 | 1142765 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-15 | Power System | Rectifiers | Components faulty | Critical | faulty module | Contractor | Contractor | M/D | Converged Run | - | - | 1.6% | 8% | 13.64%
356364 | 1142808 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | B-12 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Unit earth | Critical | not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 1.714% | 12% | 13.64%
356364 | 1142853 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | faulty | Aging | Converged Run | M/D | Converged Run | - | - | 1.714% | 12% | 13.64%
356364 | 1142844 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | B-17 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Wrong connection | Critical | wrong connections | Contractor | Contractor | M/D | Converged Run | - | - | 1.714% | 12% | 13.64%
356364 | 1142810 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | B-41 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Some parts are (missing / stolen) | Critical | covers missing | Contractor | Contractor | M/D | Converged Run | - | - | 1.714% | 12% | 13.64%
356364 | 1142809 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | B-7 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Unit unfixed/not installed well | Critical | fix | Contractor | Contractor | M/D | Converged Run | - | - | 1.714% | 12% | 13.64%
356364 | 1142786 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | C-15 | Fire System | Fire Alarm and Fighting System | Components faulty | Critical | faulty and need cleaning | Contractor | Contractor | M/D | Converged Run | - | - | 3.333% | 10% | 13.64%
356364 | 1142794 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | C-60 | Fire System | Fire Alarm and Fighting System | Fire extinguisher missing/empty/expired/(safety seal) | Critical | expired | Contractor | Contractor | M/D | Converged Run | - | - | 3.333% | 10% | 13.64%
356364 | 1142789 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-10 | Civil | Shelter Body / Main Enclosure | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…) | Critical | seal | Converged Run | Contractor | M/D | Converged Run | - | - | 1.286% | 9% | 13.64%
356364 | 1142832 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-8 | Civil | Shelter Body / Main Enclosure | Door/frame fixation that affects door from open easily or close firmly | Critical | seal | Aging | Contractor | M/D | Converged Run | - | - | 1.286% | 9% | 13.64%
356364 | 1142812 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-77 | Civil | Antenna Support | Climbing safety wire | Critical | rusty | Aging | Converged Run | M/D | Converged Run | - | - | 0.7778% | 7% | 13.64%
356364 | 1142811 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-78 | Civil | Antenna Support | Earth connected to antennas & MW ODU | Critical | not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 0.7778% | 7% | 13.64%
356364 | 1142828 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-66 | Civil | Fence / Roof | Flammable junk/trash inside/outside (e.g. plastics, papers, cartoon boxes, etc…) | Critical | clean | Guard | Contractor | M/D | Converged Run | - | - | 3.5% | 7% | 13.64%
356357 | 1142629 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-1-12 | Power System | Power Meter & Main Breaker | Unit earth | Critical | Earth cable of 100A Box door disconnected | Aging | Contractor | M/D | Converged Run | - | - | 0.8333% | 5% | 35%
356357 | 1142631 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-1-17 | Power System | Power Meter & Main Breaker | Wrong connection | Critical | Earth cable & Neutral cable connected to the same bar | Contractor | Contractor | M/D | Converged Run | - | - | 0.8333% | 5% | 35%
356357 | 1142635 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-3-23 | Power System | GEDP | Cables termination/lugs (AC side), lugs (DC side) | Critical | Power cable has no terminal | Contractor | Contractor | M/D | Converged Run | - | - | 4% | 12% | 35%
356357 | 1142638 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-3-7 | Power System | GEDP | Unit unfixed/not installed well | Critical | GEDP cover not fixed | Aging | Contractor | M/D | Converged Run | - | - | 4% | 12% | 35%
356357 | 1142645 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-6-12 | Power System | Rectifiers | Unit earth | Critical | Rectifier earth cable disconnected | Stealth | Contractor | M/D | Converged Run | - | - | 2.667% | 8% | 35%
356357 | 1142646 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-6-19 | Power System | Rectifiers | Alarms reporting to the OMC | Critical | Rectifier minor alarm not report the OMC | Aging | Contractor | M/D | Converged Run | - | - | 2.667% | 8% | 35%
356357 | 1142670 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | B-12 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Unit earth | Critical | A/C ODU not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 2% | 12% | 35%
356357 | 1142659 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | A/C 1,2 not work , please replay with current reading | Aging | Contractor | M/D | Converged Run | - | - | 2% | 12% | 35%
356357 | 1142658 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | B-17 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Wrong connection | Critical | Wrong connection welded cable , & missing control card | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 12% | 35%
356357 | 1142664 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | B-41 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Some parts are (missing / stolen) | Critical | Unfixed power cable cover | Aging | Contractor | M/D | Converged Run | - | - | 2% | 12% | 35%
356357 | 1142666 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | B-7 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Unit unfixed/not installed well | Critical | A/C ODU cover not fixed | Aging | Contractor | M/D | Converged Run | - | - | 2% | 12% | 35%
356357 | 1142672 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | C-15 | Fire System | Fire Alarm and Fighting System | Components faulty | Critical | Fire panel not work ( Defected battery ) | Aging | Contractor | M/D | Converged Run | - | - | 5% | 5% | 35%
356357 | 1142679 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | E-1-9 | Civil | Shelter Body / Main Enclosure | Door lock/handle that affects door from open easily or close firmly | Critical | Shelter door open , due to defected A/C1 & A/C2 | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 7% | 35%
356357 | 1142698 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | E-2-33 | Civil | Antenna Support | Trays covers missing/unfixed (if laid on the ground only) | Critical | Cable tray cover not fixed | Aging | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 35%
356357 | 1142700 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | E-2-77 | Civil | Antenna Support | Climbing safety wire | Critical | Safety wire rusty | Aging | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 35%
356349 | 1141772 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-17 | Power System | Power Meter & Main Breaker | Wrong connection | Critical | wrong connection , remove and install CB 10A instead | Guard | Contractor | M/D | Converged Run | - | - | 0.8333% | 5% | 53.83%
356349 | 1141760 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-23 | Power System | Power Meter & Main Breaker | Cables termination/lugs (AC side), lugs (DC side) | Critical | termination is needed | Contractor | Contractor | M/D | Converged Run | - | - | 0.8333% | 5% | 53.83%
356349 | 1141766 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-31 | Power System | Power Meter & Main Breaker | Trays/ducts/conduits unfixed | Critical | fix | Contractor | Contractor | M/D | Converged Run | - | - | 0.8333% | 5% | 53.83%
356349 | 1141745 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-15 | Power System | Rectifiers | Components faulty | Critical | faulty surge | Electricity Company | Converged Run | M/D | Converged Run | - | - | 2.667% | 8% | 53.83%
356349 | 1141775 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-52 | Power System | Rectifiers | Temperature sensor not inserted between batteries (if applicable) | Critical | disconnecetd sensor | Contractor | Contractor | M/D | Converged Run | - | - | 2.667% | 8% | 53.83%
356349 | 1141743 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | C-15 | Fire System | Fire Alarm and Fighting System | Components faulty | Critical | faulty panel | Contractor | Contractor | M/D | Converged Run | - | - | 2.5% | 2.5% | 53.83%
356349 | 1141767 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | D-15 | Equipment and DDF | Equipment and DDF | Components faulty | Critical | faulty sensors | Aging | Contractor | M/D | Converged Run | - | - | 2.5% | 5.667% | 53.83%
356349 | 1141783 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-78 | Civil | Antenna Support | Earth connected to antennas & MW ODU | Critical | tower is not earthed and as well all antennas and MW links | Stealth | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 53.83%
356349 | 1141785 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-66 | Civil | Fence / Roof | Flammable junk/trash inside/outside (e.g. plastics, papers, cartoon boxes, etc…) | Critical | clean | Aging | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 53.83%
356346 | 1141370 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-1-12 | Power System | Power Meter & Main Breaker | Unit earth | Critical | The power meter panel isn't earthed | Converged Run | Contractor | M/D | Converged Run | - | - | 1% | 5% | 28.5%
356346 | 1141367 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-1-23 | Power System | Power Meter & Main Breaker | Cables termination/lugs (AC side), lugs (DC side) | Critical | Missing terminals of power cables inside the power meter panel | Converged Run | Contractor | M/D | Converged Run | - | - | 1% | 5% | 28.5%
356346 | 1141410 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-2-11 | Power System | Shared Panel | Unit sharp edges | Critical | Sharp edges of the shared panel | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 4% | 28.5%
356346 | 1141371 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-3-12 | Power System | GEDP | Unit earth | Critical | Stolen earth connections of the GEDP | Stealth | Contractor | M/D | Converged Run | - | - | 2% | 4.5% | 28.5%
356346 | 1141378 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-4-12 | Power System | Surge Arrestor | Unit earth | Critical | Missing earth connections between surge arrestors | Stealth | Contractor | M/D | Converged Run | - | - | 2% | 9% | 28.5%
356346 | 1141379 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-6-15 | Power System | Rectifiers | Components faulty | Critical | One surge arrestor is defected | Aging | Contractor | M/D | Converged Run | - | - | 2.667% | 8% | 28.5%
356346 | 1141381 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-6-51 | Power System | Rectifiers | Batteries charging current unlimited per the manufacturer specs | Critical | I battery max. should be adjusted to 75 A. (3*170 Ah battery strings) | Contractor | Contractor | M/D | Converged Run | - | - | 2.667% | 8% | 28.5%
356346 | 1141388 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | B-22 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Cables/Feeders/Jumpers/Coaxial/FO/PCM connection tightness | Critical | Loose connection of a control cable connected inside ODU2 (also the Y connection is not clear to be connected) | Contractor | Contractor | M/D | Converged Run | - | - | 6% | 12% | 28.5%
356346 | 1141389 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | C-15 | Fire System | Fire Alarm and Fighting System | Components faulty | Critical | The fire panel is faulty | Aging | Contractor | M/D | Converged Run | - | - | 5% | 5% | 28.5%
356346 | 1141397 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | E-1-66 | Civil | Shelter Body / Main Enclosure | Flammable junk/trash inside/outside (e.g. plastics, papers, cartoon boxes, etc…) | Critical | Flammable materials inside the shelter | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 9% | 28.5%
356346 | 1141403 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | E-2-31 | Civil | Antenna Support | Trays/ducts/conduits unfixed | Critical | Supports of trays are not fixed well | Contractor | Contractor | M/D | Converged Run | - | - | 1.4% | 7% | 28.5%
356346 | 1141407 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | E-3-66 | Civil | Fence / Roof | Flammable junk/trash inside/outside (e.g. plastics, papers, cartoon boxes, etc…) | Critical | Flammable materials outside the shelter | ET | Converged Run | M/D | Converged Run | - | - | 5% | 5% | 28.5%
356345 | 1141579 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-12 | Power System | Power Meter & Main Breaker | Unit earth | Critical | not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 0.7143% | 5% | 18.42%
356345 | 1141573 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-31 | Power System | Power Meter & Main Breaker | Trays/ducts/conduits unfixed | Critical | fix | Aging | Contractor | M/D | Converged Run | - | - | 0.7143% | 5% | 18.42%
356345 | 1141574 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-7 | Power System | Power Meter & Main Breaker | Unit unfixed/not installed well | Critical | fix | Electricity Company | Contractor | M/D | Converged Run | - | - | 0.7143% | 5% | 18.42%
356345 | 1141519 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-16 | Power System | GEDP | Components below/over rate (excluding main power feeder if not hot) | Critical | high temp rate | Contractor | Contractor | M/D | Converged Run | - | - | 6% | 12% | 18.42%
356345 | 1141521 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-22 | Power System | GEDP | Cables/Feeders/Jumpers/Coaxial/FO/PCM connection tightness | Critical | loose | Contractor | Contractor | M/D | Converged Run | - | - | 6% | 12% | 18.42%
356345 | 1141520 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-4-3 | Power System | Surge Arrestor | Panel/cables secured location/route (e.g. Surge panel outside the shelter or far away from other panels) | Critical | relocate | Converged Run | Converged Run | M/D | Converged Run | - | - | 10% | 10% | 18.42%
356345 | 1141522 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-5-7 | Power System | DC Boxes | Unit unfixed/not installed well | Critical | turn on | Electricity Company | Contractor | M/D | Converged Run | - | - | 2.5% | 2.5% | 18.42%
356345 | 1141584 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-12 | Power System | Rectifiers | Unit earth | Critical | wrong earth connection | Contractor | Contractor | M/D | Converged Run | - | - | 1.333% | 8% | 18.42%
356345 | 1141543 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-15 | Power System | Rectifiers | Components faulty | Critical | faulty surge | Electricity Company | Converged Run | M/D | Converged Run | - | - | 1.333% | 8% | 18.42%
356345 | 1141533 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-52 | Power System | Rectifiers | Temperature sensor not inserted between batteries (if applicable) | Critical | insteal beyween batteries | Contractor | Contractor | M/D | Converged Run | - | - | 1.333% | 8% | 18.42%
356345 | 1141532 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-7-41 | Power System | Batteries | Some parts are (missing / stolen) | Critical | stolen batteries | Stealth | Converged Run | M/D | Converged Run | - | - | 3.333% | 3.333% | 18.42%
356345 | 1141540 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | B-7 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Unit unfixed/not installed well | Critical | 4 energy is disconnected | Contractor | Contractor | M/D | Converged Run | - | - | 2.5% | 10.75% | 18.42%
356345 | 1141528 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | D-15 | Equipment and DDF | Equipment and DDF | Components faulty | Critical | not working | Aging | Contractor | M/D | Converged Run | - | - | 1% | 7% | 18.42%
356345 | 1141545 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-10 | Civil | Shelter Body / Main Enclosure | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…) | Critical | seal | Converged Run | Contractor | M/D | Converged Run | - | - | 1.8% | 9% | 18.42%
356345 | 1141530 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-7 | Civil | Shelter Body / Main Enclosure | Unit unfixed/not installed well | Critical | unfixed roxtec | Converged Run | Contractor | M/D | Converged Run | - | - | 1.8% | 9% | 18.42%
356345 | 1141585 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-9 | Civil | Shelter Body / Main Enclosure | Door lock/handle that affects door from open easily or close firmly | Critical | no lock | Contractor | Contractor | M/D | Converged Run | - | - | 1.8% | 9% | 18.42%
356345 | 1141567 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-77 | Civil | Antenna Support | Climbing safety wire | Critical | fix | Aging | Contractor | M/D | Converged Run | - | - | 1.4% | 7% | 18.42%
356345 | 1141517 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-66 | Civil | Fence / Roof | Flammable junk/trash inside/outside (e.g. plastics, papers, cartoon boxes, etc…) | Critical | remove | Aging | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 18.42%
356344 | 1141352 | 6OCT-DIPLOMAT | C2_0882UP_PH12 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-12 | Power System | GEDP | Unit earth | Critical | not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 5% | 7% | 36%
356344 | 1141324 | 6OCT-DIPLOMAT | C2_0882UP_PH12 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-7 | Power System | Rectifiers | Unit unfixed/not installed well | Critical | fix cover | Aging | Contractor | M/D | Converged Run | - | - | 8% | 8% | 36%
356344 | 1141323 | 6OCT-DIPLOMAT | C2_0882UP_PH12 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | faulty A/C and disconnected | Contractor | Contractor | M/D | Converged Run | - | - | 10% | 10% | 36%
356344 | 1141353 | 6OCT-DIPLOMAT | C2_0882UP_PH12 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | C-60 | Fire System | Fire Alarm and Fighting System | Fire extinguisher missing/empty/expired/(safety seal) | Critical | fake certification | Contractor | Contractor | M/D | Converged Run | - | - | 10% | 10% | 36%
356344 | 1141327 | 6OCT-DIPLOMAT | C2_0882UP_PH12 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-10 | Civil | Shelter Body / Main Enclosure | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…) | Critical | seal | Converged Run | Contractor | M/D | Converged Run | - | - | 1.5% | 9% | 36%
356344 | 1141346 | 6OCT-DIPLOMAT | C2_0882UP_PH12 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-33 | Civil | Shelter Body / Main Enclosure | Trays covers missing/unfixed (if laid on the ground only) | Critical | fix cover | Aging | Contractor | M/D | Converged Run | - | - | 1.5% | 9% | 36%
356344 | 1141318 | 6OCT-DIPLOMAT | C2_0882UP_PH12 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-9 | Civil | Shelter Body / Main Enclosure | Door lock/handle that affects door from open easily or close firmly | Critical | faulty lock and found cabinet open | Contractor | Contractor | M/D | Converged Run | - | - | 1.5% | 9% | 36%
356344 | 1141347 | 6OCT-DIPLOMAT | C2_0882UP_PH12 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-77 | Civil | Antenna Support | Climbing safety wire | Critical | not fixed well | Aging | Contractor | M/D | Converged Run | - | - | 2.333% | 7% | 36%
356343 | 1141301 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-12 | Power System | Power Meter & Main Breaker | Unit earth | Critical | not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 1.25% | 5% | 31.33%
356343 | 1141308 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-31 | Power System | Power Meter & Main Breaker | Trays/ducts/conduits unfixed | Critical | fix or replace | Contractor | Contractor | M/D | Converged Run | - | - | 1.25% | 5% | 31.33%
356343 | 1141273 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-4-3 | Power System | Surge Arrestor | Panel/cables secured location/route (e.g. Surge panel outside the shelter or far away from other panels) | Critical | relocate | Converged Run | Converged Run | M/D | Converged Run | - | - | 10% | 10% | 31.33%
356343 | 1141287 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-7-41 | Power System | Batteries | Some parts are (missing / stolen) | Critical | stolen batteries | Stealth | Converged Run | M/D | Converged Run | - | - | 3.333% | 3.333% | 31.33%
356343 | 1141306 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | B-12 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Unit earth | Critical | disconnected earth , clear earth plate | Contractor | Contractor | M/D | Converged Run | - | - | 4% | 12% | 31.33%
356343 | 1141288 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | 4Energy stem is not working | Converged Run | Converged Run | M/D | Converged Run | - | - | 4% | 12% | 31.33%
356343 | 1141284 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | B-7 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Unit unfixed/not installed well | Critical | fix | Contractor | Contractor | M/D | Converged Run | - | - | 4% | 12% | 31.33%
356343 | 1141282 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | C-15 | Fire System | Fire Alarm and Fighting System | Components faulty | Critical | faulty batteries | Contractor | Contractor | M/D | Converged Run | - | - | 3.333% | 5.833% | 31.33%
356343 | 1141278 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | D-15 | Equipment and DDF | Equipment and DDF | Components faulty | Critical | ZTE system isn't operate | Converged Run | Converged Run | M/D | Converged Run | - | - | 1.75% | 7% | 31.33%
356343 | 1141305 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-66 | Civil | Fence / Roof | Flammable junk/trash inside/outside (e.g. plastics, papers, cartoon boxes, etc…) | Critical | remove | Guard | Converged Run | M/D | Converged Run | - | - | 7% | 7% | 31.33%
356342 | 1140572 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-12 | Power System | Power Meter & Main Breaker | Unit earth | Critical | not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 1% | 5% | 44.17%
356342 | 1140598 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-31 | Power System | Power Meter & Main Breaker | Trays/ducts/conduits unfixed | Critical | fix | Aging | Contractor | M/D | Converged Run | - | - | 1% | 5% | 44.17%
356342 | 1140570 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-12 | Power System | GEDP | Unit earth | Critical | not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 3.333% | 5.833% | 44.17%
356342 | 1140565 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-7 | Power System | GEDP | Unit unfixed/not installed well | Critical | replace by metal one | Aging | Contractor | M/D | Converged Run | - | - | 2.5% | 5.833% | 44.17%
356342 | 1140591 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | C-60 | Fire System | Fire Alarm and Fighting System | Fire extinguisher missing/empty/expired/(safety seal) | Critical | need to test | Contractor | Contractor | M/D | Converged Run | - | - | 3.333% | 10% | 44.17%
356342 | 1140590 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | C-7 | Fire System | Fire Alarm and Fighting System | Unit unfixed/not installed well | Critical | remove the fire extinguisher and reinstall in its place | Aging | Contractor | M/D | Converged Run | - | - | 3.333% | 10% | 44.17%
356342 | 1140581 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-19 | Civil | Shelter Body / Main Enclosure | Alarms reporting to the OMC | Critical | door sensor looped | Contractor | Contractor | M/D | Converged Run | - | - | 1.5% | 9% | 44.17%
356342 | 1140580 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-7 | Civil | Shelter Body / Main Enclosure | Unit unfixed/not installed well | Critical | fix hook | Contractor | Contractor | M/D | Converged Run | - | - | 1.5% | 9% | 44.17%
356342 | 1140575 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-9 | Civil | Shelter Body / Main Enclosure | Door lock/handle that affects door from open easily or close firmly | Critical | faulty lock | Contractor | Contractor | M/D | Converged Run | - | - | 1.5% | 9% | 44.17%
356342 | 1140587 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-7 | Civil | Antenna Support | Unit unfixed/not installed well | Critical | adjust the camera direction | Aging | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 44.17%
356342 | 1140592 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-77 | Civil | Antenna Support | Climbing safety wire | Critical | need to fix well | Contractor | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 44.17%
356342 | 1140604 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-66 | Civil | Fence / Roof | Flammable junk/trash inside/outside (e.g. plastics, papers, cartoon boxes, etc…) | Critical | remove | Guard | Converged Run | M/D | Converged Run | - | - | 2.333% | 7% | 44.17%
356341 | 1140632 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-11 | Power System | Power Meter & Main Breaker | Unit sharp edges | Critical | sharp edges | Contractor | Contractor | M/D | Converged Run | - | - | 0.625% | 5% | 43%
356341 | 1140633 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-12 | Power System | Power Meter & Main Breaker | Unit earth | Critical | disconnected earth | Aging | Contractor | M/D | Converged Run | - | - | 0.625% | 5% | 43%
356341 | 1140623 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-17 | Power System | Power Meter & Main Breaker | Wrong connection | Critical | remove wrong connection | Guard | Converged Run | M/D | Converged Run | - | - | 0.625% | 5% | 43%
356341 | 1140624 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-20 | Power System | Power Meter & Main Breaker | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Critical | protect cables | Contractor | Contractor | M/D | Converged Run | - | - | 0.625% | 5% | 43%
356341 | 1140627 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-31 | Power System | Power Meter & Main Breaker | Trays/ducts/conduits unfixed | Critical | fix | Aging | Contractor | M/D | Converged Run | - | - | 0.625% | 5% | 43%
356341 | 1140612 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-5-7 | Power System | DC Boxes | Unit unfixed/not installed well | Critical | fix CBs and cover | Converged Run | Contractor | M/D | Converged Run | - | - | 4% | 4% | 43%
356341 | 1140647 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | faulty A/C | Contractor | Contractor | M/D | Converged Run | - | - | 10% | 10% | 43%
356341 | 1140615 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-10 | Civil | Shelter Body / Main Enclosure | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…) | Critical | seal | Contractor | Contractor | M/D | Converged Run | - | - | 2.25% | 9% | 43%
356341 | 1140646 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-19 | Civil | Shelter Body / Main Enclosure | Alarms reporting to the OMC | Critical | alarm looped | Contractor | Contractor | M/D | Converged Run | - | - | 2.25% | 9% | 43%
356341 | 1140635 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-9 | Civil | Shelter Body / Main Enclosure | Door lock/handle that affects door from open easily or close firmly | Critical | no lock, install ASAP | Contractor | Contractor | M/D | Converged Run | - | - | 2.25% | 9% | 43%
356341 | 1140652 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-33 | Civil | Antenna Support | Trays covers missing/unfixed (if laid on the ground only) | Critical | fix | Converged Run | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 43%
356341 | 1140651 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-7 | Civil | Antenna Support | Unit unfixed/not installed well | Critical | fix | Aging | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 43%
356341 | 1140667 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-77 | Civil | Antenna Support | Climbing safety wire | Critical | not fixed | Converged Run | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 43%
356341 | 1140662 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-80 | Civil | Antenna Support | Palm tree fronds (broke/fall) | Critical | palm tree fronds missing | Aging | Converged Run | M/D | Converged Run | - | - | 1.167% | 7% | 43%
356341 | 1140665 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-9 | Civil | Fence / Roof | Door lock/handle that affects door from open easily or close firmly | Critical | no lock, install ASAP | Aging | Contractor | M/D | Converged Run | - | - | 3.5% | 7% | 43%
356340 | 1140444 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-20 | Power System | Power Meter & Main Breaker | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Critical | protect cable | Electricity Company | Contractor | M/D | Converged Run | - | - | 2.5% | 5% | 22.83%
356340 | 1140397 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-7 | Power System | GEDP | Unit unfixed/not installed well | Critical | turned CB | Contractor | Contractor | M/D | Converged Run | - | - | 2.5% | 2.5% | 22.83%
356340 | 1140394 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-4-3 | Power System | Surge Arrestor | Panel/cables secured location/route (e.g. Surge panel outside the shelter or far away from other panels) | Critical | relocate | Converged Run | Converged Run | M/D | Converged Run | - | - | 5% | 10% | 22.83%
356340 | 1140395 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-4-7 | Power System | Surge Arrestor | Unit unfixed/not installed well | Critical | turn on CB | Electricity Company | Contractor | M/D | Converged Run | - | - | 5% | 10% | 22.83%
356340 | 1140399 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-11 | Power System | Rectifiers | Unit sharp edges | Critical | sharp edge | Contractor | Contractor | M/D | Converged Run | - | - | 1.6% | 8% | 22.83%
356340 | 1140401 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-51 | Power System | Rectifiers | Batteries charging current unlimited per the manufacturer specs | Critical | adjust | Contractor | Contractor | M/D | Converged Run | - | - | 1.6% | 8% | 22.83%
356340 | 1140403 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-7 | Power System | Rectifiers | Unit unfixed/not installed well | Critical | fix | Contractor | Contractor | M/D | Converged Run | - | - | 1.6% | 8% | 22.83%
356340 | 1140456 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | B-23 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Cables termination/lugs (AC side), lugs (DC side) | Critical | missing cable termination | Contractor | Contractor | M/D | Converged Run | - | - | 10% | 10% | 22.83%
356340 | 1140396 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | C-15 | Fire System | Fire Alarm and Fighting System | Components faulty | Critical | faulty batteiers | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 10% | 22.83%
356340 | 1140452 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | D-15 | Equipment and DDF | Equipment and DDF | Components faulty | Critical | faulty 4 energy system | Converged Run | Converged Run | M/D | Converged Run | - | - | 5% | 6.667% | 22.83%
356340 | 1140422 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-10 | Civil | Shelter Body / Main Enclosure | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…) | Critical | seal | Converged Run | Contractor | M/D | Converged Run | - | - | 3% | 9% | 22.83%
356340 | 1140430 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-7 | Civil | Antenna Support | Unit unfixed/not installed well | Critical | fix door | Aging | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 22.83%
356339 | 1140531 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-20 | Power System | Power Meter & Main Breaker | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Critical | replace PVC | Aging | Contractor | M/D | Converged Run | - | - | 5% | 5% | 27%
356339 | 1140467 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-15 | Power System | GEDP | Components faulty | Critical | A/C1 and fire panel CBs found OFF | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 10% | 27%
356339 | 1140555 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-16 | Power System | GEDP | Components below/over rate (excluding main power feeder if not hot) | Critical | high temp rate | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 10% | 27%
356339 | 1140506 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-5-7 | Power System | DC Boxes | Unit unfixed/not installed well | Critical | fix | Aging | Contractor | M/D | Converged Run | - | - | 2% | 3% | 27%
356339 | 1140498 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-12 | Power System | Rectifiers | Unit earth | Critical | earth for surge is missing | Stealth | Contractor | M/D | Converged Run | - | - | 2.5% | 3.5% | 27%
356339 | 1140477 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | B-16 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components below/over rate (excluding main power feeder if not hot) | Critical | burned cables | Contractor | Contractor | M/D | Converged Run | - | - | 3% | 12% | 27%
356339 | 1140489 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | B-41 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Some parts are (missing / stolen) | Critical | cover | Contractor | Contractor | M/D | Converged Run | - | - | 3% | 12% | 27%
356339 | 1140501 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | B-7 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Unit unfixed/not installed well | Critical | fix | Aging | Contractor | M/D | Converged Run | - | - | 3% | 12% | 27%
356339 | 1140530 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | C-15 | Fire System | Fire Alarm and Fighting System | Components faulty | Critical | replace | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 10% | 27%
356339 | 1140493 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | C-17 | Fire System | Fire Alarm and Fighting System | Wrong connection | Critical | disconnected battery | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 10% | 27%
356339 | 1140500 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | C-60 | Fire System | Fire Alarm and Fighting System | Fire extinguisher missing/empty/expired/(safety seal) | Critical | expired | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 10% | 27%
356339 | 1140503 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | C-7 | Fire System | Fire Alarm and Fighting System | Unit unfixed/not installed well | Critical | fix | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 10% | 27%
356339 | 1140510 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | D-7 | Equipment and DDF | Equipment and DDF | Unit unfixed/not installed well | Critical | fix and arrange cables | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 6.5% | 27%
356339 | 1140537 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-10 | Civil | Shelter Body / Main Enclosure | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…) | Critical | seal | Converged Run | Contractor | M/D | Converged Run | - | - | 1.5% | 9% | 27%
356339 | 1140539 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-7 | Civil | Shelter Body / Main Enclosure | Unit unfixed/not installed well | Critical | tray need to fix | Converged Run | Contractor | M/D | Converged Run | - | - | 1.5% | 9% | 27%
356339 | 1140518 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-9 | Civil | Shelter Body / Main Enclosure | Door lock/handle that affects door from open easily or close firmly | Critical | lock found open | Contractor | Contractor | M/D | Converged Run | - | - | 1.5% | 9% | 27%
356339 | 1140499 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-78 | Civil | Antenna Support | Earth connected to antennas & MW ODU | Critical | equipment not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 1% | 7% | 27%
356338 | 1140379 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-17 | Power System | Power Meter & Main Breaker | Wrong connection | Critical | wrong connection | Guard | Converged Run | M/D | Converged Run | - | - | 2.5% | 5% | 5.5%
356338 | 1140269 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-16 | Power System | GEDP | Components below/over rate (excluding main power feeder if not hot) | Critical | high rate | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 5.5%
356338 | 1140268 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-7 | Power System | GEDP | Unit unfixed/not installed well | Critical | Fire panel CB turned off | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 5.5%
356338 | 1140267 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-4-3 | Power System | Surge Arrestor | Panel/cables secured location/route (e.g. Surge panel outside the shelter or far away from other panels) | Critical | relocate | Converged Run | Converged Run | M/D | Converged Run | - | - | 5% | 10% | 5.5%
356338 | 1140266 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-4-7 | Power System | Surge Arrestor | Unit unfixed/not installed well | Critical | turn on CB | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 10% | 5.5%
356338 | 1140319 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-5-7 | Power System | DC Boxes | Unit unfixed/not installed well | Critical | fix frame | Converged Run | Contractor | M/D | Converged Run | - | - | 1.667% | 4% | 5.5%
356338 | 1140309 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-11 | Power System | Rectifiers | Unit sharp edges | Critical | sharp edge | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 8% | 5.5%
356338 | 1140311 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-51 | Power System | Rectifiers | Batteries charging current unlimited per the manufacturer specs | Critical | adjust | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 8% | 5.5%
356338 | 1140336 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | B-41 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Some parts are (missing / stolen) | Critical | cover | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 5.5%
356338 | 1140340 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | B-7 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Unit unfixed/not installed well | Critical | fix covers | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 5.5%
356338 | 1140274 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | C-15 | Fire System | Fire Alarm and Fighting System | Components faulty | Critical | faulty batteries | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 10% | 5.5%
356338 | 1140321 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | C-60 | Fire System | Fire Alarm and Fighting System | Fire extinguisher missing/empty/expired/(safety seal) | Critical | fake date, need to test | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 10% | 5.5%
356338 | 1140375 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | D-15 | Equipment and DDF | Equipment and DDF | Components faulty | Critical | ZTE system is not working | Contractor | Contractor | M/D | Converged Run | - | - | 1.4% | 7% | 5.5%
356338 | 1140317 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | D-7 | Equipment and DDF | Equipment and DDF | Unit unfixed/not installed well | Critical | sensor not installed | Contractor | Contractor | M/D | Converged Run | - | - | 1.4% | 7% | 5.5%
356338 | 1140288 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-10 | Civil | Shelter Body / Main Enclosure | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…) | Critical | seal | Converged Run | Contractor | M/D | Converged Run | - | - | 1.286% | 9% | 5.5%
356338 | 1140281 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-17 | Civil | Shelter Body / Main Enclosure | Wrong connection | Critical | wrong connections | Contractor | Contractor | M/D | Converged Run | - | - | 1.286% | 9% | 5.5%
356338 | 1140371 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-8 | Civil | Shelter Body / Main Enclosure | Door/frame fixation that affects door from open easily or close firmly | Critical | seal | Aging | Contractor | M/D | Converged Run | - | - | 1.286% | 9% | 5.5%
356338 | 1140345 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-9 | Civil | Shelter Body / Main Enclosure | Door lock/handle that affects door from open easily or close firmly | Critical | faulty lock | Contractor | Contractor | M/D | Converged Run | - | - | 1.286% | 9% | 5.5%
356338 | 1140346 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-19 | Civil | Fence / Roof | Alarms reporting to the OMC | Critical | no gate sensor | Contractor | Contractor | M/D | Converged Run | - | - | 1.4% | 7% | 5.5%
356338 | 1140377 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-66 | Civil | Fence / Roof | Flammable junk/trash inside/outside (e.g. plastics, papers, cartoon boxes, etc…) | Critical | clean area around the shelter | Aging | Contractor | M/D | Converged Run | - | - | 1.4% | 7% | 5.5%
356338 | 1140347 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-8 | Civil | Fence / Roof | Door/frame fixation that affects door from open easily or close firmly | Critical | door need fixation | Aging | Contractor | M/D | Converged Run | - | - | 1.4% | 7% | 5.5%
356338 | 1140365 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | F-10 | Generator | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…) | Critical | check and clean | Contractor | Contractor | M/D | Converged Run | - | - | 1.25% | 10% | 5.5%
356338 | 1140360 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | F-17 | Generator | ATS / Engine | Wrong connection | Critical | two cables in one slote | Contractor | Contractor | M/D | Converged Run | - | - | 1.25% | 10% | 5.5%
356338 | 1140328 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | F-19 | Generator | ATS / Engine | Alarms reporting to the OMC | Critical | disconnect ZTE sensor cable | Contractor | Contractor | M/D | Converged Run | - | - | 1.25% | 10% | 5.5%
356338 | 1140361 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | F-23 | Generator | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side) | Critical | terminals need to replace | Contractor | Contractor | M/D | Converged Run | - | - | 1.25% | 10% | 5.5%
356338 | 1140356 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | F-7 | Generator | ATS / Engine | Unit unfixed/not installed well | Critical | battery not conencted | Contractor | Contractor | M/D | Converged Run | - | - | 1.25% | 10% | 5.5%
356337 | 1141135 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-1-7 | Power System | Power Meter & Main Breaker | Unit unfixed/not installed well | Critical | C.B not fixed | Aging | Contractor | M/D | Converged Run | - | - | 3.333% | 3.333% | 19.5%
356337 | 1141139 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-3-15 | Power System | GEDP | Components faulty | Critical | Power cable burnet | Aging | Contractor | M/D | Converged Run | - | - | 3% | 12% | 19.5%
356337 | 1141147 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-3-17 | Power System | GEDP | Wrong connection | Critical | Terminate the two cable should by double terminal | Aging | Contractor | M/D | Converged Run | - | - | 3% | 12% | 19.5%
356337 | 1141148 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-3-23 | Power System | GEDP | Cables termination/lugs (AC side), lugs (DC side) | Critical | Terminate the two cable should be by double terminal | Aging | Contractor | M/D | Converged Run | - | - | 3% | 12% | 19.5%
356337 | 1141151 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-4-12 | Power System | Surge Arrestor | Unit earth | Critical | Earth cable of surge is not connected direct to earth bar | Contractor | Contractor | M/D | Converged Run | - | - | 2.5% | 3.5% | 19.5%
356337 | 1141160 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-6-12 | Power System | Rectifiers | Unit earth | Critical | Earth cable disconnected | Stealth | Contractor | M/D | Converged Run | - | - | 2.5% | 6.833% | 19.5%
356337 | 1141162 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-6-19 | Power System | Rectifiers | Alarms reporting to the OMC | Critical | Rectifier 1,2 alarm not report the OMC | Aging | Contractor | M/D | Converged Run | - | - | 3.333% | 6.833% | 19.5%
356337 | 1141179 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | B-10 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…) | Critical | A/C ODU leakage water | Aging | Contractor | M/D | Converged Run | - | - | 3% | 12% | 19.5%
356337 | 1141182 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | C-60 | Fire System | Fire Alarm and Fighting System | Fire extinguisher missing/empty/expired/(safety seal) | Critical | Fire extinguisher missing expire date label | Contractor | Contractor | M/D | Converged Run | - | - | 10% | 10% | 19.5%
356337 | 1141214 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | D-19 | Equipment and DDF | Equipment and DDF | Alarms reporting to the OMC | Critical | H.T alarm not report the OMC | Aging | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 19.5%
356337 | 1141216 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | D-7 | Equipment and DDF | Equipment and DDF | Unit unfixed/not installed well | Critical | BTS Cover not fixed | Aging | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 19.5%
356337 | 1141221 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | E-1-7 | Civil | Shelter Body / Main Enclosure | Unit unfixed/not installed well | Critical | Rox Teck not isolated | Aging | Converged Run | M/D | Converged Run | - | - | 3.333% | 7.833% | 19.5%
356337 | 1141249 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | E-2-77 | Civil | Antenna Support | Climbing safety wire | Critical | Safety wire rusty | Aging | Converged Run | M/D | Converged Run | - | - | 2.333% | 7% | 19.5%
356330 | 1140240 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-12 | Power System | Power Meter & Main Breaker | Unit earth | Critical | not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 1.667% | 5% | 34.5%
356330 | 1140238 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-17 | Power System | Power Meter & Main Breaker | Wrong connection | Critical | remove wrong connection | Guard | Contractor | M/D | Converged Run | - | - | 1.667% | 5% | 34.5%
356330 | 1140201 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-12 | Power System | Rectifiers | Unit earth | Critical | disconnected earth | Contractor | Contractor | M/D | Converged Run | - | - | 2.5% | 5.5% | 34.5%
356330 | 1140202 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-7 | Power System | Rectifiers | Unit unfixed/not installed well | Critical | fix | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 5.5% | 34.5%
356330 | 1140195 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | faulty | Contractor | Contractor | M/D | Converged Run | - | - | 10% | 10% | 34.5%
356330 | 1140197 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | D-17 | Equipment and DDF | Equipment and DDF | Wrong connection | Critical | wrong connection for the alarms cables | Contractor | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 34.5%
356330 | 1140211 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | D-7 | Equipment and DDF | Equipment and DDF | Unit unfixed/not installed well | Critical | replace connectors by standard ones | Converged Run | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 34.5%
356330 | 1140204 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-10 | Civil | Shelter Body / Main Enclosure | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…) | Critical | seal | Contractor | Contractor | M/D | Converged Run | - | - | 1.286% | 9% | 34.5%
356330 | 1140206 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-19 | Civil | Shelter Body / Main Enclosure | Alarms reporting to the OMC | Critical | door alarm looped | Contractor | Contractor | M/D | Converged Run | - | - | 1.286% | 9% | 34.5%
356330 | 1140241 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-33 | Civil | Shelter Body / Main Enclosure | Trays covers missing/unfixed (if laid on the ground only) | Critical | fix covers | Contractor | Contractor | M/D | Converged Run | - | - | 1.286% | 9% | 34.5%
356330 | 1140242 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-7 | Civil | Shelter Body / Main Enclosure | Unit unfixed/not installed well | Critical | fix top part | Aging | Contractor | M/D | Converged Run | - | - | 1.286% | 9% | 34.5%
356330 | 1140249 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-7 | Civil | Antenna Support | Unit unfixed/not installed well | Critical | fix door | Aging | Contractor | M/D | Converged Run | - | - | 2% | 7% | 34.5%
356330 | 1140255 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-9 | Civil | Fence / Roof | Door lock/handle that affects door from open easily or close firmly | Critical | faulty lock | Contractor | Contractor | M/D | Converged Run | - | - | 3.5% | 7% | 34.5%
356330 | 1140248 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | F-17 | Generator | ATS / Engine | Wrong connection | Critical | two cables in one slote | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 10% | 34.5%
356330 | 1140250 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | F-7 | Generator | ATS / Engine | Unit unfixed/not installed well | Critical | disconnected battery | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 10% | 34.5%
356328 | 1140005 | DREAM-PARK | C3_0183UP_PH3 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-12 | Power System | Power Meter & Main Breaker | Unit earth | Critical | not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 2% | 2% | 53%
356328 | 1140000 | DREAM-PARK | C3_0183UP_PH3 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-12 | Power System | GEDP | Unit earth | Critical | earth missing | Stealth | Contractor | M/D | Converged Run | - | - | 2% | 2% | 53%
356328 | 1139990 | DREAM-PARK | C3_0183UP_PH3 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-52 | Power System | Rectifiers | Temperature sensor not inserted between batteries (if applicable) | Critical | insert between batteries | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 8% | 53%
356328 | 1139988 | DREAM-PARK | C3_0183UP_PH3 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | faulty fans | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 5% | 53%
356328 | 1140009 | DREAM-PARK | C3_0183UP_PH3 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | C-60 | Fire System | Fire Alarm and Fighting System | Fire extinguisher missing/empty/expired/(safety seal) | Critical | missing extinguisher | Stealth | Contractor | M/D | Converged Run | - | - | 10% | 10% | 53%
356328 | 1140007 | DREAM-PARK | C3_0183UP_PH3 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | D-15 | Equipment and DDF | Equipment and DDF | Components faulty | Critical | faulty sensors | Aging | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 53%
356328 | 1140012 | DREAM-PARK | C3_0183UP_PH3 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | D-7 | Equipment and DDF | Equipment and DDF | Unit unfixed/not installed well | Critical | faulty panel , need to change by metal one | Converged Run | Converged Run | M/D | Converged Run | - | - | 1.167% | 7% | 53%
356328 | 1140020 | DREAM-PARK | C3_0183UP_PH3 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-33 | Civil | Shelter Body / Main Enclosure | Trays covers missing/unfixed (if laid on the ground only) | Critical | fix cover | Aging | Contractor | M/D | Converged Run | - | - | 2.25% | 9% | 53%
356328 | 1139998 | DREAM-PARK | C3_0183UP_PH3 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-9 | Civil | Shelter Body / Main Enclosure | Door lock/handle that affects door from open easily or close firmly | Critical | faulty lock and found open | Contractor | Contractor | M/D | Converged Run | - | - | 2.25% | 9% | 53%
356326 | 1140770 | DK-TILBANA | C1_0602DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | A-6-15 | Power System | Rectifiers | Components faulty | Critical | Faulty and missing rectifier surge arrestor. | Aging | Converged Run | M/D | Converged Run | - | - | 4% | 8% | 67%
356326 | 1140757 | DK-TILBANA | C1_0602DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | - | Aging | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 67%
356326 | 1140768 | DK-TILBANA | C1_0602DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | B-41 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Some parts are (missing / stolen) | Critical | OD power cables need cover. | Aging | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 67%
356324 | 1140720 | DK-BELGAY-VLG | C1_3774DE_PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | A-7-41 | Power System | Batteries | Some parts are (missing / stolen) | Critical | No backup batteries. | Stealth | Converged Run | M/D | Converged Run | - | - | 5% | 5% | 77%
356324 | 1140721 | DK-BELGAY-VLG | C1_3774DE_PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | - | Aging | Contractor | M/D | Converged Run | - | - | 4% | 12% | 77%
356323 | 1140696 | DK-MIT-KHAYRON | C3_3257DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | A-1-12 | Power System | Power Meter & Main Breaker | Unit earth | Critical | Power meter panel need earthing. | Aging | Contractor | M/D | Converged Run | - | - | 5% | 5% | 45%
356323 | 1140704 | DK-MIT-KHAYRON | C3_3257DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | A-2-17 | Power System | Shared Panel | Wrong connection | Critical | Vodafone has bad connections. | VF | Converged Run | M/D | Converged Run | - | - | 2% | 4% | 45%
356323 | 1140705 | DK-MIT-KHAYRON | C3_3257DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | A-2-23 | Power System | Shared Panel | Cables termination/lugs (AC side), lugs (DC side) | Critical | Vodafone Power cables need proper terminals. | VF | Converged Run | M/D | Converged Run | - | - | 2% | 4% | 45%
356323 | 1140690 | DK-MIT-KHAYRON | C3_3257DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | A-6-15 | Power System | Rectifiers | Components faulty | Critical | Faulty rectifier surge arrestor. | Aging | Converged Run | M/D | Converged Run | - | - | 2.667% | 8% | 45%
356323 | 1140698 | DK-MIT-KHAYRON | C3_3257DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | B-41 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Some parts are (missing / stolen) | Critical | OD power cables has missing cover. | Aging | Contractor | M/D | Converged Run | - | - | 10% | 12% | 45%
356323 | 1140687 | DK-MIT-KHAYRON | C3_3257DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | D-17 | Equipment and DDF | Equipment and DDF | Wrong connection | Critical | ZTE system has generator alarm (due to removed generator) and its OD camera isn't working and need to be connected. | Aging | Contractor | M/D | Converged Run | - | - | 2.333% | 7% | 45%
356323 | 1140694 | DK-MIT-KHAYRON | C3_3257DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | D-7 | Equipment and DDF | Equipment and DDF | Unit unfixed/not installed well | Critical | Cables need arrangement, termination, fixation and unused cables need to be removed. | Aging | Contractor | M/D | Converged Run | - | - | 2.333% | 7% | 45%
356323 | 1140699 | DK-MIT-KHAYRON | C3_3257DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | E-2-77 | Civil | Antenna Support | Climbing safety wire | Critical | Safety wire need proper installation and fixation. | Aging | Converged Run | M/D | Converged Run | - | - | 3.5% | 7% | 45%
356323 | 1140678 | DK-MIT-KHAYRON | C3_3257DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | E-3-66 | Civil | Fence / Roof | Flammable junk/trash inside/outside (e.g. plastics, papers, cartoon boxes, etc…) | Critical | Generator removed and its area needs cleaning and adjust. | Aging | Contractor | M/D | Converged Run | - | - | 7% | 7% | 45%
356321 | 1140886 | 23_S_ ZAHREYA-TOWN_ 0583AL_S000 | C3_0583AL_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Abdullatief | Eslam Ahmed | Sectra | 2019-09-17 | AGLI | Orascom | ALEX | Alex East | V10R00 | A-1-3 | Power System | Power Meter & Main Breaker | Panel/cables secured location/route (e.g. Surge panel outside the shelter or far away from other panels) | Critical | Panel need proper sealing with iron protective iron cover with glands | Converged Run | Converged Run | M/D | Converged Run | - | - | 2.5% | 5% | 75.5%
356321 | 1140875 | 23_S_ ZAHREYA-TOWN_ 0583AL_S000 | C3_0583AL_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Abdullatief | Eslam Ahmed | Sectra | 2019-09-17 | AGLI | Orascom | ALEX | Alex East | V10R00 | A-7-15 | Power System | Batteries | Components faulty | Critical | Battary can not carry site | Aging | Converged Run | M/D | Converged Run | - | - | 5% | 5% | 75.5%
356321 | 1140876 | 23_S_ ZAHREYA-TOWN_ 0583AL_S000 | C3_0583AL_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Abdullatief | Eslam Ahmed | Sectra | 2019-09-17 | AGLI | Orascom | ALEX | Alex East | V10R00 | E-1-19 | Civil | Shelter Body / Main Enclosure | Alarms reporting to the OMC | Critical | Door alarm not appear at OMC | Contractor | Contractor | M/D | Converged Run | - | - | 1.8% | 9% | 75.5%
356321 | 1140866 | 23_S_ ZAHREYA-TOWN_ 0583AL_S000 | C3_0583AL_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Abdullatief | Eslam Ahmed | Sectra | 2019-09-17 | AGLI | Orascom | ALEX | Alex East | V10R00 | E-1-8 | Civil | Shelter Body / Main Enclosure | Door/frame fixation that affects door from open easily or close firmly | Critical | Door uninstalled | Aging | Contractor | M/D | Converged Run | - | - | 1.8% | 9% | 75.5%
356321 | 1140864 | 23_S_ ZAHREYA-TOWN_ 0583AL_S000 | C3_0583AL_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Abdullatief | Eslam Ahmed | Sectra | 2019-09-17 | AGLI | Orascom | ALEX | Alex East | V10R00 | E-1-9 | Civil | Shelter Body / Main Enclosure | Door lock/handle that affects door from open easily or close firmly | Critical | Faulty lock | Aging | Contractor | M/D | Converged Run | - | - | 1.8% | 9% | 75.5%
356318 | 1139929 | QL-DEER-2 | C1_3275DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | A-1-23 | Power System | Power Meter & Main Breaker | Cables termination/lugs (AC side), lugs (DC side) | Critical | Terminals requried | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 5% | 43.17%
356318 | 1139934 | QL-DEER-2 | C1_3275DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | A-2-23 | Power System | Shared Panel | Cables termination/lugs (AC side), lugs (DC side) | Critical | Terminals requried | Contractor | Contractor | M/D | Converged Run | - | - | 4% | 4% | 43.17%
356318 | 1139923 | QL-DEER-2 | C1_3275DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | A-6-15 | Power System | Rectifiers | Components faulty | Critical | Faulty SA | Aging | Converged Run | M/D | Converged Run | - | - | 2.667% | 8% | 43.17%
356318 | 1139904 | QL-DEER-2 | C1_3275DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | A-6-19 | Power System | Rectifiers | Alarms reporting to the OMC | Critical | Alarm cable disconnected (Alarms not appear at OMC) | Contractor | Contractor | M/D | Converged Run | - | - | 2.667% | 8% | 43.17%
356318 | 1139896 | QL-DEER-2 | C1_3275DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | A-7-15 | Power System | Batteries | Components faulty | Critical | Faulty battaries | Aging | Converged Run | M/D | Converged Run | - | - | 3.333% | 3.333% | 43.17%
356318 | 1139900 | QL-DEER-2 | C1_3275DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | B-41 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Some parts are (missing / stolen) | Critical | There is no A/C IDU and ODU | Stealth | Contractor | M/D | Converged Run | - | - | 5% | 10.5% | 43.17%
356318 | 1139903 | QL-DEER-2 | C1_3275DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | C-15 | Fire System | Fire Alarm and Fighting System | Components faulty | Critical | Fire panel not working | Aging | Contractor | M/D | Converged Run | - | - | 3.333% | 10% | 43.17%
356318 | 1139908 | QL-DEER-2 | C1_3275DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | C-19 | Fire System | Fire Alarm and Fighting System | Alarms reporting to the OMC | Critical | Alarm cable disconnected (Alarms not appear at OMC) | Contractor | Contractor | M/D | Converged Run | - | - | 3.333% | 10% | 43.17%
356318 | 1139914 | QL-DEER-2 | C1_3275DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | C-60 | Fire System | Fire Alarm and Fighting System | Fire extinguisher missing/empty/expired/(safety seal) | Critical | Expired date | Contractor | Contractor | M/D | Converged Run | - | - | 3.333% | 10% | 43.17%
356318 | 1139933 | QL-DEER-2 | C1_3275DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | D-7 | Equipment and DDF | Equipment and DDF | Unit unfixed/not installed well | Critical | Tray need proper fixation | Contractor | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 43.17%
356318 | 1139910 | QL-DEER-2 | C1_3275DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | E-1-19 | Civil | Shelter Body / Main Enclosure | Alarms reporting to the OMC | Critical | Alarm cable disconnected (Alarms not appear at OMC) | Contractor | Contractor | M/D | Converged Run | - | - | 2.25% | 9% | 43.17%
356318 | 1139924 | QL-DEER-2 | C1_3275DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | E-1-9 | Civil | Shelter Body / Main Enclosure | Door lock/handle that affects door from open easily or close firmly | Critical | Upper lock requried | Aging | Converged Run | M/D | Converged Run | - | - | 2.25% | 9% | 43.17%
356317 | 1139823 | QL-DEER | C2_0423DE_PH4 | Golden | Whitelist | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | A-3-23 | Power System | GEDP | Cables termination/lugs (AC side), lugs (DC side) | Critical | Burned terminals | Contractor | Contractor | M/D | Converged Run | - | - | 10% | 10% | 44%
356317 | 1139826 | QL-DEER | C2_0423DE_PH4 | Golden | Whitelist | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | A-6-15 | Power System | Rectifiers | Components faulty | Critical | Faulty SA | Aging | Converged Run | M/D | Converged Run | - | - | 4% | 8% | 44%
356317 | 1139828 | QL-DEER | C2_0423DE_PH4 | Golden | Whitelist | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | A/C has no proper cooling (Working only as a fan) | Contractor | Contractor | M/D | Converged Run | - | - | 3% | 12% | 44%
356317 | 1139821 | QL-DEER | C2_0423DE_PH4 | Golden | Whitelist | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | B-17 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Wrong connection | Critical | Missing the control board and replacing it by temperature sensor | Contractor | Contractor | M/D | Converged Run | - | - | 3% | 12% | 44%
356317 | 1139822 | QL-DEER | C2_0423DE_PH4 | Golden | Whitelist | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | C-60 | Fire System | Fire Alarm and Fighting System | Fire extinguisher missing/empty/expired/(safety seal) | Critical | Expired date | Contractor | Contractor | M/D | Converged Run | - | - | 10% | 10% | 44%
356315 | 1139781 | QL-MUSHTAHER | C1_0703DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | A-7-41 | Power System | Batteries | Some parts are (missing / stolen) | Critical | There is no battery for site | Stealth | Converged Run | M/D | Converged Run | - | - | 5% | 5% | 42%
356315 | 1139791 | QL-MUSHTAHER | C1_0703DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | B-10 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…) | Critical | A/C has condensed water leaks | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 42%
356315 | 1139792 | QL-MUSHTAHER | C1_0703DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | A/C has no proper cooling (Working only as a fan) | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 42%
356315 | 1139808 | QL-MUSHTAHER | C1_0703DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | B-23 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Cables termination/lugs (AC side), lugs (DC side) | Critical | Burned terminals | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 42%
356315 | 1139786 | QL-MUSHTAHER | C1_0703DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | C-15 | Fire System | Fire Alarm and Fighting System | Components faulty | Critical | Faulty battery | Aging | Contractor | M/D | Converged Run | - | - | 5% | 10% | 42%
356315 | 1139783 | QL-MUSHTAHER | C1_0703DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | C-60 | Fire System | Fire Alarm and Fighting System | Fire extinguisher missing/empty/expired/(safety seal) | Critical | Expired date | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 10% | 42%
356315 | 1139806 | QL-MUSHTAHER | C1_0703DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | E-2-77 | Civil | Antenna Support | Climbing safety wire | Critical | Safety wire uninstalled | Aging | Converged Run | M/D | Converged Run | - | - | 1.75% | 7% | 42%
356315 | 1139789 | QL-MUSHTAHER | C1_0703DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | E-3-19 | Civil | Fence / Roof | Alarms reporting to the OMC | Critical | Site has history fence gate alarm | Contractor | Contractor | M/D | Converged Run | - | - | 3.5% | 7% | 42%
356313 | 1139763 | 6th October 5 | C1_8032UP_PH2 | Bronze | Whitelist | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-10 | Power System | Power Meter & Main Breaker | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…) | Critical | seal and use gland | Converged Run | Contractor | M/D | Converged Run | - | - | 1.667% | 5% | 46%
356313 | 1139753 | 6th October 5 | C1_8032UP_PH2 | Bronze | Whitelist | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-20 | Power System | Power Meter & Main Breaker | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Critical | protect power cables | Converged Run | Contractor | M/D | Converged Run | - | - | 1.667% | 5% | 46%
356313 | 1139731 | 6th October 5 | C1_8032UP_PH2 | Bronze | Whitelist | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-12 | Power System | GEDP | Unit earth | Critical | no earth | Stealth | Contractor | M/D | Converged Run | - | - | 6% | 12% | 46%
356313 | 1139732 | 6th October 5 | C1_8032UP_PH2 | Bronze | Whitelist | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-7 | Power System | GEDP | Unit unfixed/not installed well | Critical | timer forced to one A/C | Contractor | Contractor | M/D | Converged Run | - | - | 6% | 12% | 46%
356313 | 1139765 | 6th October 5 | C1_8032UP_PH2 | Bronze | Whitelist | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | B-12 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Unit earth | Critical | not connected to earth system | Stealth | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 46%
356313 | 1139733 | 6th October 5 | C1_8032UP_PH2 | Bronze | Whitelist | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | Faulty A/C | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 46%
356313 | 1139739 | 6th October 5 | C1_8032UP_PH2 | Bronze | Whitelist | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | C-15 | Fire System | Fire Alarm and Fighting System | Components faulty | Critical | faulty | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 5% | 46%
356313 | 1139751 | 6th October 5 | C1_8032UP_PH2 | Bronze | Whitelist | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-10 | Civil | Shelter Body / Main Enclosure | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…) | Critical | seal | Converged Run | Contractor | M/D | Converged Run | - | - | 3% | 9% | 46%
356313 | 1139768 | 6th October 5 | C1_8032UP_PH2 | Bronze | Whitelist | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-66 | Civil | Fence / Roof | Flammable junk/trash inside/outside (e.g. plastics, papers, cartoon boxes, etc…) | Critical | clean | Aging | Contractor | M/D | Converged Run | - | - | 3.5% | 7% | 46%
356312 | 1139677 | 6OCT-MENA-CTY | C1_3252UP_PH13 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-16 | Power System | GEDP | Components below/over rate (excluding main power feeder if not hot) | Critical | high temp rate | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 45.17%
356312 | 1139681 | 6OCT-MENA-CTY | C1_3252UP_PH13 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-17 | Power System | GEDP | Wrong connection | Critical | wrong connection | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 45.17%
356312 | 1139682 | 6OCT-MENA-CTY | C1_3252UP_PH13 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-22 | Power System | GEDP | Cables/Feeders/Jumpers/Coaxial/FO/PCM connection tightness | Critical | loose connection | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 45.17%
356312 | 1139691 | 6OCT-MENA-CTY | C1_3252UP_PH13 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-23 | Power System | GEDP | Cables termination/lugs (AC side), lugs (DC side) | Critical | missing termination | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 45.17%
356312 | 1139683 | 6OCT-MENA-CTY | C1_3252UP_PH13 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-7 | Power System | GEDP | Unit unfixed/not installed well | Critical | timer forced to one A/C | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 45.17%
356312 | 1139684 | 6OCT-MENA-CTY | C1_3252UP_PH13 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | faulty A/C and its CB turned off | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 10.83% | 45.17%
356312 | 1139692 | 6OCT-MENA-CTY | C1_3252UP_PH13 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | B-17 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Wrong connection | Critical | no card found and using sensor | Contractor | Contractor | M/D | Converged Run | - | - | 3.333% | 10.83% | 45.17%
356312 | 1139696 | 6OCT-MENA-CTY | C1_3252UP_PH13 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | B-7 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Unit unfixed/not installed well | Critical | fix | Contractor | Contractor | M/D | Converged Run | - | - | 2.5% | 10.83% | 45.17%
356312 | 1139687 | 6OCT-MENA-CTY | C1_3252UP_PH13 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | C-15 | Fire System | Fire Alarm and Fighting System | Components faulty | Critical | faulty and its CB is turned off | Contractor | Contractor | M/D | Converged Run | - | - | 3.333% | 10% | 45.17%
356312 | 1139694 | 6OCT-MENA-CTY | C1_3252UP_PH13 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | C-60 | Fire System | Fire Alarm and Fighting System | Fire extinguisher missing/empty/expired/(safety seal) | Critical | expired | Contractor | Contractor | M/D | Converged Run | - | - | 3.333% | 10% | 45.17%
356312 | 1139689 | 6OCT-MENA-CTY | C1_3252UP_PH13 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | C-7 | Fire System | Fire Alarm and Fighting System | Unit unfixed/not installed well | Critical | disconnected batteries | Sabotage | Contractor | M/D | Converged Run | - | - | 3.333% | 10% | 45.17%
356312 | 1139674 | 6OCT-MENA-CTY | C1_3252UP_PH13 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-17 | Civil | Shelter Body / Main Enclosure | Wrong connection | Critical | wrong connection feeds anther room outside the fence and shop beside the site | Guard | Converged Run | M/D | Converged Run | - | - | 2.25% | 9% | 45.17%
356312 | 1139707 | 6OCT-MENA-CTY | C1_3252UP_PH13 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-7 | Civil | Shelter Body / Main Enclosure | Unit unfixed/not installed well | Critical | guard build an extra building and use flammable materials | Guard | Converged Run | M/D | Converged Run | - | - | 2.25% | 9% | 45.17%
356312 | 1139711 | 6OCT-MENA-CTY | C1_3252UP_PH13 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-66 | Civil | Fence / Roof | Flammable junk/trash inside/outside (e.g. plastics, papers, cartoon boxes, etc…) | Critical | remove | Guard | Converged Run | M/D | Converged Run | - | - | 7% | 7% | 45.17%
356311 | 1139587 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-20 | Power System | Power Meter & Main Breaker | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Critical | fix PVC | Aging | Contractor | M/D | Converged Run | - | - | 5% | 5% | 22%
356311 | 1139558 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | A-4-15 | Power System | Surge Arrestor | Components faulty | Critical | faulty surge | Electricity Company | Contractor | M/D | Converged Run | - | - | 3.333% | 10% | 22%
356311 | 1139556 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | A-4-3 | Power System | Surge Arrestor | Panel/cables secured location/route (e.g. Surge panel outside the shelter or far away from other panels) | Critical | relocate | Converged Run | Converged Run | M/D | Converged Run | - | - | 3.333% | 10% | 22%
356311 | 1139557 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | A-4-7 | Power System | Surge Arrestor | Unit unfixed/not installed well | Critical | replace box by metal IP55 | Converged Run | Converged Run | M/D | Converged Run | - | - | 3.333% | 10% | 22%
356311 | 1139575 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-11 | Power System | Rectifiers | Unit sharp edges | Critical | sharp edge and fix cover well | Contractor | Contractor | M/D | Converged Run | - | - | 4% | 8% | 22%
356311 | 1139589 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | B-12 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Unit earth | Critical | not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 2% | 12% | 22%
356311 | 1139559 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | Faulty 4Enrgy system | Aging | Converged Run | M/D | Converged Run | - | - | 2% | 12% | 22%
356311 | 1139573 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | B-7 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Unit unfixed/not installed well | Critical | fix | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 12% | 22%
356311 | 1139580 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | C-15 | Fire System | Fire Alarm and Fighting System | Components faulty | Critical | faulty batteries | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 10% | 22%
356311 | 1139562 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | C-59 | Fire System | Fire Alarm and Fighting System | Fire alarm does not stop A/Cs and/or generator | Critical | check and clear alarm | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 10% | 22%
356311 | 1139578 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | D-7 | Equipment and DDF | Equipment and DDF | Unit unfixed/not installed well | Critical | ZTE camera need to fix | Aging | Contractor | M/D | Converged Run | - | - | 2.333% | 7% | 22%
356311 | 1139607 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-19 | Civil | Shelter Body / Main Enclosure | Alarms reporting to the OMC | Critical | adjust sites alarms | Contractor | Contractor | M/D | Converged Run | - | - | 1.8% | 9% | 22%
356311 | 1139581 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-8 | Civil | Shelter Body / Main Enclosure | Door/frame fixation that affects door from open easily or close firmly | Critical | door need fixation | Aging | Contractor | M/D | Converged Run | - | - | 1.8% | 9% | 22%
356311 | 1139598 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-80 | Civil | Antenna Support | Palm tree fronds (broke/fall) | Critical | missing some tree fronds and others are faulty | Aging | Converged Run | M/D | Converged Run | - | - | 2.333% | 7% | 22%
356311 | 1139583 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-19 | Civil | Fence / Roof | Alarms reporting to the OMC | Critical | adjust the fence gate sensor | Contractor | Contractor | M/D | Converged Run | - | - | 3.5% | 7% | 22%
356311 | 1139591 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-66 | Civil | Fence / Roof | Flammable junk/trash inside/outside (e.g. plastics, papers, cartoon boxes, etc…) | Critical | remove | Aging | Contractor | M/D | Converged Run | - | - | 3.5% | 7% | 22%
356309 | 1139324 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-1-12 | Power System | Power Meter & Main Breaker | Unit earth | Critical | Earth tape of the MFP is disconnected | Stealth | Contractor | M/D | Converged Run | - | - | 2.5% | 5% | 29.17%
356309 | 1139325 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-1-17 | Power System | Power Meter & Main Breaker | Wrong connection | Critical | Wrong connections of power cables inside the MFP (related to Etisalat) | ET | Contractor | M/D | Converged Run | - | - | 2.5% | 5% | 29.17%
356309 | 1139333 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-3-23 | Power System | GEDP | Cables termination/lugs (AC side), lugs (DC side) | Critical | Defected terminal of the main neutral cable connected to the GEDP | Contractor | Contractor | M/D | Converged Run | - | - | 10% | 11% | 29.17%
356309 | 1139339 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-6-15 | Power System | Rectifiers | Components faulty | Critical | Defected surge arrestor of the rectifier | Aging | Contractor | M/D | Converged Run | - | - | 1.333% | 8% | 29.17%
356309 | 1139345 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-6-52 | Power System | Rectifiers | Temperature sensor not inserted between batteries (if applicable) | Critical | The temprature sensor is inserted in IDU2 | Contractor | Contractor | M/D | Converged Run | - | - | 1.333% | 8% | 29.17%
356309 | 1139332 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | A/C1 is switched off | Contractor | Contractor | M/D | Converged Run | - | - | 3.333% | 6.833% | 29.17%
356309 | 1139372 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | E-1-17 | Civil | Shelter Body / Main Enclosure | Wrong connection | Critical | Welded cables of the fence lights | Contractor | Contractor | M/D | Converged Run | - | - | 4.5% | 9% | 29.17%
356309 | 1139336 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | E-1-19 | Civil | Shelter Body / Main Enclosure | Alarms reporting to the OMC | Critical | Shelter's door alarm doesn't appear on the OMC | Contractor | Contractor | M/D | Converged Run | - | - | 4.5% | 9% | 29.17%
356309 | 1139373 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | F-10 | Generator | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…) | Critical | Oil leakage of Etisalat genset | ET | Contractor | M/D | Converged Run | - | - | 2% | 10% | 29.17%
356309 | 1139382 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | F-15 | Generator | ATS / Engine | Components faulty | Critical | Faulty rubber bases of the radiator | Aging | Contractor | M/D | Converged Run | - | - | 2% | 10% | 29.17%
356309 | 1139379 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | F-41 | Generator | ATS / Engine | Some parts are (missing / stolen) | Critical | The genset battery is missing and DC cables that should have been connected to the battery are left floating (can cause fire) | Stealth | Contractor | M/D | Converged Run | - | - | 2% | 10% | 29.17%
356285 | 1138192 | Khattara 1 & 2 BSC | C1_8050UP_PH9_1 | Golden | Whitelist | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | A-1-23 | Power System | Power Meter & Main Breaker | Cables termination/lugs (AC side), lugs (DC side) | Critical | Missing terminals in power cables at 100 A C.B | Contractor | Contractor | M/D | Converged Run | - | - | 2.5% | 5% | 64%
356285 | 1138188 | Khattara 1 & 2 BSC | C1_8050UP_PH9_1 | Golden | Whitelist | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | A-3-15 | Power System | GEDP | Components faulty | Critical | Surge arrestor fuses are blown | Aging | Contractor | M/D | Converged Run | - | - | 10% | 10% | 64%
356285 | 1138185 | Khattara 1 & 2 BSC | C1_8050UP_PH9_1 | Golden | Whitelist | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | A-7-41 | Power System | Batteries | Some parts are (missing / stolen) | Critical | Some of Batteries were stolen | Stealth | Converged Run | M/D | Converged Run | - | - | 5% | 5% | 64%
356285 | 1138189 | Khattara 1 & 2 BSC | C1_8050UP_PH9_1 | Golden | Whitelist | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | B-41 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Some parts are (missing / stolen) | Critical | One of A/C's was stolen | Stealth | Converged Run | M/D | Converged Run | - | - | 5% | 6% | 64%
356284 | 1138127 | 01_W_QN-KHATARA_0273UP | C1_0273UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | A-3-17 | Power System | GEDP | Wrong connection | Critical | Two cables inserted in one slot can cause bad connections | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 5% | 58%
356284 | 1138140 | 01_W_QN-KHATARA_0273UP | C1_0273UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | A-6-15 | Power System | Rectifiers | Components faulty | Critical | Surge arrestors inside the rectifier are blown | Aging | Converged Run | M/D | Converged Run | - | - | 2.667% | 8% | 58%
356284 | 1138142 | 01_W_QN-KHATARA_0273UP | C1_0273UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | A-6-51 | Power System | Rectifiers | Batteries charging current unlimited per the manufacturer specs | Critical | I battery max is not correct and to be changed to 35A for 1Strings | Contractor | Contractor | M/D | Converged Run | - | - | 2.667% | 8% | 58%
356284 | 1138122 | 01_W_QN-KHATARA_0273UP | C1_0273UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | A/c 1 Not functioning | Contractor | Contractor | M/D | Converged Run | - | - | 3% | 12% | 58%
356284 | 1138152 | 01_W_QN-KHATARA_0273UP | C1_0273UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | B-17 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Wrong connection | Critical | welded cables at A/C's odu | Contractor | Contractor | M/D | Converged Run | - | - | 3% | 12% | 58%
356284 | 1138155 | 01_W_QN-KHATARA_0273UP | C1_0273UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | B-41 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Some parts are (missing / stolen) | Critical | A/c odu rosette missing cover | Aging | Contractor | M/D | Converged Run | - | - | 3% | 12% | 58%
356283 | 1138114 | 01_H_QN-MAHROUSA_0274UP | C1_0274UP_PH8 | Golden | BSC | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | A/c odu fan grid is broken | Aging | Contractor | M/D | Converged Run | - | - | 10% | 10% | 70%
356283 | 1138090 | 01_H_QN-MAHROUSA_0274UP | C1_0274UP_PH8 | Golden | BSC | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | D-25 | Equipment and DDF | Equipment and DDF | Messy DDF (more than or equal to 10 Krone Blocks or equivalent) | Critical | DDF cables need attachment and arrangement | Converged Run | Converged Run | M/D | Converged Run | - | - | 2.333% | 7% | 70%
356282 | 1138347 | BH-SHOBRA-RIS | C1_4360DE_PH13 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | A-1-17 | Power System | Power Meter & Main Breaker | Wrong connection | Critical | Wrong connection | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 5% | 67.67%
356282 | 1138354 | BH-SHOBRA-RIS | C1_4360DE_PH13 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | E-3-19 | Civil | Fence / Roof | Alarms reporting to the OMC | Critical | Site has history fence gate alarm | Contractor | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 67.67%
356282 | 1138358 | BH-SHOBRA-RIS | C1_4360DE_PH13 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | E-3-9 | Civil | Fence / Roof | Door lock/handle that affects door from open easily or close firmly | Critical | Faulty guard lock | Aging | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 67.67%
356280 | 1138281 | BH-KFR-QASHASH | C4_0545DE_PH8 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | A-3-16 | Power System | GEDP | Components below/over rate (excluding main power feeder if not hot) | Critical | Rectifier CB has low rate | Contractor | Contractor | M/D | Converged Run | - | - | 10% | 10% | 46%
356280 | 1138280 | BH-KFR-QASHASH | C4_0545DE_PH8 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | A/C not working | Contractor | Contractor | M/D | Converged Run | - | - | 10% | 12% | 46%
356280 | 1138284 | BH-KFR-QASHASH | C4_0545DE_PH8 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | E-3-19 | Civil | Fence / Roof | Alarms reporting to the OMC | Critical | Sensor need proper fixation | Contractor | Contractor | M/D | Converged Run | - | - | 3.5% | 7% | 46%
356278 | 1138080 | BH-DAHRIA | C2_3508DE_PH13 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Tanta | V10R00 | A-6-15 | Power System | Rectifiers | Components faulty | Critical | Faulty SA | Aging | Converged Run | M/D | Converged Run | - | - | 4% | 8% | 73%
356278 | 1138066 | BH-DAHRIA | C2_3508DE_PH13 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Tanta | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | A/C CB off | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 5% | 73%
356274 | 1137922 | MF-BANI-SALAMA | C1-3232DE-PH12 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-09 | AGLI | AGLI-Contractor | Delta South | Sadat | V10R00 | E-2-77 | Civil | Antenna Support | Climbing safety wire | Critical | Safety wire need tension | Aging | Converged Run | M/D | Converged Run | - | - | 1.75% | 7% | 71%
356274 | 1137936 | MF-BANI-SALAMA | C1-3232DE-PH12 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-09 | AGLI | AGLI-Contractor | Delta South | Sadat | V10R00 | E-3-19 | Civil | Fence / Roof | Alarms reporting to the OMC | Critical | Site has history fence gate alarm | Contractor | Contractor | M/D | Converged Run | - | - | 2.333% | 7% | 71%
356266 | 1137517 | AT-QUSIYA5 | C1_3920UP_PH15 | Bronze | New Sites (After 2015) | Atef Zidan | Mohamed Abd Assalam Abass | Sectra | 2019-09-08 | NGLI | Huawei | North Upper | Asyout | V10R00 | A-7-41 | Power System | Batteries | Some parts are (missing / stolen) | Critical | Batteries were stolen | Stealth | New Sites | M/D | New Sites | - | - | 5% | 5% | 81%
356266 | 1137518 | AT-QUSIYA5 | C1_3920UP_PH15 | Bronze | New Sites (After 2015) | Atef Zidan | Mohamed Abd Assalam Abass | Sectra | 2019-09-08 | NGLI | Huawei | North Upper | Asyout | V10R00 | E-2-33 | Civil | Antenna Support | Trays covers missing/unfixed (if laid on the ground only) | Critical | Missing Trays covers | New Sites | New Sites | M/D | New Sites | - | - | 7% | 7% | 81%
356264 | 1138321 | SK-QUDAH | C1-3402DE-PH13 | Golden | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | A-1-20 | Power System | Power Meter & Main Breaker | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Critical | Main power cable need proper installation and protection. | Contractor | Contractor | M/D | Converged Run | - | - | 2.5% | 5% | 44%
356264 | 1138326 | SK-QUDAH | C1-3402DE-PH13 | Golden | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | A-1-7 | Power System | Power Meter & Main Breaker | Unit unfixed/not installed well | Critical | - | Aging | Contractor | M/D | Converged Run | - | - | 2.5% | 5% | 44%
356264 | 1138314 | SK-QUDAH | C1-3402DE-PH13 | Golden | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | A/C2 is faulty and its CB tripped off. | Aging | Contractor | M/D | Converged Run | - | - | 10% | 10% | 44%
356264 | 1138317 | SK-QUDAH | C1-3402DE-PH13 | Golden | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | C-60 | Fire System | Fire Alarm and Fighting System | Fire extinguisher missing/empty/expired/(safety seal) | Critical | No fire ext. | Contractor | Contractor | M/D | Converged Run | - | - | 10% | 10% | 44%
356264 | 1138319 | SK-QUDAH | C1-3402DE-PH13 | Golden | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | E-1-10 | Civil | Shelter Body / Main Enclosure | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…) | Critical | Roxtec is required. | Aging | Converged Run | M/D | Converged Run | - | - | 4.5% | 9% | 44%
356264 | 1138322 | SK-QUDAH | C1-3402DE-PH13 | Golden | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | E-3-19 | Civil | Fence / Roof | Alarms reporting to the OMC | Critical | Fence gate sensor cable is cut and need adjust. | Aging | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 44%
356264 | 1138329 | SK-QUDAH | C1-3402DE-PH13 | Golden | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | E-3-66 | Civil | Fence / Roof | Flammable junk/trash inside/outside (e.g. plastics, papers, cartoon boxes, etc…) | Critical | - | Aging | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 44%
356263 | 1138258 | SK-SHARQAYA | C1-3793DE-PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | A-2-17 | Power System | Shared Panel | Wrong connection | Critical | Sharing panel CB has bad connections and need adjust. | ET | Converged Run | M/D | Converged Run | - | - | 2% | 4% | 37.67%
356263 | 1138257 | SK-SHARQAYA | C1-3793DE-PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | A-2-23 | Power System | Shared Panel | Cables termination/lugs (AC side), lugs (DC side) | Critical | - | ET | Converged Run | M/D | Converged Run | - | - | 2% | 4% | 37.67%
356263 | 1138247 | SK-SHARQAYA | C1-3793DE-PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | Cabinet A/C faulty and its control board needs repair. | Aging | Contractor | M/D | Converged Run | - | - | 5% | 5% | 37.67%
356263 | 1138263 | SK-SHARQAYA | C1-3793DE-PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | C-60 | Fire System | Fire Alarm and Fighting System | Fire extinguisher missing/empty/expired/(safety seal) | Critical | No fire ext. | Contractor | Contractor | M/D | Converged Run | - | - | 10% | 10% | 37.67%
356263 | 1138260 | SK-SHARQAYA | C1-3793DE-PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | D-7 | Equipment and DDF | Equipment and DDF | Unit unfixed/not installed well | Critical | - | Aging | Contractor | M/D | Converged Run | - | - | 5% | 5.667% | 37.67%
356263 | 1138241 | SK-SHARQAYA | C1-3793DE-PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | E-1-7 | Civil | Shelter Body / Main Enclosure | Unit unfixed/not installed well | Critical | Cage needs repair. | Stealth | Converged Run | M/D | Converged Run | - | - | 3% | 9% | 37.67%
356263 | 1138244 | SK-SHARQAYA | C1-3793DE-PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | E-1-8 | Civil | Shelter Body / Main Enclosure | Door/frame fixation that affects door from open easily or close firmly | Critical | Cabinet door needs repair. | Aging | Contractor | M/D | Converged Run | - | - | 3% | 9% | 37.67%
356263 | 1138234 | SK-SHARQAYA | C1-3793DE-PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | E-3-66 | Civil | Fence / Roof | Flammable junk/trash inside/outside (e.g. plastics, papers, cartoon boxes, etc…) | Critical | Area needs cleaning and junk need to be removed. | Aging | Contractor | M/D | Converged Run | - | - | 3.5% | 7% | 37.67%
356263 | 1138254 | SK-SHARQAYA | C1-3793DE-PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | F-15 | Generator | ATS / Engine | Components faulty | Critical | Faulty module. | Aging | Contractor | M/D | Converged Run | - | - | 2.5% | 10% | 37.67%
356263 | 1138255 | SK-SHARQAYA | C1-3793DE-PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | F-23 | Generator | ATS / Engine | Cables termination/lugs (AC side), lugs (DC side) | Critical | ATS cables need proper terminals. | Contractor | Contractor | M/D | Converged Run | - | - | 2.5% | 10% | 37.67%
356263 | 1138252 | SK-SHARQAYA | C1-3793DE-PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | F-41 | Generator | ATS / Engine | Some parts are (missing / stolen) | Critical | No dynamo fan grid. | Contractor | Contractor | M/D | Converged Run | - | - | 2.5% | 10% | 37.67%
356254 | 1137186 | SZ-MENA-OASIS | C1_0032RE_PH1 | Golden | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | A-3-15 | Power System | GEDP | Components faulty | Critical | Power cable burnet | Aging | Contractor | M/D | Converged Run | - | - | 6% | 12% | 31.17%
356254 | 1137188 | SZ-MENA-OASIS | C1_0032RE_PH1 | Golden | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | A-3-23 | Power System | GEDP | Cables termination/lugs (AC side), lugs (DC side) | Critical | Power cable has no terminal | Contractor | Contractor | M/D | Converged Run | - | - | 6% | 12% | 31.17%
356254 | 1137192 | SZ-MENA-OASIS | C1_0032RE_PH1 | Golden | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | A-4-12 | Power System | Surge Arrestor | Unit earth | Critical | Earth cable of surge panel door disconnected | Aging | Contractor | M/D | Converged Run | - | - | 5% | 9.5% | 31.17%
356254 | 1137193 | SZ-MENA-OASIS | C1_0032RE_PH1 | Golden | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | A-4-15 | Power System | Surge Arrestor | Components faulty | Critical | C.B of surge switched off | Aging | Contractor | M/D | Converged Run | - | - | 2.5% | 9.5% | 31.17%
356254 | 1137204 | SZ-MENA-OASIS | C1_0032RE_PH1 | Golden | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | A-6-19 | Power System | Rectifiers | Alarms reporting to the OMC | Critical | Rectifier minor alarm not report the OMC | Aging | Contractor | M/D | Converged Run | - | - | 2.667% | 8% | 31.17%
356254 | 1137203 | SZ-MENA-OASIS | C1_0032RE_PH1 | Golden | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | A-6-52 | Power System | Rectifiers | Temperature sensor not inserted between batteries (if applicable) | Critical | Temperature sensor not inserted between battery | Aging | Contractor | M/D | Converged Run | - | - | 2.667% | 8% | 31.17%
356254 | 1137202 | SZ-MENA-OASIS | C1_0032RE_PH1 | Golden | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | A-6-7 | Power System | Rectifiers | Unit unfixed/not installed well | Critical | Rectifier cover not fixed | Aging | Contractor | M/D | Converged Run | - | - | 2.667% | 8% | 31.17%
356254 | 1137206 | SZ-MENA-OASIS | C1_0032RE_PH1 | Golden | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | A-7-41 | Power System | Batteries | Some parts are (missing / stolen) | Critical | Missing battery pole cover | Aging | Contractor | M/D | Converged Run | - | - | 1.667% | 5% | 31.17%
356254 | 1137225 | SZ-MENA-OASIS | C1_0032RE_PH1 | Golden | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | A/C 1 not work , please replay with current reading | Aging | Contractor | M/D | Converged Run | - | - | 2.5% | 9.167% | 31.17%
356254 | 1137222 | SZ-MENA-OASIS | C1_0032RE_PH1 | Golden | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | B-7 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Unit unfixed/not installed well | Critical | Power cable cover not fixed | Aging | Contractor | M/D | Converged Run | - | - | 5% | 9.167% | 31.17%
356254 | 1137227 | SZ-MENA-OASIS | C1_0032RE_PH1 | Golden | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | C-15 | Fire System | Fire Alarm and Fighting System | Components faulty | Critical | Fire panel not work | Aging | Contractor | M/D | Converged Run | - | - | 2.5% | 2.5% | 31.17%
356251 | 1136989 | SUKHNA-RD6 | C2_0014RE_PH1 | Golden | Whitelist | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | A-3-15 | Power System | GEDP | Components faulty | Critical | Beacon C.B switched off | Aging | Contractor | M/D | Converged Run | - | - | 10% | 10% | 31.5%
356251 | 1136951 | SUKHNA-RD6 | C2_0014RE_PH1 | Golden | Whitelist | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | A-6-19 | Power System | Rectifiers | Alarms reporting to the OMC | Critical | Rectifier minor alarm not report the OMC | Aging | Contractor | M/D | Converged Run | - | - | 4% | 8% | 31.5%
356251 | 1136960 | SUKHNA-RD6 | C2_0014RE_PH1 | Golden | Whitelist | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | B-7 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Unit unfixed/not installed well | Critical | Unfixed power cable cover | Aging | Contractor | M/D | Converged Run | - | - | 5% | 6.25% | 31.5%
356251 | 1136965 | SUKHNA-RD6 | C2_0014RE_PH1 | Golden | Whitelist | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | C-60 | Fire System | Fire Alarm and Fighting System | Fire extinguisher missing/empty/expired/(safety seal) | Critical | Fire extinguisher missing safety seal | Aging | Contractor | M/D | Converged Run | - | - | 10% | 10% | 31.5%
356251 | 1136976 | SUKHNA-RD6 | C2_0014RE_PH1 | Golden | Whitelist | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | E-1-9 | Civil | Shelter Body / Main Enclosure | Door lock/handle that affects door from open easily or close firmly | Critical | Shelter armed door lock not work | Aging | Contractor | M/D | Converged Run | - | - | 5% | 5% | 31.5%
356251 | 1136980 | SUKHNA-RD6 | C2_0014RE_PH1 | Golden | Whitelist | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | E-2-31 | Civil | Antenna Support | Trays/ducts/conduits unfixed | Critical | Missing cable tray support | Aging | Converged Run | M/D | Converged Run | - | - | 1.75% | 7% | 31.5%
356251 | 1136992 | SUKHNA-RD6 | C2_0014RE_PH1 | Golden | Whitelist | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | F-10 | Generator | ATS / Engine | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…) | Critical | Oil leakage | Aging | Contractor | M/D | Converged Run | - | - | 2% | 10% | 31.5%
356251 | 1137002 | SUKHNA-RD6 | C2_0014RE_PH1 | Golden | Whitelist | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | F-12 | Generator | ATS / Engine | Unit earth | Critical | Earth cable not connected to earth ring | Stealth | Contractor | M/D | Converged Run | - | - | 2% | 10% | 31.5%
356251 | 1136996 | SUKHNA-RD6 | C2_0014RE_PH1 | Golden | Whitelist | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | F-41 | Generator | ATS / Engine | Some parts are (missing / stolen) | Critical | Missing fan grid | Aging | Contractor | M/D | Converged Run | - | - | 2% | 10% | 31.5%
356251 | 1137003 | SUKHNA-RD6 | C2_0014RE_PH1 | Golden | Whitelist | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | F-7 | Generator | ATS / Engine | Unit unfixed/not installed well | Critical | Light not exist & unisolated power cable | Aging | Contractor | M/D | Converged Run | - | - | 2% | 10% | 31.5%
356332 | 1140898 | 10TH-RSD1 | C5_0241CA_PH2 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-3-23 | Power System | GEDP | Cables termination/lugs (AC side), lugs (DC side) | Critical | Power cable has no terminal | Contractor | Contractor | M/D | Converged Run | - | - | 10% | 12% | 51%
356332 | 1140913 | 10TH-RSD1 | C5_0241CA_PH2 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-5-7 | Power System | DC Boxes | Unit unfixed/not installed well | Critical | DC box cover not fixed | Aging | Contractor | M/D | Converged Run | - | - | 2% | 4% | 51%
356332 | 1140923 | 10TH-RSD1 | C5_0241CA_PH2 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | B-15 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Components faulty | Critical | A/C 2 not work , please replay with current reading | Aging | Contractor | M/D | Converged Run | - | - | 4% | 12% | 51%
356332 | 1140925 | 10TH-RSD1 | C5_0241CA_PH2 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | B-7 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Unit unfixed/not installed well | Critical | Temp sensor not fixed & missing indicator & cable not protected in flexible | Aging | Contractor | M/D | Converged Run | - | - | 4% | 12% | 51%
356332 | 1140927 | 10TH-RSD1 | C5_0241CA_PH2 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | C-15 | Fire System | Fire Alarm and Fighting System | Components faulty | Critical | Fire panel not work ( Defected battery ) | Aging | Contractor | M/D | Converged Run | - | - | 5% | 5% | 51%
356414 | 1144783 | I-CTYSTR-COM_BBU1 | C01_1142CA_PH17 | Bronze | Old Sites (Before 2015) | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | A-6-18 | Power System | Rectifiers | Alarms on equipment (excluding ADM) | Major | alarm on equipment | Aging | Contractor | M/D | Converged Run | - | - | 5% | 5% | 61.5%
356414 | 1144799 | I-CTYSTR-COM_BBU1 | C01_1142CA_PH17 | Bronze | Old Sites (Before 2015) | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | D-12 | Equipment and DDF | Equipment and DDF | Unit earth | Major | equipment not earthed | Converged Run | Contractor | M/D | Converged Run | - | - | 3.5% | 7% | 61.5%
356414 | 1144792 | I-CTYSTR-COM_BBU1 | C01_1142CA_PH17 | Bronze | Old Sites (Before 2015) | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | earth plate missing | Stealth | Contractor | M/D | Converged Run | - | - | 2.5% | 2.5% | 61.5%
356413 | 1144767 | GOLDEN-PYRAMDS | C1_0531CA_PH4 | Silver | Nodal/VIP | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | A-6-18 | Power System | Rectifiers | Alarms on equipment (excluding ADM) | Major | alarm on equipment | Aging | Contractor | M/D | Converged Run | - | - | 5% | 5% | 62%
356413 | 1144771 | GOLDEN-PYRAMDS | C1_0531CA_PH4 | Silver | Nodal/VIP | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | earth cut | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 7% | 62%
356412 | 1144755 | M-ANDREA | C1_1154CA_PH8 | Bronze | Old Sites (Before 2015) | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | A-6-18 | Power System | Rectifiers | Alarms on equipment (excluding ADM) | Major | alarm on equipment | Aging | Contractor | M/D | Converged Run | - | - | 5% | 5% | 76%
356412 | 1144756 | M-ANDREA | C1_1154CA_PH8 | Bronze | Old Sites (Before 2015) | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | D-12 | Equipment and DDF | Equipment and DDF | Unit earth | Major | equipment nit earthed | Stealth | Contractor | M/D | Converged Run | - | - | 5% | 7% | 76%
356411 | 1144742 | I-MARIOT-MRAGE_BBU1 | C01_1118CA_PH05 | Silver | Nodal/VIP | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | E-1-65 | Civil | Shelter Body / Main Enclosure | Unused assets | Major | unuswd equipment | Converged Run | Contractor | M/D | Converged Run | - | - | 2.25% | 9% | 71%
356391 | 1143611 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-4-19 | Power System | Surge Arrestor | Alarms reporting to the OMC | Major | The surge alarm isn't connected | Contractor | Contractor | M/D | Converged Run | - | - | 3.333% | 5.833% | 20%
356391 | 1143620 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-6-18 | Power System | Rectifiers | Alarms on equipment (excluding ADM) | Major | Major and minor alarms appear on the rectifier | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 8% | 20%
356391 | 1143624 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | B-1 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Clean (not normal dust) | Major | IDU and ODU need cleaning (please provide the low/high pressure + current readings for all units) | Aging | Contractor | M/D | Converged Run | - | - | 1.714% | 12% | 20%
356391 | 1143628 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | B-20 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Major | Cables and refrigerant lines are not inserted in trays | Contractor | Contractor | M/D | Converged Run | - | - | 1.714% | 12% | 20%
356391 | 1143634 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | C-41 | Fire System | Fire Alarm and Fighting System | Some parts are (missing / stolen) | Major | One battery is missing | Stealth | Contractor | M/D | Converged Run | - | - | 3.333% | 10% | 20%
356391 | 1143646 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | E-1-41 | Civil | Shelter Body / Main Enclosure | Some parts are (missing / stolen) | Major | The ventilation fan is stolen | Stealth | Converged Run | M/D | Converged Run | - | - | 3% | 9% | 20%
356391 | 1143651 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | E-1-65 | Civil | Shelter Body / Main Enclosure | Unused assets | Major | Unused cables | Contractor | Contractor | M/D | Converged Run | - | - | 3% | 9% | 20%
356391 | 1143656 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | E-2-12 | Civil | Antenna Support | Unit earth | Major | Stolen earth connections of the tower | Stealth | Contractor | M/D | Converged Run | - | - | 2% | 7% | 20%
356391 | 1143655 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | E-2-34 | Civil | Antenna Support | Trays untied by metal belts | Major | Metal belts are needed | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 7% | 20%
356365 | 1142892 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-41 | Power System | Rectifiers | Some parts are (missing / stolen) | Major | protection cover | Aging | Contractor | M/D | Converged Run | - | - | 1.6% | 8% | 20.33%
356365 | 1142952 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | B-1 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Clean (not normal dust) | Major | clean | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 20.33%
356365 | 1142887 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | D-12 | Equipment and DDF | Equipment and DDF | Unit earth | Major | not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 20.33%
356365 | 1142869 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | D-20 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Major | arrange | Converged Run | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 20.33%
356365 | 1142876 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | D-31 | Equipment and DDF | Equipment and DDF | Trays/ducts/conduits unfixed | Major | fix tray support | Converged Run | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 20.33%
356365 | 1142890 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-28 | Civil | Shelter Body / Main Enclosure | Feeders without tray on the horizontal path | Major | out of tray | Converged Run | Converged Run | M/D | Converged Run | - | - | 1.5% | 9% | 20.33%
356365 | 1142932 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-20 | Civil | Antenna Support | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Major | arrange and protect | Converged Run | Contractor | M/D | Converged Run | - | - | 1% | 7% | 20.33%
356365 | 1142923 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-41 | Civil | Antenna Support | Some parts are (missing / stolen) | Major | lock | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 7% | 20.33%
356365 | 1142950 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-76 | Civil | Antenna Support | Beacon light function | Major | not working | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 7% | 20.33%
356365 | 1142925 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-15 | Civil | Fence / Roof | Components faulty | Major | extra building done by the guard and has access to the site from the fence | Guard | Converged Run | M/D | Converged Run | - | - | 1.75% | 7% | 20.33%
356365 | 1142930 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-28 | Civil | Fence / Roof | Feeders without tray on the horizontal path | Major | out of tray | Converged Run | Converged Run | M/D | Converged Run | - | - | 1.75% | 7% | 20.33%
356365 | 1142917 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-65 | Civil | Fence / Roof | Unused assets | Major | remove | Converged Run | Converged Run | M/D | Converged Run | - | - | 1.75% | 7% | 20.33%
356365 | 1142957 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | F-53 | Generator | ATS / Engine | High vibration/noise level (e.g. faulty rubber bases) | Major | high vibration | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 10% | 20.33%
356365 | 1142956 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | F-87 | Generator | ATS / Engine | Exhaust pipes insulation/fixation/kit | Major | isolate | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 10% | 20.33%
356365 | 1142958 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | F-9 | Generator | ATS / Engine | Door lock/handle that affects door from open easily or close firmly | Major | add lock | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 10% | 20.33%
356364 | 1142801 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-33 | Power System | Power Meter & Main Breaker | Trays covers missing/unfixed (if laid on the ground only) | Major | covers missing | Contractor | Contractor | M/D | Converged Run | - | - | 1.667% | 5% | 13.64%
356364 | 1142761 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-18 | Power System | Rectifiers | Alarms on equipment (excluding ADM) | Major | check | Contractor | Contractor | M/D | Converged Run | - | - | 1.6% | 8% | 13.64%
356364 | 1142768 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-7-12 | Power System | Batteries | Unit earth | Major | not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 1.429% | 2.262% | 13.64%
356364 | 1142775 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | B-1 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Clean (not normal dust) | Major | clean | Contractor | Contractor | M/D | Converged Run | - | - | 1.714% | 12% | 13.64%
356364 | 1142756 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | B-56 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | A/Cs ATS thermostat sensor (former 27 degree sensor) operation | Major | adjust | Contractor | Contractor | M/D | Converged Run | - | - | 1.714% | 12% | 13.64%
356364 | 1142758 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | C-41 | Fire System | Fire Alarm and Fighting System | Some parts are (missing / stolen) | Major | missing batteries | Contractor | Contractor | M/D | Converged Run | - | - | 3.333% | 10% | 13.64%
356364 | 1142778 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | D-12 | Equipment and DDF | Equipment and DDF | Unit earth | Major | not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 1.429% | 2.262% | 13.64%
356364 | 1142797 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | main earth missing | Stealth | Contractor | M/D | Converged Run | - | - | 1.286% | 9% | 13.64%
356364 | 1142843 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-65 | Civil | Shelter Body / Main Enclosure | Unused assets | Major | ununsed ,remove | Converged Run | Converged Run | M/D | Converged Run | - | - | 1.286% | 9% | 13.64%
356364 | 1142814 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-12 | Civil | Antenna Support | Unit earth | Major | not connected to earth ring | Stealth | Contractor | M/D | Converged Run | - | - | 0.7778% | 7% | 13.64%
356364 | 1142817 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-20 | Civil | Antenna Support | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Major | arrange and protect cables | Converged Run | Contractor | M/D | Converged Run | - | - | 0.7778% | 7% | 13.64%
356364 | 1142842 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-75 | Civil | Antenna Support | Feeders earth kit and connectors isolation | Major | isolate connectors | Aging | Contractor | M/D | Converged Run | - | - | 0.7778% | 7% | 13.64%
356364 | 1142841 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-76 | Civil | Antenna Support | Beacon light function | Major | not working | Contractor | Contractor | M/D | Converged Run | - | - | 0.7778% | 7% | 13.64%
356364 | 1142820 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-65 | Civil | Fence / Roof | Unused assets | Major | remove | Converged Run | Converged Run | M/D | Converged Run | - | - | 3.5% | 7% | 13.64%
356357 | 1142650 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-7-20 | Power System | Batteries | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Major | Battery pole cover not fixed | Aging | Contractor | M/D | Converged Run | - | - | 2.5% | 5% | 35%
356357 | 1142654 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | B-1 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Clean (not normal dust) | Major | Unclean A/C filter | Aging | Contractor | M/D | Converged Run | - | - | 2% | 12% | 35%
356357 | 1142701 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | E-2-27 | Civil | Antenna Support | Feeders unfixed/unorganized on the vertical path | Major | Cable not fixed | Aging | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 35%
356357 | 1142699 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | E-2-72 | Civil | Antenna Support | Stairs/climbing ladder condition (if applicable) | Major | Anti climb door open | Aging | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 35%
356349 | 1141744 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-18 | Power System | Rectifiers | Alarms on equipment (excluding ADM) | Major | check and clear | Contractor | Contractor | M/D | Converged Run | - | - | 2.667% | 8% | 53.83%
356349 | 1141741 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | D-20 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Major | arrange and protect cable | Contractor | Contractor | M/D | Converged Run | - | - | 2.5% | 5.667% | 53.83%
356349 | 1141786 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | main earth disconnected | Aging | Contractor | M/D | Converged Run | - | - | 2.5% | 8% | 53.83%
356349 | 1141739 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-65 | Civil | Shelter Body / Main Enclosure | Unused assets | Major | unused, remove | Converged Run | Converged Run | M/D | Converged Run | - | - | 2.5% | 8% | 53.83%
356349 | 1141779 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-12 | Civil | Antenna Support | Unit earth | Major | not connected to earth system and need cleaning as well | Contractor | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 53.83%
356349 | 1141778 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-41 | Civil | Antenna Support | Some parts are (missing / stolen) | Major | lock and close | Contractor | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 53.83%
356349 | 1141780 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-76 | Civil | Antenna Support | Beacon light function | Major | not working | Contractor | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 53.83%
356349 | 1141792 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-15 | Civil | Fence / Roof | Components faulty | Major | extra buildings related to the guard need to remove | Guard | Converged Run | M/D | Converged Run | - | - | 1.167% | 7% | 53.83%
356349 | 1141791 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-20 | Civil | Fence / Roof | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Major | protect sensors cables | Contractor | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 53.83%
356349 | 1141795 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-62 | Civil | Fence / Roof | Lights operation | Major | faulty only one is working | Contractor | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 53.83%
356349 | 1141782 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-65 | Civil | Fence / Roof | Unused assets | Major | unused roxtec | Converged Run | Converged Run | M/D | Converged Run | - | - | 1.167% | 7% | 53.83%
356349 | 1141794 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-69 | Civil | Fence / Roof | Barbed wire & supports | Major | rusty | Aging | Converged Run | M/D | Converged Run | - | - | 1.167% | 7% | 53.83%
356346 | 1141411 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-2-20 | Power System | Shared Panel | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Major | Cables of the guard room are not protected | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 4% | 28.5%
356346 | 1141373 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-3-9 | Power System | GEDP | Door lock/handle that affects door from open easily or close firmly | Major | Broken door lock of the GEDP | Contractor | Contractor | M/D | Converged Run | - | - | 2.5% | 4.5% | 28.5%
356346 | 1141377 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-4-19 | Power System | Surge Arrestor | Alarms reporting to the OMC | Major | The surge alarm isn't connected | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 9% | 28.5%
356346 | 1141384 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | B-1 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Clean (not normal dust) | Major | IDUs and ODUs need cleaning (please provide the low/high pressure + current readings for all units) | Aging | Contractor | M/D | Converged Run | - | - | 6% | 12% | 28.5%
356346 | 1141398 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | Stolen earth connections inside the shelter | Stealth | Contractor | M/D | Converged Run | - | - | 2% | 9% | 28.5%
356346 | 1141419 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | E-2-12 | Civil | Antenna Support | Unit earth | Major | Stolen earth connections of the tower | Stealth | Contractor | M/D | Converged Run | - | - | 1.4% | 7% | 28.5%
356346 | 1141413 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | E-2-20 | Civil | Antenna Support | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Major | The power cable of the halogen light is not protected | Contractor | Contractor | M/D | Converged Run | - | - | 1.4% | 7% | 28.5%
356346 | 1141416 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | E-2-34 | Civil | Antenna Support | Trays untied by metal belts | Major | Metal belts are needed | Contractor | Contractor | M/D | Converged Run | - | - | 1.4% | 7% | 28.5%
356345 | 1141577 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-41 | Power System | Power Meter & Main Breaker | Some parts are (missing / stolen) | Major | glass | Aging | Contractor | M/D | Converged Run | - | - | 0.7143% | 5% | 18.42%
356345 | 1141580 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-18 | Power System | Rectifiers | Alarms on equipment (excluding ADM) | Major | check and clear | Contractor | Contractor | M/D | Converged Run | - | - | 1.333% | 8% | 18.42%
356345 | 1141535 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | B-1 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Clean (not normal dust) | Major | clean | Contractor | Contractor | M/D | Converged Run | - | - | 1.25% | 10.75% | 18.42%
356345 | 1141538 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | B-53 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | High vibration/noise level (e.g. faulty rubber bases) | Major | check vibration | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 10.75% | 18.42%
356345 | 1141527 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | D-12 | Equipment and DDF | Equipment and DDF | Unit earth | Major | not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 1% | 7% | 18.42%
356345 | 1141553 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | D-22 | Equipment and DDF | Equipment and DDF | Cables/Feeders/Jumpers/Coaxial/FO/PCM connection tightness | Major | loose | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 7% | 18.42%
356345 | 1141581 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | D-26 | Equipment and DDF | Equipment and DDF | Messy DDF (less than 10 Krone Blocks or equivalent) | Major | arrange and test alarms | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 7% | 18.42%
356345 | 1141526 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | D-41 | Equipment and DDF | Equipment and DDF | Some parts are (missing / stolen) | Major | stolen router | Stealth | Converged Run | M/D | Converged Run | - | - | 1% | 7% | 18.42%
356345 | 1141571 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | main earth stolen | Stealth | Contractor | M/D | Converged Run | - | - | 1.8% | 9% | 18.42%
356345 | 1141562 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-12 | Civil | Antenna Support | Unit earth | Major | not connected to earth ring | Stealth | Contractor | M/D | Converged Run | - | - | 1.4% | 7% | 18.42%
356345 | 1141565 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-76 | Civil | Antenna Support | Beacon light function | Major | faulty | Contractor | Contractor | M/D | Converged Run | - | - | 1.4% | 7% | 18.42%
356345 | 1141588 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-15 | Civil | Fence / Roof | Components faulty | Major | fence missing part, easy to access | Aging | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 18.42%
356345 | 1141529 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-65 | Civil | Fence / Roof | Unused assets | Major | unused feeders | Converged Run | Converged Run | M/D | Converged Run | - | - | 1.75% | 7% | 18.42%
356344 | 1141342 | 6OCT-DIPLOMAT | C2_0882UP_PH12 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | D-20 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Major | protect and arrange cables | Converged Run | Contractor | M/D | Converged Run | - | - | 5% | 7% | 36%
356344 | 1141333 | 6OCT-DIPLOMAT | C2_0882UP_PH12 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | stolen earth | Stealth | Contractor | M/D | Converged Run | - | - | 1.5% | 9% | 36%
356344 | 1141350 | 6OCT-DIPLOMAT | C2_0882UP_PH12 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-41 | Civil | Antenna Support | Some parts are (missing / stolen) | Major | door | Aging | Contractor | M/D | Converged Run | - | - | 2.333% | 7% | 36%
356344 | 1141328 | 6OCT-DIPLOMAT | C2_0882UP_PH12 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-65 | Civil | Fence / Roof | Unused assets | Major | unused, remove | Converged Run | Converged Run | M/D | Converged Run | - | - | 5% | 5% | 36%
356343 | 1141295 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-18 | Power System | Rectifiers | Alarms on equipment (excluding ADM) | Major | check and clear | Contractor | Contractor | M/D | Converged Run | - | - | 2.5% | 5.5% | 31.33%
356343 | 1141281 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | C-18 | Fire System | Fire Alarm and Fighting System | Alarms on equipment (excluding ADM) | Major | check and clear | Contractor | Contractor | M/D | Converged Run | - | - | 2.5% | 5.833% | 31.33%
356343 | 1141304 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | D-12 | Equipment and DDF | Equipment and DDF | Unit earth | Major | not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 31.33%
356343 | 1141277 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | D-41 | Equipment and DDF | Equipment and DDF | Some parts are (missing / stolen) | Major | missing router | Converged Run | Converged Run | M/D | Converged Run | - | - | 1.75% | 7% | 31.33%
356343 | 1141303 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-41 | Civil | Antenna Support | Some parts are (missing / stolen) | Major | door | Aging | Contractor | M/D | Converged Run | - | - | 2.333% | 7% | 31.33%
356343 | 1141310 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-76 | Civil | Antenna Support | Beacon light function | Major | faulty | Contractor | Contractor | M/D | Converged Run | - | - | 2.333% | 7% | 31.33%
356342 | 1140576 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | C-18 | Fire System | Fire Alarm and Fighting System | Alarms on equipment (excluding ADM) | Major | check alarm and clear | Contractor | Contractor | M/D | Converged Run | - | - | 3.333% | 10% | 44.17%
356342 | 1140585 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | D-11 | Equipment and DDF | Equipment and DDF | Unit sharp edges | Major | protect cables from sharp edge | Aging | Contractor | M/D | Converged Run | - | - | 5% | 6% | 44.17%
356342 | 1140584 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | main earth is missing | Stealth | Contractor | M/D | Converged Run | - | - | 1.5% | 9% | 44.17%
356342 | 1140600 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-65 | Civil | Fence / Roof | Unused assets | Major | unused genset and tank | Converged Run | Converged Run | M/D | Converged Run | - | - | 2.333% | 7% | 44.17%
356341 | 1140643 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-41 | Power System | Rectifiers | Some parts are (missing / stolen) | Major | cover is missing | Converged Run | Contractor | M/D | Converged Run | - | - | 5% | 8% | 43%
356341 | 1140654 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | D-12 | Equipment and DDF | Equipment and DDF | Unit earth | Major | not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 43%
356341 | 1140645 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | D-26 | Equipment and DDF | Equipment and DDF | Messy DDF (less than 10 Krone Blocks or equivalent) | Major | arrange, add labels and check alarms | Contractor | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 43%
356341 | 1140626 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 2.25% | 9% | 43%
356341 | 1140659 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-20 | Civil | Antenna Support | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Major | protect cable and reinstall in its normal path | Contractor | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 43%
356341 | 1140664 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-76 | Civil | Antenna Support | Beacon light function | Major | not working | Contractor | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 43%
356341 | 1140621 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-65 | Civil | Fence / Roof | Unused assets | Major | remove cabinet | Converged Run | Converged Run | M/D | Converged Run | - | - | 3.5% | 7% | 43%
356340 | 1140457 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | C-18 | Fire System | Fire Alarm and Fighting System | Alarms on equipment (excluding ADM) | Major | check and fix | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 10% | 22.83%
356340 | 1140407 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | D-12 | Equipment and DDF | Equipment and DDF | Unit earth | Major | not earth | Contractor | Contractor | M/D | Converged Run | - | - | 1.667% | 6.667% | 22.83%
356340 | 1140427 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | main earth not connected | Contractor | Contractor | M/D | Converged Run | - | - | 3% | 9% | 22.83%
356340 | 1140440 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-12 | Civil | Antenna Support | Unit earth | Major | not connected to earth ring | Stealth | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 22.83%
356340 | 1140441 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-20 | Civil | Antenna Support | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Major | arrange and protect cables | Converged Run | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 22.83%
356340 | 1140446 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-27 | Civil | Antenna Support | Feeders unfixed/unorganized on the vertical path | Major | fix and arrange | Converged Run | Converged Run | M/D | Converged Run | - | - | 1.167% | 7% | 22.83%
356340 | 1140412 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-65 | Civil | Fence / Roof | Unused assets | Major | unused feeders | Converged Run | Converged Run | M/D | Converged Run | - | - | 5% | 7% | 22.83%
356339 | 1140485 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | B-1 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Clean (not normal dust) | Major | clean | Contractor | Contractor | M/D | Converged Run | - | - | 3% | 12% | 27%
356339 | 1140479 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | C-18 | Fire System | Fire Alarm and Fighting System | Alarms on equipment (excluding ADM) | Major | check alarm and fix | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 10% | 27%
356339 | 1140527 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | D-12 | Equipment and DDF | Equipment and DDF | Unit earth | Major | not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 2.5% | 6.5% | 27%
356339 | 1140525 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | main earh stolen | Stealth | Contractor | M/D | Converged Run | - | - | 1.5% | 9% | 27%
356339 | 1140523 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-12 | Civil | Antenna Support | Unit earth | Major | main earh stolen | Stealth | Contractor | M/D | Converged Run | - | - | 1% | 7% | 27%
356339 | 1140475 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-27 | Civil | Antenna Support | Feeders unfixed/unorganized on the vertical path | Major | arrange and fix well | Converged Run | Contractor | M/D | Converged Run | - | - | 1% | 7% | 27%
356339 | 1140513 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-75 | Civil | Antenna Support | Feeders earth kit and connectors isolation | Major | isolate connectors | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 7% | 27%
356339 | 1140553 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-65 | Civil | Fence / Roof | Unused assets | Major | unused feeders | Converged Run | Converged Run | M/D | Converged Run | - | - | 5% | 5% | 27%
356338 | 1140335 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | B-1 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Clean (not normal dust) | Major | clean | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 5.5%
356338 | 1140337 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | B-53 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | High vibration/noise level (e.g. faulty rubber bases) | Major | high vibration and fix cover | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 5.5%
356338 | 1140293 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | D-12 | Equipment and DDF | Equipment and DDF | Unit earth | Major | wrong earth connections | Converged Run | Contractor | M/D | Converged Run | - | - | 1.4% | 7% | 5.5%
356338 | 1140329 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | D-20 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Major | protect cables | Aging | Contractor | M/D | Converged Run | - | - | 1.4% | 7% | 5.5%
356338 | 1140378 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-41 | Civil | Shelter Body / Main Enclosure | Some parts are (missing / stolen) | Major | door hook | Contractor | Contractor | M/D | Converged Run | - | - | 1.286% | 9% | 5.5%
356338 | 1140301 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-65 | Civil | Shelter Body / Main Enclosure | Unused assets | Major | unused batteries | Converged Run | Converged Run | M/D | Converged Run | - | - | 1.286% | 9% | 5.5%
356338 | 1140363 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | F-8 | Generator | ATS / Engine | Door/frame fixation that affects door from open easily or close firmly | Major | close | Contractor | Contractor | M/D | Converged Run | - | - | 1.25% | 10% | 5.5%
356338 | 1140364 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | F-87 | Generator | ATS / Engine | Exhaust pipes insulation/fixation/kit | Major | isolate | Contractor | Contractor | M/D | Converged Run | - | - | 1.25% | 10% | 5.5%
356337 | 1141171 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-7-12 | Power System | Batteries | Unit earth | Major | Earth cable of battery string is not connected to earth ring | Stealth | Contractor | M/D | Converged Run | - | - | 1.25% | 5% | 19.5%
356337 | 1141170 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-7-20 | Power System | Batteries | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Major | Missing battery pole cover | Aging | Contractor | M/D | Converged Run | - | - | 1.25% | 5% | 19.5%
356337 | 1141173 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | B-1 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Clean (not normal dust) | Major | Unclean A/C ODU & Condencer | Aging | Contractor | M/D | Converged Run | - | - | 3% | 12% | 19.5%
356337 | 1141180 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | B-19 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Alarms reporting to the OMC | Major | A/C fail alarm not report the OMC | Aging | Contractor | M/D | Converged Run | - | - | 3% | 12% | 19.5%
356337 | 1141210 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | D-26 | Equipment and DDF | Equipment and DDF | Messy DDF (less than 10 Krone Blocks or equivalent) | Major | DDF cover not fixed | Aging | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 19.5%
356337 | 1141225 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | Earth bar stolen | Stealth | Contractor | M/D | Converged Run | - | - | 2.5% | 7.833% | 19.5%
356337 | 1141250 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | E-2-27 | Civil | Antenna Support | Feeders unfixed/unorganized on the vertical path | Major | Cable not fixed & bad arrangement | Aging | Contractor | M/D | Converged Run | - | - | 2.333% | 7% | 19.5%
356337 | 1141248 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | E-2-72 | Civil | Antenna Support | Stairs/climbing ladder condition (if applicable) | Major | Anti climb door open | Aging | Contractor | M/D | Converged Run | - | - | 2.333% | 7% | 19.5%
356337 | 1141244 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | E-3-28 | Civil | Fence / Roof | Feeders without tray on the horizontal path | Major | Cable out of tray | Aging | Contractor | M/D | Converged Run | - | - | 5% | 5% | 19.5%
356330 | 1140212 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | D-12 | Equipment and DDF | Equipment and DDF | Unit earth | Major | stolen earth | Stealth | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 34.5%
356330 | 1140230 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | main earth missing | Stealth | Contractor | M/D | Converged Run | - | - | 1.286% | 9% | 34.5%
356330 | 1140225 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-76 | Civil | Antenna Support | Beacon light function | Major | faulty and beacon is not working | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 7% | 34.5%
356330 | 1140226 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-65 | Civil | Fence / Roof | Unused assets | Major | unused cabinet and enclosure | Converged Run | Converged Run | M/D | Converged Run | - | - | 3.5% | 7% | 34.5%
356330 | 1140251 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | F-53 | Generator | ATS / Engine | High vibration/noise level (e.g. faulty rubber bases) | Major | replace | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 10% | 34.5%
356330 | 1140246 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | F-87 | Generator | ATS / Engine | Exhaust pipes insulation/fixation/kit | Major | isolate | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 10% | 34.5%
356330 | 1140245 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | F-9 | Generator | ATS / Engine | Door lock/handle that affects door from open easily or close firmly | Major | no lock | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 10% | 34.5%
356328 | 1140004 | DREAM-PARK | C3_0183UP_PH3 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | A-5-12 | Power System | DC Boxes | Unit earth | Major | not earthed | Stealth | Contractor | M/D | Converged Run | - | - | 2% | 3% | 53%
356328 | 1139989 | DREAM-PARK | C3_0183UP_PH3 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-18 | Power System | Rectifiers | Alarms on equipment (excluding ADM) | Major | check and clear alarm | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 8% | 53%
356328 | 1140021 | DREAM-PARK | C3_0183UP_PH3 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | D-12 | Equipment and DDF | Equipment and DDF | Unit earth | Major | disconnected earth | Stealth | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 53%
356328 | 1140030 | DREAM-PARK | C3_0183UP_PH3 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | D-20 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Major | protect and arrange cables | Contractor | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 53%
356328 | 1140017 | DREAM-PARK | C3_0183UP_PH3 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | D-41 | Equipment and DDF | Equipment and DDF | Some parts are (missing / stolen) | Major | covers | Aging | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 53%
356328 | 1140025 | DREAM-PARK | C3_0183UP_PH3 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | no main earth exist | Stealth | Contractor | M/D | Converged Run | - | - | 2.25% | 9% | 53%
356326 | 1140760 | DK-TILBANA | C1_0602DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | A-4-19 | Power System | Surge Arrestor | Alarms reporting to the OMC | Major | Surge arrestor alarm isn't appearing at OMC. | Aging | Contractor | M/D | Converged Run | - | - | 5% | 7% | 67%
356326 | 1140769 | DK-TILBANA | C1_0602DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | A-6-18 | Power System | Rectifiers | Alarms on equipment (excluding ADM) | Major | Site has old rectifier alarms. | Aging | Contractor | M/D | Converged Run | - | - | 4% | 8% | 67%
356326 | 1140765 | DK-TILBANA | C1_0602DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | B-1 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Clean (not normal dust) | Major | Area needs cleaning. | Aging | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 67%
356326 | 1140762 | DK-TILBANA | C1_0602DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | E-2-12 | Civil | Antenna Support | Unit earth | Major | - | Aging | Contractor | M/D | Converged Run | - | - | 5% | 5% | 67%
356324 | 1140717 | DK-BELGAY-VLG | C1_3774DE_PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | A-4-19 | Power System | Surge Arrestor | Alarms reporting to the OMC | Major | Surge arrestor alarm isn't appearing at OMC. | Aging | Contractor | M/D | Converged Run | - | - | 5% | 5% | 77%
356324 | 1140724 | DK-BELGAY-VLG | C1_3774DE_PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | B-1 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Clean (not normal dust) | Major | A/C's need cleaning. | Aging | Contractor | M/D | Converged Run | - | - | 4% | 12% | 77%
356323 | 1140686 | DK-MIT-KHAYRON | C3_3257DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | A-4-19 | Power System | Surge Arrestor | Alarms reporting to the OMC | Major | No surge arrestor alarm. | Aging | Contractor | M/D | Converged Run | - | - | 5% | 5% | 45%
356323 | 1140691 | DK-MIT-KHAYRON | C3_3257DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | A-6-18 | Power System | Rectifiers | Alarms on equipment (excluding ADM) | Major | Site has old rectifier alarm due to faulty surge arrestor. | Aging | Converged Run | M/D | Converged Run | - | - | 2.667% | 8% | 45%
356323 | 1140677 | DK-MIT-KHAYRON | C3_3257DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | D-20 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Major | Cable need proper installation and protection. | Aging | Contractor | M/D | Converged Run | - | - | 2.333% | 7% | 45%
356321 | 1140887 | 23_S_ ZAHREYA-TOWN_ 0583AL_S000 | C3_0583AL_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Abdullatief | Eslam Ahmed | Sectra | 2019-09-17 | AGLI | Orascom | ALEX | Alex East | V10R00 | A-1-41 | Power System | Power Meter & Main Breaker | Some parts are (missing / stolen) | Major | Bad fixation for power meter | Converged Run | Converged Run | M/D | Converged Run | - | - | 2.5% | 5% | 75.5%
356321 | 1140863 | 23_S_ ZAHREYA-TOWN_ 0583AL_S000 | C3_0583AL_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Abdullatief | Eslam Ahmed | Sectra | 2019-09-17 | AGLI | Orascom | ALEX | Alex East | V10R00 | D-41 | Equipment and DDF | Equipment and DDF | Some parts are (missing / stolen) | Major | Covers uninstalled | Contractor | Contractor | M/D | Converged Run | - | - | 2.5% | 3.5% | 75.5%
356321 | 1140868 | 23_S_ ZAHREYA-TOWN_ 0583AL_S000 | C3_0583AL_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Abdullatief | Eslam Ahmed | Sectra | 2019-09-17 | AGLI | Orascom | ALEX | Alex East | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | Earth incomplete (There is no connection to main earth rod) | Stealth | Converged Run | M/D | Converged Run | - | - | 1.8% | 9% | 75.5%
356318 | 1139922 | QL-DEER-2 | C1_3275DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | A-6-18 | Power System | Rectifiers | Alarms on equipment (excluding ADM) | Major | Rectifier has minor and major alarm | Contractor | Contractor | M/D | Converged Run | - | - | 2.667% | 8% | 43.17%
356318 | 1139906 | QL-DEER-2 | C1_3275DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | B-19 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Alarms reporting to the OMC | Major | Alarm cable disconnected (Alarms not appear at OMC) | Contractor | Contractor | M/D | Converged Run | - | - | 2.5% | 10.5% | 43.17%
356318 | 1139931 | QL-DEER-2 | C1_3275DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | D-31 | Equipment and DDF | Equipment and DDF | Trays/ducts/conduits unfixed | Major | Tray need proper fixation with ground | Aging | Converged Run | M/D | Converged Run | - | - | 1.75% | 7% | 43.17%
356318 | 1139912 | QL-DEER-2 | C1_3275DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | D-41 | Equipment and DDF | Equipment and DDF | Some parts are (missing / stolen) | Major | Covers uninstalled | Contractor | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 43.17%
356318 | 1139927 | QL-DEER-2 | C1_3275DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | Earth incomplete (There is no connection to main earth rod) | Contractor | Contractor | M/D | Converged Run | - | - | 2.25% | 9% | 43.17%
356317 | 1139820 | QL-DEER | C2_0423DE_PH4 | Golden | Whitelist | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | A-6-18 | Power System | Rectifiers | Alarms on equipment (excluding ADM) | Major | Rectifier has minor and major alarm | Contractor | Contractor | M/D | Converged Run | - | - | 4% | 8% | 44%
356317 | 1139827 | QL-DEER | C2_0423DE_PH4 | Golden | Whitelist | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | B-56 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | A/Cs ATS thermostat sensor (former 27 degree sensor) operation | Major | Timer not adjusted on auto mood | Contractor | Contractor | M/D | Converged Run | - | - | 3% | 12% | 44%
356317 | 1139819 | QL-DEER | C2_0423DE_PH4 | Golden | Whitelist | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | D-41 | Equipment and DDF | Equipment and DDF | Some parts are (missing / stolen) | Major | Covers uninstalled | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 5% | 44%
356317 | 1139830 | QL-DEER | C2_0423DE_PH4 | Golden | Whitelist | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | Loose earth cable | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 7% | 44%
356315 | 1139782 | QL-MUSHTAHER | C1_0703DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | A-6-18 | Power System | Rectifiers | Alarms on equipment (excluding ADM) | Major | Rectifier has minor alarm | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 5% | 42%
356315 | 1139788 | QL-MUSHTAHER | C1_0703DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | B-56 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | A/Cs ATS thermostat sensor (former 27 degree sensor) operation | Major | Timer not adjusted on auto mood | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 42%
356315 | 1139780 | QL-MUSHTAHER | C1_0703DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | D-41 | Equipment and DDF | Equipment and DDF | Some parts are (missing / stolen) | Major | Covers uninstalled | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 5% | 42%
356315 | 1139810 | QL-MUSHTAHER | C1_0703DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | Loose earth cable | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 7% | 42%
356315 | 1139804 | QL-MUSHTAHER | C1_0703DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | E-2-76 | Civil | Antenna Support | Beacon light function | Major | Beacon light not working | Aging | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 42%
356315 | 1139803 | QL-MUSHTAHER | C1_0703DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | E-3-62 | Civil | Fence / Roof | Lights operation | Major | Halogen light not working | Aging | Contractor | M/D | Converged Run | - | - | 3.5% | 7% | 42%
356313 | 1139764 | 6th October 5 | C1_8032UP_PH2 | Bronze | Whitelist | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | B-53 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | High vibration/noise level (e.g. faulty rubber bases) | Major | high vibration | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 46%
356313 | 1139737 | 6th October 5 | C1_8032UP_PH2 | Bronze | Whitelist | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | B-56 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | A/Cs ATS thermostat sensor (former 27 degree sensor) operation | Major | adjust | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 46%
356313 | 1139766 | 6th October 5 | C1_8032UP_PH2 | Bronze | Whitelist | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | not connected to main earth | Stealth | Contractor | M/D | Converged Run | - | - | 3% | 9% | 46%
356313 | 1139747 | 6th October 5 | C1_8032UP_PH2 | Bronze | Whitelist | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-65 | Civil | Shelter Body / Main Enclosure | Unused assets | Major | unused roxtec | Converged Run | Converged Run | M/D | Converged Run | - | - | 3% | 9% | 46%
356311 | 1139571 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | B-1 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Clean (not normal dust) | Major | clean | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 12% | 22%
356311 | 1139606 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | B-19 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Alarms reporting to the OMC | Major | diaconnected | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 12% | 22%
356311 | 1139560 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | D-41 | Equipment and DDF | Equipment and DDF | Some parts are (missing / stolen) | Major | stolen ZTE router | Stealth | Converged Run | M/D | Converged Run | - | - | 2.333% | 7% | 22%
356311 | 1139592 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | main earth stolen | Stealth | Contractor | M/D | Converged Run | - | - | 1.8% | 9% | 22%
356311 | 1139563 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-76 | Civil | Antenna Support | Beacon light function | Major | check connection and turned ON the CB | Aging | Contractor | M/D | Converged Run | - | - | 2.333% | 7% | 22%
356309 | 1139327 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-4-19 | Power System | Surge Arrestor | Alarms reporting to the OMC | Major | The surge alarm isn't connected | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 5% | 29.17%
356309 | 1139346 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | B-1 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Clean (not normal dust) | Major | IDUs and ODUs need cleaning (please provide the low/high pressure + current readings for all units) | Aging | Contractor | M/D | Converged Run | - | - | 2.5% | 6.833% | 29.17%
356309 | 1139356 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | D-20 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Major | Jumpers and feeders are not inserted in trays | Converged Run | Contractor | M/D | Converged Run | - | - | 1.4% | 7% | 29.17%
356309 | 1139362 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | D-31 | Equipment and DDF | Equipment and DDF | Trays/ducts/conduits unfixed | Major | Supports of basket trays are not fixed well | Contractor | Contractor | M/D | Converged Run | - | - | 1.4% | 7% | 29.17%
356309 | 1139367 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | E-2-11 | Civil | Antenna Support | Unit sharp edges | Major | Sharp edges of cable trays | Contractor | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 29.17%
356309 | 1139369 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | E-2-27 | Civil | Antenna Support | Feeders unfixed/unorganized on the vertical path | Major | Bad arrangement of cables and feeders | Contractor | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 29.17%
356309 | 1139364 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | E-2-34 | Civil | Antenna Support | Trays untied by metal belts | Major | Metal belts are needed | Contractor | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 29.17%
356309 | 1139375 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | F-8 | Generator | ATS / Engine | Door/frame fixation that affects door from open easily or close firmly | Major | Doors of the genset are not closed | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 10% | 29.17%
356285 | 1138177 | Khattara 1 & 2 BSC | C1_8050UP_PH9_1 | Golden | Whitelist | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | Shelter door earth cable is missing | Contractor | Contractor | M/D | Converged Run | - | - | 3% | 9% | 64%
356285 | 1138173 | Khattara 1 & 2 BSC | C1_8050UP_PH9_1 | Golden | Whitelist | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | E-1-65 | Civil | Shelter Body / Main Enclosure | Unused assets | Major | Unused rectifier panel inside shelter | Converged Run | Converged Run | M/D | Converged Run | - | - | 3% | 9% | 64%
356284 | 1138129 | 01_W_QN-KHATARA_0273UP | C1_0273UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | D-20 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Major | 3G cables are not protected | Converged Run | Converged Run | M/D | Converged Run | - | - | 2.333% | 7% | 58%
356284 | 1138136 | 01_W_QN-KHATARA_0273UP | C1_0273UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | E-1-65 | Civil | Shelter Body / Main Enclosure | Unused assets | Major | Unused Duct inside shelter | Converged Run | Contractor | M/D | Converged Run | - | - | 2.5% | 2.5% | 58%
356284 | 1138164 | 01_W_QN-KHATARA_0273UP | C1_0273UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | E-2-84 | Civil | Antenna Support | Bolts & nuts of the base (missing/loose) | Major | loose bolt at tower base | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 5% | 58%
356284 | 1138160 | 01_W_QN-KHATARA_0273UP | C1_0273UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | E-3-65 | Civil | Fence / Roof | Unused assets | Major | Unused Gen left in the site | Converged Run | Converged Run | M/D | Converged Run | - | - | 2.5% | 2.5% | 58%
356283 | 1138112 | 01_H_QN-MAHROUSA_0274UP | C1_0274UP_PH8 | Golden | BSC | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | E-2-27 | Civil | Antenna Support | Feeders unfixed/unorganized on the vertical path | Major | feeder on the tower need attachment and arrangement | Converged Run | Contractor | M/D | Converged Run | - | - | 5% | 5% | 70%
356283 | 1138105 | 01_H_QN-MAHROUSA_0274UP | C1_0274UP_PH8 | Golden | BSC | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | F-89 | Generator | ATS / Engine | Filters condition oil/fuel/air | Major | oil & fuel filters are not original | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 7% | 70%
356282 | 1138349 | BH-SHOBRA-RIS | C1_4360DE_PH13 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | D-26 | Equipment and DDF | Equipment and DDF | Messy DDF (less than 10 Krone Blocks or equivalent) | Major | Wires need installation inside crona | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 5% | 67.67%
356282 | 1138364 | BH-SHOBRA-RIS | C1_4360DE_PH13 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | E-2-76 | Civil | Antenna Support | Beacon light function | Major | Beacon light not working | Aging | Contractor | M/D | Converged Run | - | - | 5% | 5.667% | 67.67%
356282 | 1138372 | BH-SHOBRA-RIS | C1_4360DE_PH13 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | F-87 | Generator | ATS / Engine | Exhaust pipes insulation/fixation/kit | Major | Need proper isolation | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 9% | 67.67%
356280 | 1138276 | BH-KFR-QASHASH | C4_0545DE_PH8 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | A-6-18 | Power System | Rectifiers | Alarms on equipment (excluding ADM) | Major | Rectifier has minor alarm | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 7% | 46%
356280 | 1138297 | BH-KFR-QASHASH | C4_0545DE_PH8 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | Loose earth cable | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 7% | 46%
356280 | 1138293 | BH-KFR-QASHASH | C4_0545DE_PH8 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | E-2-76 | Civil | Antenna Support | Beacon light function | Major | Terminals requried // Protective cover requried | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 6% | 46%
356280 | 1138285 | BH-KFR-QASHASH | C4_0545DE_PH8 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | E-3-62 | Civil | Fence / Roof | Lights operation | Major | Welding cables // Cables unisollated well with PVC pipes | Contractor | Contractor | M/D | Converged Run | - | - | 3.5% | 7% | 46%
356278 | 1138073 | BH-DAHRIA | C2_3508DE_PH13 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Tanta | V10R00 | A-6-18 | Power System | Rectifiers | Alarms on equipment (excluding ADM) | Major | Rectifier has major alarm | Contractor | Contractor | M/D | Converged Run | - | - | 4% | 8% | 73%
356278 | 1138079 | BH-DAHRIA | C2_3508DE_PH13 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Tanta | V10R00 | C-41 | Fire System | Fire Alarm and Fighting System | Some parts are (missing / stolen) | Major | Fire extinguisher has missing hose | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 7% | 73%
356278 | 1138074 | BH-DAHRIA | C2_3508DE_PH13 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Tanta | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | Lose earth cables | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 7% | 73%
356274 | 1137937 | MF-BANI-SALAMA | C1-3232DE-PH12 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-09 | AGLI | AGLI-Contractor | Delta South | Sadat | V10R00 | A-1-41 | Power System | Power Meter & Main Breaker | Some parts are (missing / stolen) | Major | Panel need proper sealing | Aging | Contractor | M/D | Converged Run | - | - | 1.667% | 1.667% | 71%
356274 | 1137933 | MF-BANI-SALAMA | C1-3232DE-PH12 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-09 | AGLI | AGLI-Contractor | Delta South | Sadat | V10R00 | A-6-18 | Power System | Rectifiers | Alarms on equipment (excluding ADM) | Major | Rectifier has major alarm | Contractor | Contractor | M/D | Converged Run | - | - | 5% | 7% | 71%
356274 | 1137929 | MF-BANI-SALAMA | C1-3232DE-PH12 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-09 | AGLI | AGLI-Contractor | Delta South | Sadat | V10R00 | C-41 | Fire System | Fire Alarm and Fighting System | Some parts are (missing / stolen) | Major | Fire extinguisher without validity certificate | Contractor | Contractor | M/D | Converged Run | - | - | 1.667% | 1.667% | 71%
356274 | 1137912 | MF-BANI-SALAMA | C1-3232DE-PH12 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-09 | AGLI | AGLI-Contractor | Delta South | Sadat | V10R00 | D-41 | Equipment and DDF | Equipment and DDF | Some parts are (missing / stolen) | Major | Covers uninstalled | Contractor | Contractor | M/D | Converged Run | - | - | 1.667% | 2.667% | 71%
356274 | 1137919 | MF-BANI-SALAMA | C1-3232DE-PH12 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-09 | AGLI | AGLI-Contractor | Delta South | Sadat | V10R00 | E-2-73 | Civil | Antenna Support | Anticlimbing door warning sign | Major | Door uninstalled | Aging | Converged Run | M/D | Converged Run | - | - | 1.75% | 7% | 71%
356274 | 1137925 | MF-BANI-SALAMA | C1-3232DE-PH12 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-09 | AGLI | AGLI-Contractor | Delta South | Sadat | V10R00 | E-2-76 | Civil | Antenna Support | Beacon light function | Major | Beacon light not working | Aging | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 71%
356274 | 1137924 | MF-BANI-SALAMA | C1-3232DE-PH12 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-09 | AGLI | AGLI-Contractor | Delta South | Sadat | V10R00 | E-3-62 | Civil | Fence / Roof | Lights operation | Major | Light not working | Aging | Contractor | M/D | Converged Run | - | - | 2.333% | 7% | 71%
356266 | 1137516 | AT-QUSIYA5 | C1_3920UP_PH15 | Bronze | New Sites (After 2015) | Atef Zidan | Mohamed Abd Assalam Abass | Sectra | 2019-09-08 | NGLI | Huawei | North Upper | Asyout | V10R00 | A-6-18 | Power System | Rectifiers | Alarms on equipment (excluding ADM) | Major | Alarm was exists on rectifier control panel to be cleared | New Sites | Converged Run | M/D | Converged Run | - | - | 5% | 7% | 81%
356264 | 1138311 | SK-QUDAH | C1-3402DE-PH13 | Golden | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | A-4-19 | Power System | Surge Arrestor | Alarms reporting to the OMC | Major | No surge arrestor alarm. | Aging | Contractor | M/D | Converged Run | - | - | 5% | 5% | 44%
356264 | 1138313 | SK-QUDAH | C1-3402DE-PH13 | Golden | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | A-6-18 | Power System | Rectifiers | Alarms on equipment (excluding ADM) | Major | Site has old rectifier alarm. | Aging | Contractor | M/D | Converged Run | - | - | 5% | 5% | 44%
356264 | 1138335 | SK-QUDAH | C1-3402DE-PH13 | Golden | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | E-1-41 | Civil | Shelter Body / Main Enclosure | Some parts are (missing / stolen) | Major | Roxtec is required. | Aging | Converged Run | M/D | Converged Run | - | - | 4.5% | 9% | 44%
356264 | 1138336 | SK-QUDAH | C1-3402DE-PH13 | Golden | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | E-2-76 | Civil | Antenna Support | Beacon light function | Major | Beacon and halogen light isn't working. | Aging | Contractor | M/D | Converged Run | - | - | 5% | 5% | 44%
356264 | 1138324 | SK-QUDAH | C1-3402DE-PH13 | Golden | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | E-3-20 | Civil | Fence / Roof | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Major | Fence gate sensor cable is cut and need adjust. | Aging | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 44%
356263 | 1138240 | SK-SHARQAYA | C1-3793DE-PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | A-4-19 | Power System | Surge Arrestor | Alarms reporting to the OMC | Major | No surge arrestor alarm. | Aging | Contractor | M/D | Converged Run | - | - | 5% | 5% | 37.67%
356263 | 1138262 | SK-SHARQAYA | C1-3793DE-PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | E-3-65 | Civil | Fence / Roof | Unused assets | Major | Unused fuel tank needs to be removed. | Aging | Contractor | M/D | Converged Run | - | - | 3.5% | 7% | 37.67%
356254 | 1137216 | SZ-MENA-OASIS | C1_0032RE_PH1 | Golden | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | B-1 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Clean (not normal dust) | Major | Unclean A/C ODU & Condencer | Aging | Contractor | M/D | Converged Run | - | - | 1.667% | 9.167% | 31.17%
356254 | 1137250 | SZ-MENA-OASIS | C1_0032RE_PH1 | Golden | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | Earth bar stolen | Stealth | Contractor | M/D | Converged Run | - | - | 3% | 9% | 31.17%
356254 | 1137255 | SZ-MENA-OASIS | C1_0032RE_PH1 | Golden | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | E-1-41 | Civil | Shelter Body / Main Enclosure | Some parts are (missing / stolen) | Major | Missing site information | Aging | Contractor | M/D | Converged Run | - | - | 3% | 9% | 31.17%
356254 | 1137258 | SZ-MENA-OASIS | C1_0032RE_PH1 | Golden | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | E-2-27 | Civil | Antenna Support | Feeders unfixed/unorganized on the vertical path | Major | Cable not fixed | Aging | Contractor | M/D | Converged Run | - | - | 3.5% | 7% | 31.17%
356254 | 1137256 | SZ-MENA-OASIS | C1_0032RE_PH1 | Golden | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | E-2-73 | Civil | Antenna Support | Anticlimbing door warning sign | Major | Anti climb door open | Aging | Contractor | M/D | Converged Run | - | - | 3.5% | 7% | 31.17%
356251 | 1136954 | SUKHNA-RD6 | C2_0014RE_PH1 | Golden | Whitelist | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | A-7-12 | Power System | Batteries | Unit earth | Major | Battery earth cable disconnected | Stealth | Contractor | M/D | Converged Run | - | - | 2.5% | 5% | 31.5%
356251 | 1136956 | SUKHNA-RD6 | C2_0014RE_PH1 | Golden | Whitelist | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | B-1 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Clean (not normal dust) | Major | Unclean A/C ODU & Condencer | Aging | Contractor | M/D | Converged Run | - | - | 1.25% | 6.25% | 31.5%
356251 | 1136981 | SUKHNA-RD6 | C2_0014RE_PH1 | Golden | Whitelist | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | E-2-20 | Civil | Antenna Support | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits | Major | Cable out of tray | Aging | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 31.5%
356251 | 1136983 | SUKHNA-RD6 | C2_0014RE_PH1 | Golden | Whitelist | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | E-2-27 | Civil | Antenna Support | Feeders unfixed/unorganized on the vertical path | Major | Cable not fixed | Aging | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 31.5%
356251 | 1136982 | SUKHNA-RD6 | C2_0014RE_PH1 | Golden | Whitelist | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | E-2-72 | Civil | Antenna Support | Stairs/climbing ladder condition (if applicable) | Major | Anti climb door open | Aging | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 31.5%
356251 | 1136990 | SUKHNA-RD6 | C2_0014RE_PH1 | Golden | Whitelist | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | F-9 | Generator | ATS / Engine | Door lock/handle that affects door from open easily or close firmly | Major | Generator door broken | Aging | Converged Run | M/D | Converged Run | - | - | 2% | 10% | 31.5%
356332 | 1140919 | 10TH-RSD1 | C5_0241CA_PH2 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-7-12 | Power System | Batteries | Unit earth | Major | Earth cable of battery string disconnected | Stealth | Contractor | M/D | Converged Run | - | - | 2.5% | 2.5% | 51%
356332 | 1140920 | 10TH-RSD1 | C5_0241CA_PH2 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | B-1 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Clean (not normal dust) | Major | Unclean A/C ODU & Condencer | Aging | Contractor | M/D | Converged Run | - | - | 4% | 12% | 51%
356332 | 1140940 | 10TH-RSD1 | C5_0241CA_PH2 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | E-1-12 | Civil | Shelter Body / Main Enclosure | Unit earth | Major | Earth bar stolen | Stealth | Contractor | M/D | Converged Run | - | - | 2.5% | 4.5% | 51%
356332 | 1140947 | 10TH-RSD1 | C5_0241CA_PH2 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | E-2-27 | Civil | Antenna Support | Feeders unfixed/unorganized on the vertical path | Major | Cable not fixed | Aging | Contractor | M/D | Converged Run | - | - | 5% | 5% | 51%
356414 | 1144790 | I-CTYSTR-COM_BBU1 | C01_1142CA_PH17 | Bronze | Old Sites (Before 2015) | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | A-5-8 | Power System | DC Boxes | Door/frame fixation that affects door from open easily or close firmly | Minor | frame not fixed | Converged Run | Contractor | M/D | Converged Run | - | - | 2% | 2% | 61.5%
356414 | 1144798 | I-CTYSTR-COM_BBU1 | C01_1142CA_PH17 | Bronze | Old Sites (Before 2015) | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | A-7-1 | Power System | Batteries | Clean (not normal dust) | Minor | cleaning | Aging | Contractor | M/D | Converged Run | - | - | 2% | 2% | 61.5%
356413 | 1144766 | GOLDEN-PYRAMDS | C1_0531CA_PH4 | Silver | Nodal/VIP | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | A-5-8 | Power System | DC Boxes | Door/frame fixation that affects door from open easily or close firmly | Minor | frame not fixed | Converged Run | Contractor | M/D | Converged Run | - | - | 2% | 2% | 62%
356413 | 1144768 | GOLDEN-PYRAMDS | C1_0531CA_PH4 | Silver | Nodal/VIP | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | D-21 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | cables not organized | Converged Run | Contractor | M/D | Converged Run | - | - | 2% | 2% | 62%
356413 | 1144772 | GOLDEN-PYRAMDS | C1_0531CA_PH4 | Silver | Nodal/VIP | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | E-1-35 | Civil | Shelter Body / Main Enclosure | Trays/Roxtec/Plate not earthed | Minor | roxtec not earthed | Converged Run | Contractor | M/D | Converged Run | - | - | 2% | 7% | 62%
356412 | 1144754 | M-ANDREA | C1_1154CA_PH8 | Bronze | Old Sites (Before 2015) | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | A-3-32 | Power System | GEDP | Ducts/conduits covers missing/unfixed | Minor | missin gduct covers | Converged Run | Contractor | M/D | Converged Run | - | - | 2% | 2% | 76%
356412 | 1144753 | M-ANDREA | C1_1154CA_PH8 | Bronze | Old Sites (Before 2015) | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | D-21 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | cables nto be organized | Converged Run | Contractor | M/D | Converged Run | - | - | 2% | 7% | 76%
356411 | 1144737 | I-MARIOT-MRAGE_BBU1 | C01_1118CA_PH05 | Silver | Nodal/VIP | Tamer Onsi | Tamer Onsi | Orange | 2019-09-10 | HGLI | Huawei | Cairo East | Madinet Nasr | V10R00 | E-1-29 | Civil | Shelter Body / Main Enclosure | Feeders unorganized on the horizontal path | Minor | cables not installed well | Converged Run | Contractor | M/D | Converged Run | - | - | 2.25% | 9% | 71%
356391 | 1143607 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-3-32 | Power System | GEDP | Ducts/conduits covers missing/unfixed | Minor | Covers of ducts are not fixed | Contractor | Contractor | M/D | Converged Run | - | - | 0.5% | 7.5% | 20%
356391 | 1143612 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-4-32 | Power System | Surge Arrestor | Ducts/conduits covers missing/unfixed | Minor | Missing covers of ducts | Contractor | Contractor | M/D | Converged Run | - | - | 0.5% | 5.833% | 20%
356391 | 1143616 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-5-32 | Power System | DC Boxes | Ducts/conduits covers missing/unfixed | Minor | Missing covers of ducts | Contractor | Contractor | M/D | Converged Run | - | - | 0.5% | 2.5% | 20%
356391 | 1143614 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-5-8 | Power System | DC Boxes | Door/frame fixation that affects door from open easily or close firmly | Minor | Cover isn't fixed | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 2.5% | 20%
356391 | 1143617 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-6-1 | Power System | Rectifiers | Clean (not normal dust) | Minor | The rectifier needs cleaning | Aging | Contractor | M/D | Converged Run | - | - | 2% | 8% | 20%
356391 | 1143621 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-6-2 | Power System | Rectifiers | Label unit/components | Minor | Missing labels of CBs | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 8% | 20%
356391 | 1143630 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | B-13 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Earth plates cleaned, waxed, covered with foil | Minor | Earth plates need cleaning and grease | Aging | Contractor | M/D | Converged Run | - | - | 1.714% | 12% | 20%
356391 | 1143623 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | B-32 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Ducts/conduits covers missing/unfixed | Minor | Missing covers of ducts | Contractor | Contractor | M/D | Converged Run | - | - | 1.714% | 12% | 20%
356391 | 1143637 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | D-1 | Equipment and DDF | Equipment and DDF | Clean (not normal dust) | Minor | Equipments need cleaning | Aging | Contractor | M/D | Converged Run | - | - | 1.667% | 3.667% | 20%
356391 | 1143640 | 01_S_QALAHA_0985UP | C2_0985UP_PH13 | Bronze | Whitelist | Atef Zidan | Ramy Kheer | Sectra | 2019-09-18 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | D-35 | Equipment and DDF | Equipment and DDF | Trays/Roxtec/Plate not earthed | Minor | Stolen earth connections of basket trays | Stealth | Contractor | M/D | Converged Run | - | - | 2% | 3.667% | 20%
356365 | 1142861 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-32 | Power System | GEDP | Ducts/conduits covers missing/unfixed | Minor | fix covers | Contractor | Contractor | M/D | Converged Run | - | - | 0.6667% | 10.67% | 20.33%
356365 | 1142898 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-5-2 | Power System | DC Boxes | Label unit/components | Minor | lables | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 4% | 20.33%
356365 | 1142894 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-2 | Power System | Rectifiers | Label unit/components | Minor | add missing labels | Contractor | Contractor | M/D | Converged Run | - | - | 1.6% | 8% | 20.33%
356365 | 1142893 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-21 | Power System | Rectifiers | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange | Converged Run | Contractor | M/D | Converged Run | - | - | 1.6% | 8% | 20.33%
356365 | 1142884 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | B-32 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Ducts/conduits covers missing/unfixed | Minor | fix | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 20.33%
356365 | 1142878 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | D-1 | Equipment and DDF | Equipment and DDF | Clean (not normal dust) | Minor | clean | Contractor | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 20.33%
356365 | 1142900 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | D-21 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange | Converged Run | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 20.33%
356365 | 1142904 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | D-32 | Equipment and DDF | Equipment and DDF | Ducts/conduits covers missing/unfixed | Minor | fix | Contractor | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 20.33%
356365 | 1142882 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-35 | Civil | Shelter Body / Main Enclosure | Trays/Roxtec/Plate not earthed | Minor | loose | Contractor | Contractor | M/D | Converged Run | - | - | 1.5% | 9% | 20.33%
356365 | 1142896 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-67 | Civil | Shelter Body / Main Enclosure | Non-flammable junk/trash inside/outside (e.g. metals, woods, etc… ) | Minor | clean | Contractor | Contractor | M/D | Converged Run | - | - | 1.5% | 9% | 20.33%
356365 | 1142948 | KORDY | C3_0237UP_PH6 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-39 | Civil | Antenna Support | Unit rust (else trays) | Minor | treat rust | Aging | Converged Run | M/D | Converged Run | - | - | 1% | 7% | 20.33%
356364 | 1142755 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-1 | Power System | GEDP | Clean (not normal dust) | Minor | clean | Contractor | Contractor | M/D | Converged Run | - | - | 3% | 12% | 13.64%
356364 | 1142806 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-4-9 | Power System | Surge Arrestor | Door lock/handle that affects door from open easily or close firmly | Minor | faulty lock | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 7.833% | 13.64%
356364 | 1142787 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-5-1 | Power System | DC Boxes | Clean (not normal dust) | Minor | clean | Contractor | Contractor | M/D | Converged Run | - | - | 1.333% | 4% | 13.64%
356364 | 1142837 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-5-2 | Power System | DC Boxes | Label unit/components | Minor | add label | Contractor | Contractor | M/D | Converged Run | - | - | 1.333% | 4% | 13.64%
356364 | 1142760 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-1 | Power System | Rectifiers | Clean (not normal dust) | Minor | clean | Contractor | Contractor | M/D | Converged Run | - | - | 1.6% | 8% | 13.64%
356364 | 1142763 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-2 | Power System | Rectifiers | Label unit/components | Minor | adjust labels | Contractor | Contractor | M/D | Converged Run | - | - | 1.6% | 8% | 13.64%
356364 | 1142767 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-7-1 | Power System | Batteries | Clean (not normal dust) | Minor | clean | Contractor | Contractor | M/D | Converged Run | - | - | 0.8333% | 2.262% | 13.64%
356364 | 1142783 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | D-1 | Equipment and DDF | Equipment and DDF | Clean (not normal dust) | Minor | clean | Contractor | Contractor | M/D | Converged Run | - | - | 0.8333% | 2.262% | 13.64%
356364 | 1142792 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-35 | Civil | Shelter Body / Main Enclosure | Trays/Roxtec/Plate not earthed | Minor | stolen earth | Stealth | Contractor | M/D | Converged Run | - | - | 1.286% | 9% | 13.64%
356364 | 1142852 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-62 | Civil | Shelter Body / Main Enclosure | Lights operation | Minor | faulty | Contractor | Contractor | M/D | Converged Run | - | - | 1.286% | 9% | 13.64%
356364 | 1142774 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-67 | Civil | Shelter Body / Main Enclosure | Non-flammable junk/trash inside/outside (e.g. metals, woods, etc… ) | Minor | clean | Contractor | Contractor | M/D | Converged Run | - | - | 1.286% | 9% | 13.64%
356364 | 1142816 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-13 | Civil | Antenna Support | Earth plates cleaned, waxed, covered with foil | Minor | clean and waxed | Contractor | Contractor | M/D | Converged Run | - | - | 0.7778% | 7% | 13.64%
356364 | 1142840 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-21 | Civil | Antenna Support | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange and remove unused cables | Converged Run | Contractor | M/D | Converged Run | - | - | 0.7778% | 7% | 13.64%
356364 | 1142813 | 6OCT-IND-ZONE2 | C5_0727UP_PH11 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-39 | Civil | Antenna Support | Unit rust (else trays) | Minor | rusty | Aging | Converged Run | M/D | Converged Run | - | - | 0.7778% | 7% | 13.64%
356357 | 1142628 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-1-1 | Power System | Power Meter & Main Breaker | Clean (not normal dust) | Minor | 100A Box unclean | Aging | Contractor | M/D | Converged Run | - | - | 0.8333% | 5% | 35%
356357 | 1142630 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-1-39 | Power System | Power Meter & Main Breaker | Unit rust (else trays) | Minor | 100A Box door rusty | Aging | Contractor | M/D | Converged Run | - | - | 0.8333% | 5% | 35%
356357 | 1142627 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-1-8 | Power System | Power Meter & Main Breaker | Door/frame fixation that affects door from open easily or close firmly | Minor | Panel not isolated | Aging | Contractor | M/D | Converged Run | - | - | 0.8333% | 5% | 35%
356357 | 1142624 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-1-9 | Power System | Power Meter & Main Breaker | Door lock/handle that affects door from open easily or close firmly | Minor | P.M door open | Aging | Contractor | M/D | Converged Run | - | - | 0.8333% | 5% | 35%
356357 | 1142633 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-3-32 | Power System | GEDP | Ducts/conduits covers missing/unfixed | Minor | Duct cover not fixed | Aging | Contractor | M/D | Converged Run | - | - | 4% | 12% | 35%
356357 | 1142642 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-5-2 | Power System | DC Boxes | Label unit/components | Minor | Missing label on C.B | Aging | Contractor | M/D | Converged Run | - | - | 2% | 3% | 35%
356357 | 1142639 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-5-8 | Power System | DC Boxes | Door/frame fixation that affects door from open easily or close firmly | Minor | DC Box cover not isolated | Aging | Contractor | M/D | Converged Run | - | - | 1% | 3% | 35%
356357 | 1142643 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-6-1 | Power System | Rectifiers | Clean (not normal dust) | Minor | Rectifier unclean | Aging | Contractor | M/D | Converged Run | - | - | 2.667% | 8% | 35%
356357 | 1142648 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-7-1 | Power System | Batteries | Clean (not normal dust) | Minor | Battery surface unclean | Aging | Contractor | M/D | Converged Run | - | - | 2.5% | 5% | 35%
356357 | 1142673 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | D-1 | Equipment and DDF | Equipment and DDF | Clean (not normal dust) | Minor | Shelter floor unclean | Aging | Contractor | M/D | Converged Run | - | - | 1% | 1% | 35%
356357 | 1142680 | 10TH-RES4 | C2_0599CA_PH6 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-21 | NGLI | Huawei | Sinai | Ismailia | V10R00 | E-1-67 | Civil | Shelter Body / Main Enclosure | Non-flammable junk/trash inside/outside (e.g. metals, woods, etc… ) | Minor | Unclean site area | Guard | Contractor | M/D | Converged Run | - | - | 2% | 7% | 35%
356349 | 1141765 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-1 | Power System | Power Meter & Main Breaker | Clean (not normal dust) | Minor | clean and treat rust | Aging | Contractor | M/D | Converged Run | - | - | 0.8333% | 5% | 53.83%
356349 | 1141759 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-21 | Power System | Power Meter & Main Breaker | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange | Electricity Company | Contractor | M/D | Converged Run | - | - | 0.8333% | 5% | 53.83%
356349 | 1141774 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-39 | Power System | Power Meter & Main Breaker | Unit rust (else trays) | Minor | treat rust | Aging | Contractor | M/D | Converged Run | - | - | 0.8333% | 5% | 53.83%
356349 | 1141748 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | A-5-1 | Power System | DC Boxes | Clean (not normal dust) | Minor | clean | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 1% | 53.83%
356349 | 1141756 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | B-54 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Refrigerant line isolation | Minor | isolate | Aging | Contractor | M/D | Converged Run | - | - | 2% | 2% | 53.83%
356349 | 1141746 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | D-21 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange | Converged Run | Converged Run | M/D | Converged Run | - | - | 0.6667% | 5.667% | 53.83%
356349 | 1141751 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-39 | Civil | Shelter Body / Main Enclosure | Unit rust (else trays) | Minor | treat rust | Aging | Contractor | M/D | Converged Run | - | - | 1% | 8% | 53.83%
356349 | 1141776 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-67 | Civil | Shelter Body / Main Enclosure | Non-flammable junk/trash inside/outside (e.g. metals, woods, etc… ) | Minor | clean | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 8% | 53.83%
356349 | 1141781 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-21 | Civil | Antenna Support | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange | Converged Run | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 53.83%
356349 | 1141784 | 6OCT-RSD | C4_0052UP_PH2 | Golden | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-16 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-35 | Civil | Antenna Support | Trays/Roxtec/Plate not earthed | Minor | not connected to earth system and need cleaning as well | Contractor | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 53.83%
356346 | 1141366 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-1-1 | Power System | Power Meter & Main Breaker | Clean (not normal dust) | Minor | Panel needs cleaning | Aging | Contractor | M/D | Converged Run | - | - | 1% | 5% | 28.5%
356346 | 1141364 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-1-39 | Power System | Power Meter & Main Breaker | Unit rust (else trays) | Minor | The power meter panel is rusty | Aging | Contractor | M/D | Converged Run | - | - | 1% | 5% | 28.5%
356346 | 1141365 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-1-9 | Power System | Power Meter & Main Breaker | Door lock/handle that affects door from open easily or close firmly | Minor | The power meter panel without a door lock | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 5% | 28.5%
356346 | 1141375 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-4-8 | Power System | Surge Arrestor | Door/frame fixation that affects door from open easily or close firmly | Minor | Broken door of the surge panel and cover isn't fixed well | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 9% | 28.5%
356346 | 1141380 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-6-2 | Power System | Rectifiers | Label unit/components | Minor | Missing labels of CBs | Contractor | Contractor | M/D | Converged Run | - | - | 2.667% | 8% | 28.5%
356346 | 1141393 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | D-21 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | Bad arrangement of cables | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 3% | 28.5%
356346 | 1141395 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | D-35 | Equipment and DDF | Equipment and DDF | Trays/Roxtec/Plate not earthed | Minor | Stolen earth connections of basket trays | Stealth | Contractor | M/D | Converged Run | - | - | 2% | 3% | 28.5%
356346 | 1141406 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | E-1-62 | Civil | Shelter Body / Main Enclosure | Lights operation | Minor | One bulb needs to be replaced | Aging | Contractor | M/D | Converged Run | - | - | 2% | 9% | 28.5%
356346 | 1141417 | 01_N_BS-TAZMANT-EST_0283UP | C1_0283UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | E-2-21 | Civil | Antenna Support | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | Bad arrangement of cables | Contractor | Contractor | M/D | Converged Run | - | - | 1.4% | 7% | 28.5%
356345 | 1141576 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-1 | Power System | Power Meter & Main Breaker | Clean (not normal dust) | Minor | clean | Aging | Contractor | M/D | Converged Run | - | - | 0.7143% | 5% | 18.42%
356345 | 1141572 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-39 | Power System | Power Meter & Main Breaker | Unit rust (else trays) | Minor | treat rust or replace belts | Contractor | Contractor | M/D | Converged Run | - | - | 0.7143% | 5% | 18.42%
356345 | 1141578 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-9 | Power System | Power Meter & Main Breaker | Door lock/handle that affects door from open easily or close firmly | Minor | faulty | Contractor | Contractor | M/D | Converged Run | - | - | 0.7143% | 5% | 18.42%
356345 | 1141542 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-1 | Power System | Rectifiers | Clean (not normal dust) | Minor | clean | Contractor | Contractor | M/D | Converged Run | - | - | 1.333% | 8% | 18.42%
356345 | 1141541 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-49 | Power System | Rectifiers | Module faulty | Minor | faulty module | Contractor | Contractor | M/D | Converged Run | - | - | 1.333% | 8% | 18.42%
356345 | 1141558 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | B-54 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Refrigerant line isolation | Minor | isolate | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 10.75% | 18.42%
356345 | 1141554 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | D-1 | Equipment and DDF | Equipment and DDF | Clean (not normal dust) | Minor | clean | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 7% | 18.42%
356345 | 1141544 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | D-21 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 7% | 18.42%
356345 | 1141555 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-67 | Civil | Shelter Body / Main Enclosure | Non-flammable junk/trash inside/outside (e.g. metals, woods, etc… ) | Minor | clean | Contractor | Contractor | M/D | Converged Run | - | - | 1.8% | 9% | 18.42%
356345 | 1141566 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-13 | Civil | Antenna Support | Earth plates cleaned, waxed, covered with foil | Minor | clean and waxed | Contractor | Contractor | M/D | Converged Run | - | - | 1.4% | 7% | 18.42%
356345 | 1141516 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-21 | Civil | Antenna Support | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange and remove unused cables | Converged Run | Contractor | M/D | Converged Run | - | - | 1.4% | 7% | 18.42%
356345 | 1141589 | TAWENEAT-ZAYED | C1_0509UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-39 | Civil | Fence / Roof | Unit rust (else trays) | Minor | treat rust | Aging | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 18.42%
356344 | 1141355 | 6OCT-DIPLOMAT | C2_0882UP_PH12 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-39 | Power System | GEDP | Unit rust (else trays) | Minor | treat rust | Aging | Contractor | M/D | Converged Run | - | - | 2% | 7% | 36%
356344 | 1141340 | 6OCT-DIPLOMAT | C2_0882UP_PH12 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-5-2 | Power System | DC Boxes | Label unit/components | Minor | labels | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 1% | 36%
356344 | 1141334 | 6OCT-DIPLOMAT | C2_0882UP_PH12 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | D-2 | Equipment and DDF | Equipment and DDF | Label unit/components | Minor | add labels | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 7% | 36%
356344 | 1141336 | 6OCT-DIPLOMAT | C2_0882UP_PH12 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | D-21 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange | Converged Run | Contractor | M/D | Converged Run | - | - | 1% | 7% | 36%
356344 | 1141322 | 6OCT-DIPLOMAT | C2_0882UP_PH12 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-67 | Civil | Shelter Body / Main Enclosure | Non-flammable junk/trash inside/outside (e.g. metals, woods, etc… ) | Minor | clean and arrange cables | Aging | Contractor | M/D | Converged Run | - | - | 1.5% | 9% | 36%
356344 | 1141351 | 6OCT-DIPLOMAT | C2_0882UP_PH12 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-75 | Civil | Shelter Body / Main Enclosure | Feeders earth kit and connectors isolation | Minor | isolate | Aging | Contractor | M/D | Converged Run | - | - | 1.5% | 9% | 36%
356344 | 1141344 | 6OCT-DIPLOMAT | C2_0882UP_PH12 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-21 | Civil | Antenna Support | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange | Converged Run | Contractor | M/D | Converged Run | - | - | 2.333% | 7% | 36%
356343 | 1141302 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-39 | Power System | Power Meter & Main Breaker | Unit rust (else trays) | Minor | treat rust | Contractor | Contractor | M/D | Converged Run | - | - | 1.25% | 5% | 31.33%
356343 | 1141299 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-9 | Power System | Power Meter & Main Breaker | Door lock/handle that affects door from open easily or close firmly | Minor | faulty lock and treat rust | Contractor | Contractor | M/D | Converged Run | - | - | 1.25% | 5% | 31.33%
356343 | 1141283 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-5-2 | Power System | DC Boxes | Label unit/components | Minor | labels | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 1% | 31.33%
356343 | 1141296 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-2 | Power System | Rectifiers | Label unit/components | Minor | add missing label | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 5.5% | 31.33%
356343 | 1141294 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-49 | Power System | Rectifiers | Module faulty | Minor | faulty module | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 5.5% | 31.33%
356343 | 1141293 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | D-32 | Equipment and DDF | Equipment and DDF | Ducts/conduits covers missing/unfixed | Minor | fix cover | Contractor | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 31.33%
356343 | 1141309 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-39 | Civil | Shelter Body / Main Enclosure | Unit rust (else trays) | Minor | treat rust | Aging | Contractor | M/D | Converged Run | - | - | 1% | 5% | 31.33%
356343 | 1141274 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-62 | Civil | Shelter Body / Main Enclosure | Lights operation | Minor | not working | Aging | Contractor | M/D | Converged Run | - | - | 2% | 5% | 31.33%
356343 | 1141289 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-67 | Civil | Shelter Body / Main Enclosure | Non-flammable junk/trash inside/outside (e.g. metals, woods, etc… ) | Minor | clean | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 5% | 31.33%
356343 | 1141307 | 6OCT-ZAYED-1ST | C2_0899UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-15 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-35 | Civil | Antenna Support | Trays/Roxtec/Plate not earthed | Minor | not connected to earth ring | Stealth | Contractor | M/D | Converged Run | - | - | 2.333% | 7% | 31.33%
356342 | 1140569 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-32 | Power System | Power Meter & Main Breaker | Ducts/conduits covers missing/unfixed | Minor | fix | Converged Run | Contractor | M/D | Converged Run | - | - | 1% | 5% | 44.17%
356342 | 1140573 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-39 | Power System | Power Meter & Main Breaker | Unit rust (else trays) | Minor | treat rust | Aging | Contractor | M/D | Converged Run | - | - | 1% | 5% | 44.17%
356342 | 1140571 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-9 | Power System | Power Meter & Main Breaker | Door lock/handle that affects door from open easily or close firmly | Minor | faulty | Aging | Contractor | M/D | Converged Run | - | - | 1% | 5% | 44.17%
356342 | 1140578 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-1 | Power System | Rectifiers | Clean (not normal dust) | Minor | clean | Aging | Contractor | M/D | Converged Run | - | - | 2% | 6% | 44.17%
356342 | 1140577 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-2 | Power System | Rectifiers | Label unit/components | Minor | labels | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 6% | 44.17%
356342 | 1140579 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-49 | Power System | Rectifiers | Module faulty | Minor | faulty module | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 6% | 44.17%
356342 | 1140595 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | D-21 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange and seal | Converged Run | Contractor | M/D | Converged Run | - | - | 1% | 6% | 44.17%
356342 | 1140586 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-13 | Civil | Shelter Body / Main Enclosure | Earth plates cleaned, waxed, covered with foil | Minor | clean and waxed and cover with foil | Contractor | Contractor | M/D | Converged Run | - | - | 1.5% | 9% | 44.17%
356342 | 1140593 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-39 | Civil | Shelter Body / Main Enclosure | Unit rust (else trays) | Minor | treat rust | Aging | Contractor | M/D | Converged Run | - | - | 1.5% | 9% | 44.17%
356342 | 1140589 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-21 | Civil | Antenna Support | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange and clean | Converged Run | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 44.17%
356342 | 1140588 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-79 | Civil | Antenna Support | Palm tree trunk section camouflage (scratch/damage) | Minor | fix | Aging | Converged Run | M/D | Converged Run | - | - | 1.75% | 7% | 44.17%
356342 | 1140568 | 6OCT-DREAM-5 | C2_3253UP_PH13 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-39 | Civil | Fence / Roof | Unit rust (else trays) | Minor | treat rust | Aging | Contractor | M/D | Converged Run | - | - | 2.333% | 7% | 44.17%
356341 | 1140630 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-1 | Power System | Power Meter & Main Breaker | Clean (not normal dust) | Minor | clean | Aging | Contractor | M/D | Converged Run | - | - | 0.625% | 5% | 43%
356341 | 1140628 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-39 | Power System | Power Meter & Main Breaker | Unit rust (else trays) | Minor | treat rust | Aging | Contractor | M/D | Converged Run | - | - | 0.625% | 5% | 43%
356341 | 1140629 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-9 | Power System | Power Meter & Main Breaker | Door lock/handle that affects door from open easily or close firmly | Minor | faulty lock | Aging | Contractor | M/D | Converged Run | - | - | 0.625% | 5% | 43%
356341 | 1140641 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-2 | Power System | Rectifiers | Label unit/components | Minor | add missing labels | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 8% | 43%
356341 | 1140642 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-21 | Power System | Rectifiers | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange cables | Converged Run | Contractor | M/D | Converged Run | - | - | 1% | 8% | 43%
356341 | 1140644 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | D-1 | Equipment and DDF | Equipment and DDF | Clean (not normal dust) | Minor | clean | Aging | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 43%
356341 | 1140649 | DREAM-LAND-3 | C4_0726UP_PH11 | Silver | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | D-21 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange cables | Converged Run | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 43%
356340 | 1140429 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-8 | Power System | Power Meter & Main Breaker | Door/frame fixation that affects door from open easily or close firmly | Minor | fix door | Aging | Contractor | M/D | Converged Run | - | - | 2.5% | 5% | 22.83%
356340 | 1140404 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-5-2 | Power System | DC Boxes | Label unit/components | Minor | labels | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 2% | 22.83%
356340 | 1140400 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-21 | Power System | Rectifiers | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange cables | Converged Run | Contractor | M/D | Converged Run | - | - | 1.6% | 8% | 22.83%
356340 | 1140409 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-9 | Power System | Rectifiers | Door lock/handle that affects door from open easily or close firmly | Minor | missing | Aging | Contractor | M/D | Converged Run | - | - | 1.6% | 8% | 22.83%
356340 | 1140425 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-67 | Civil | Shelter Body / Main Enclosure | Non-flammable junk/trash inside/outside (e.g. metals, woods, etc… ) | Minor | clean | Contractor | Contractor | M/D | Converged Run | - | - | 3% | 9% | 22.83%
356340 | 1140439 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-13 | Civil | Antenna Support | Earth plates cleaned, waxed, covered with foil | Minor | clean | Contractor | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 22.83%
356340 | 1140445 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-21 | Civil | Antenna Support | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange cables | Converged Run | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 22.83%
356340 | 1140449 | 6OCT-IND-NTH2 | C5_0668UP_PH9 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-39 | Civil | Fence / Roof | Unit rust (else trays) | Minor | treat rust | Aging | Contractor | M/D | Converged Run | - | - | 2% | 7% | 22.83%
356339 | 1140517 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-5-2 | Power System | DC Boxes | Label unit/components | Minor | labels | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 3% | 27%
356339 | 1140516 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-2 | Power System | Rectifiers | Label unit/components | Minor | labels | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 3.5% | 27%
356339 | 1140480 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-7-1 | Power System | Batteries | Clean (not normal dust) | Minor | clean | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 2% | 27%
356339 | 1140490 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | D-32 | Equipment and DDF | Equipment and DDF | Ducts/conduits covers missing/unfixed | Minor | cover | Aging | Contractor | M/D | Converged Run | - | - | 2% | 6.5% | 27%
356339 | 1140548 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-39 | Civil | Shelter Body / Main Enclosure | Unit rust (else trays) | Minor | treat rust | Aging | Contractor | M/D | Converged Run | - | - | 1.5% | 9% | 27%
356339 | 1140486 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-67 | Civil | Shelter Body / Main Enclosure | Non-flammable junk/trash inside/outside (e.g. metals, woods, etc… ) | Minor | clean | Contractor | Contractor | M/D | Converged Run | - | - | 1.5% | 9% | 27%
356339 | 1140487 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-13 | Civil | Antenna Support | Earth plates cleaned, waxed, covered with foil | Minor | clean and connect to earth system | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 7% | 27%
356339 | 1140470 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-21 | Civil | Antenna Support | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange | Converged Run | Contractor | M/D | Converged Run | - | - | 1% | 7% | 27%
356339 | 1140550 | 6OCT-IND-WST | C2_0230UP_PH5 | Silver | Nodal/VIP | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-39 | Civil | Antenna Support | Unit rust (else trays) | Minor | treat rust | Aging | Converged Run | M/D | Converged Run | - | - | 1% | 7% | 27%
356338 | 1140380 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-9 | Power System | Power Meter & Main Breaker | Door lock/handle that affects door from open easily or close firmly | Minor | faulty lock | Aging | Contractor | M/D | Converged Run | - | - | 2.5% | 5% | 5.5%
356338 | 1140369 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-1 | Power System | GEDP | Clean (not normal dust) | Minor | clean | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 5.5%
356338 | 1140270 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-2 | Power System | GEDP | Label unit/components | Minor | fix labels and clean panel | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 5.5%
356338 | 1140265 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-32 | Power System | GEDP | Ducts/conduits covers missing/unfixed | Minor | fix covers | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 5.5%
356338 | 1140370 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-5-1 | Power System | DC Boxes | Clean (not normal dust) | Minor | clean | Contractor | Contractor | M/D | Converged Run | - | - | 1.667% | 4% | 5.5%
356338 | 1140320 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-5-2 | Power System | DC Boxes | Label unit/components | Minor | labels | Contractor | Contractor | M/D | Converged Run | - | - | 0.6667% | 4% | 5.5%
356338 | 1140376 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-2 | Power System | Rectifiers | Label unit/components | Minor | wrong label | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 8% | 5.5%
356338 | 1140308 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-21 | Power System | Rectifiers | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange | Converged Run | Contractor | M/D | Converged Run | - | - | 2% | 8% | 5.5%
356338 | 1140343 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | B-54 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Refrigerant line isolation | Minor | isolate | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 5.5%
356338 | 1140287 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | D-21 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange | Converged Run | Contractor | M/D | Converged Run | - | - | 1.4% | 7% | 5.5%
356338 | 1140383 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-62 | Civil | Shelter Body / Main Enclosure | Lights operation | Minor | faulty lamp | Aging | Contractor | M/D | Converged Run | - | - | 1.286% | 9% | 5.5%
356338 | 1140349 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-21 | Civil | Antenna Support | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange | Converged Run | Contractor | M/D | Converged Run | - | - | 0.5% | 0.5% | 5.5%
356338 | 1140366 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-39 | Civil | Fence / Roof | Unit rust (else trays) | Minor | treat rust | Aging | Contractor | M/D | Converged Run | - | - | 1.4% | 7% | 5.5%
356338 | 1140353 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-67 | Civil | Fence / Roof | Non-flammable junk/trash inside/outside (e.g. metals, woods, etc… ) | Minor | remove | Guard | Converged Run | M/D | Converged Run | - | - | 1.4% | 7% | 5.5%
356338 | 1140359 | DAR-FOUAD | C3_0390UP_PH8 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-19 | HGLI | Huawei | Cairo West | October | V10R00 | F-21 | Generator | ATS / Engine | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange and clean | Contractor | Contractor | M/D | Converged Run | - | - | 1.25% | 10% | 5.5%
356337 | 1141138 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-3-32 | Power System | GEDP | Ducts/conduits covers missing/unfixed | Minor | Duct cover not fixed | Aging | Contractor | M/D | Converged Run | - | - | 3% | 12% | 19.5%
356337 | 1141150 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-4-1 | Power System | Surge Arrestor | Clean (not normal dust) | Minor | Surge panel unclean | Aging | Contractor | M/D | Converged Run | - | - | 1% | 3.5% | 19.5%
356337 | 1141152 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-5-2 | Power System | DC Boxes | Label unit/components | Minor | Missing label on C.B | Aging | Contractor | M/D | Converged Run | - | - | 1% | 1% | 19.5%
356337 | 1141155 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-6-1 | Power System | Rectifiers | Clean (not normal dust) | Minor | Rectifier unclean | Aging | Contractor | M/D | Converged Run | - | - | 1% | 6.833% | 19.5%
356337 | 1141165 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-7-1 | Power System | Batteries | Clean (not normal dust) | Minor | Battery surface unclean | Aging | Contractor | M/D | Converged Run | - | - | 1.25% | 5% | 19.5%
356337 | 1141164 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-7-2 | Power System | Batteries | Label unit/components | Minor | Battery string label not fixed | Aging | Contractor | M/D | Converged Run | - | - | 1.25% | 5% | 19.5%
356337 | 1141178 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | B-54 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Refrigerant line isolation | Minor | Refrigerant line not isolated well | Aging | Contractor | M/D | Converged Run | - | - | 3% | 12% | 19.5%
356337 | 1141183 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | D-1 | Equipment and DDF | Equipment and DDF | Clean (not normal dust) | Minor | Shelter floor unclean | Aging | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 19.5%
356337 | 1141203 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | D-21 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | Cable not fixed & bad arrangement | Aging | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 19.5%
356337 | 1141217 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | D-32 | Equipment and DDF | Equipment and DDF | Ducts/conduits covers missing/unfixed | Minor | Duct cover not fixed | Aging | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 19.5%
356337 | 1141239 | 10th of Ramadan BSC 2 | C1_8039CA_PH3_2 | Golden | BSC | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | E-1-13 | Civil | Shelter Body / Main Enclosure | Earth plates cleaned, waxed, covered with foil | Minor | Unclean earth bar | Aging | Contractor | M/D | Converged Run | - | - | 2% | 7.833% | 19.5%
356330 | 1140239 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-9 | Power System | Power Meter & Main Breaker | Door lock/handle that affects door from open easily or close firmly | Minor | faulty lock | Aging | Contractor | M/D | Converged Run | - | - | 1.667% | 5% | 34.5%
356330 | 1140192 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | A-3-2 | Power System | GEDP | Label unit/components | Minor | add missing labels | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 1% | 34.5%
356330 | 1140237 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | A-5-9 | Power System | DC Boxes | Door lock/handle that affects door from open easily or close firmly | Minor | faulty | Aging | Contractor | M/D | Converged Run | - | - | 2% | 2% | 34.5%
356330 | 1140203 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-2 | Power System | Rectifiers | Label unit/components | Minor | add labels | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 5.5% | 34.5%
356330 | 1140235 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | A-7-39 | Power System | Batteries | Unit rust (else trays) | Minor | treat rust | Aging | Contractor | M/D | Converged Run | - | - | 2% | 2% | 34.5%
356330 | 1140199 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | D-21 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange | Contractor | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 34.5%
356330 | 1140231 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-13 | Civil | Shelter Body / Main Enclosure | Earth plates cleaned, waxed, covered with foil | Minor | clean | Contractor | Contractor | M/D | Converged Run | - | - | 1.286% | 9% | 34.5%
356330 | 1140217 | 6OCT-DREAM-4 | C3_0902UP_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-75 | Civil | Shelter Body / Main Enclosure | Feeders earth kit and connectors isolation | Minor | isolate connectors | Contractor | Contractor | M/D | Converged Run | - | - | 1.286% | 9% | 34.5%
356328 | 1140003 | DREAM-PARK | C3_0183UP_PH3 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | A-5-2 | Power System | DC Boxes | Label unit/components | Minor | labels | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 3% | 53%
356328 | 1139994 | DREAM-PARK | C3_0183UP_PH3 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-2 | Power System | Rectifiers | Label unit/components | Minor | add labels | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 8% | 53%
356328 | 1139996 | DREAM-PARK | C3_0183UP_PH3 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-8 | Power System | Rectifiers | Door/frame fixation that affects door from open easily or close firmly | Minor | fix frame | Converged Run | Contractor | M/D | Converged Run | - | - | 2% | 8% | 53%
356328 | 1140022 | DREAM-PARK | C3_0183UP_PH3 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | D-21 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange | Converged Run | Contractor | M/D | Converged Run | - | - | 1.167% | 7% | 53%
356328 | 1140029 | DREAM-PARK | C3_0183UP_PH3 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-13 | Civil | Shelter Body / Main Enclosure | Earth plates cleaned, waxed, covered with foil | Minor | not connected to earth ring | Stealth | Contractor | M/D | Converged Run | - | - | 2.25% | 9% | 53%
356328 | 1140010 | DREAM-PARK | C3_0183UP_PH3 | Bronze | Old Sites (Before 2015) | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-18 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-21 | Civil | Antenna Support | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange and remove unsued cables and jumpers | Converged Run | Contractor | M/D | Converged Run | - | - | 1% | 1% | 53%
356326 | 1140759 | DK-TILBANA | C1_0602DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | A-4-39 | Power System | Surge Arrestor | Unit rust (else trays) | Minor | Panel has some rust. | Aging | Contractor | M/D | Converged Run | - | - | 2% | 7% | 67%
356326 | 1140766 | DK-TILBANA | C1_0602DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | B-13 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Earth plates cleaned, waxed, covered with foil | Minor | Outside earth plates need cleaning and wax. | Aging | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 67%
356326 | 1140767 | DK-TILBANA | C1_0602DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | B-54 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Refrigerant line isolation | Minor | Pipes need isolation. | Aging | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 67%
356326 | 1140761 | DK-TILBANA | C1_0602DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | E-1-13 | Civil | Shelter Body / Main Enclosure | Earth plates cleaned, waxed, covered with foil | Minor | Outside earth plates need cleaning and wax. | Aging | Contractor | M/D | Converged Run | - | - | 1% | 1% | 67%
356324 | 1140725 | DK-BELGAY-VLG | C1_3774DE_PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | B-13 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Earth plates cleaned, waxed, covered with foil | Minor | Outside earth plates need cleaning and wax. | Aging | Contractor | M/D | Converged Run | - | - | 4% | 12% | 77%
356324 | 1140726 | DK-BELGAY-VLG | C1_3774DE_PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | E-2-13 | Civil | Antenna Support | Earth plates cleaned, waxed, covered with foil | Minor | Outside earth plates need cleaning and wax. | Aging | Contractor | M/D | Converged Run | - | - | 1% | 1% | 77%
356323 | 1140692 | DK-MIT-KHAYRON | C3_3257DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | A-6-32 | Power System | Rectifiers | Ducts/conduits covers missing/unfixed | Minor | Protective elements need cover. | Aging | Contractor | M/D | Converged Run | - | - | 2.667% | 8% | 45%
356323 | 1140697 | DK-MIT-KHAYRON | C3_3257DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | B-13 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Earth plates cleaned, waxed, covered with foil | Minor | Outside earth plates need cleaning and wax. | Aging | Contractor | M/D | Converged Run | - | - | 2% | 12% | 45%
356323 | 1140700 | DK-MIT-KHAYRON | C3_3257DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-18 | AGLI | AGLI-Contractor | Delta North | Mansoura | V10R00 | E-2-21 | Civil | Antenna Support | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | Cable need proper installation and fixation. | Aging | Contractor | M/D | Converged Run | - | - | 3.5% | 7% | 45%
356321 | 1140871 | 23_S_ ZAHREYA-TOWN_ 0583AL_S000 | C3_0583AL_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Abdullatief | Eslam Ahmed | Sectra | 2019-09-17 | AGLI | Orascom | ALEX | Alex East | V10R00 | A-3-21 | Power System | GEDP | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | Rosite need proper fixation | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 1% | 75.5%
356321 | 1140878 | 23_S_ ZAHREYA-TOWN_ 0583AL_S000 | C3_0583AL_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Abdullatief | Eslam Ahmed | Sectra | 2019-09-17 | AGLI | Orascom | ALEX | Alex East | V10R00 | D-21 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | Need arrangement | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 3.5% | 75.5%
356321 | 1140879 | 23_S_ ZAHREYA-TOWN_ 0583AL_S000 | C3_0583AL_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Abdullatief | Eslam Ahmed | Sectra | 2019-09-17 | AGLI | Orascom | ALEX | Alex East | V10R00 | E-1-39 | Civil | Shelter Body / Main Enclosure | Unit rust (else trays) | Minor | Treat rust and paint | Aging | Contractor | M/D | Converged Run | - | - | 1.8% | 9% | 75.5%
356321 | 1140884 | 23_S_ ZAHREYA-TOWN_ 0583AL_S000 | C3_0583AL_PH12 | Bronze | Old Sites (Before 2015) | Ahmed Abdullatief | Eslam Ahmed | Sectra | 2019-09-17 | AGLI | Orascom | ALEX | Alex East | V10R00 | E-2-39 | Civil | Antenna Support | Unit rust (else trays) | Minor | Rusty bolts | Aging | Converged Run | M/D | Converged Run | - | - | 1% | 1% | 75.5%
356318 | 1139925 | QL-DEER-2 | C1_3275DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | B-32 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Ducts/conduits covers missing/unfixed | Minor | Cover uninstalled | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 10.5% | 43.17%
356318 | 1139932 | QL-DEER-2 | C1_3275DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | B-39 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Unit rust (else trays) | Minor | Treat rust and paint | Aging | Contractor | M/D | Converged Run | - | - | 2% | 10.5% | 43.17%
356318 | 1139915 | QL-DEER-2 | C1_3275DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | D-32 | Equipment and DDF | Equipment and DDF | Ducts/conduits covers missing/unfixed | Minor | Duct not covered well | Contractor | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 43.17%
356318 | 1139926 | QL-DEER-2 | C1_3275DE_PH12 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | E-1-35 | Civil | Shelter Body / Main Enclosure | Trays/Roxtec/Plate not earthed | Minor | Need proper sealing | Contractor | Contractor | M/D | Converged Run | - | - | 2.25% | 9% | 43.17%
356317 | 1139832 | QL-DEER | C2_0423DE_PH4 | Golden | Whitelist | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | A-1-9 | Power System | Power Meter & Main Breaker | Door lock/handle that affects door from open easily or close firmly | Minor | Faulty lock | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 2% | 44%
356317 | 1139837 | QL-DEER | C2_0423DE_PH4 | Golden | Whitelist | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | B-32 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Ducts/conduits covers missing/unfixed | Minor | Cover uninstalled | Contractor | Contractor | M/D | Converged Run | - | - | 3% | 12% | 44%
356317 | 1139831 | QL-DEER | C2_0423DE_PH4 | Golden | Whitelist | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | E-1-35 | Civil | Shelter Body / Main Enclosure | Trays/Roxtec/Plate not earthed | Minor | Need proper sealing | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 7% | 44%
356317 | 1139835 | QL-DEER | C2_0423DE_PH4 | Golden | Whitelist | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | E-2-21 | Civil | Antenna Support | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | Need arrangement | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 2% | 44%
356315 | 1139807 | QL-MUSHTAHER | C1_0703DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | B-32 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Ducts/conduits covers missing/unfixed | Minor | Cover uninstalled | Contractor | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 42%
356315 | 1139794 | QL-MUSHTAHER | C1_0703DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | E-1-35 | Civil | Shelter Body / Main Enclosure | Trays/Roxtec/Plate not earthed | Minor | Need proper sealing | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 7% | 42%
356315 | 1139811 | QL-MUSHTAHER | C1_0703DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | E-2-21 | Civil | Antenna Support | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | Need arrangement | Contractor | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 42%
356315 | 1139805 | QL-MUSHTAHER | C1_0703DE_PH9 | Silver | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-15 | AGLI | AGLI-Contractor | Delta South | Banha | V10R00 | E-2-39 | Civil | Antenna Support | Unit rust (else trays) | Minor | Rusty bolts | Aging | Converged Run | M/D | Converged Run | - | - | 1.75% | 7% | 42%
356313 | 1139761 | 6th October 5 | C1_8032UP_PH2 | Bronze | Whitelist | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-1 | Power System | Power Meter & Main Breaker | Clean (not normal dust) | Minor | clean | Aging | Contractor | M/D | Converged Run | - | - | 1.667% | 5% | 46%
356313 | 1139742 | 6th October 5 | C1_8032UP_PH2 | Bronze | Whitelist | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | A-5-8 | Power System | DC Boxes | Door/frame fixation that affects door from open easily or close firmly | Minor | fix | Converged Run | Contractor | M/D | Converged Run | - | - | 2% | 2% | 46%
356313 | 1139767 | 6th October 5 | C1_8032UP_PH2 | Bronze | Whitelist | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | B-54 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Refrigerant line isolation | Minor | isolate | Aging | Contractor | M/D | Converged Run | - | - | 2.4% | 12% | 46%
356313 | 1139748 | 6th October 5 | C1_8032UP_PH2 | Bronze | Whitelist | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | D-21 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange | Converged Run | Contractor | M/D | Converged Run | - | - | 1% | 1% | 46%
356313 | 1139755 | 6th October 5 | C1_8032UP_PH2 | Bronze | Whitelist | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-21 | Civil | Antenna Support | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange | Converged Run | Contractor | M/D | Converged Run | - | - | 1% | 1% | 46%
356313 | 1139772 | 6th October 5 | C1_8032UP_PH2 | Bronze | Whitelist | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | E-3-67 | Civil | Fence / Roof | Non-flammable junk/trash inside/outside (e.g. metals, woods, etc… ) | Minor | clean | Aging | Contractor | M/D | Converged Run | - | - | 3.5% | 7% | 46%
356312 | 1139703 | 6OCT-MENA-CTY | C1_3252UP_PH13 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-39 | Power System | Power Meter & Main Breaker | Unit rust (else trays) | Minor | treat rust | Aging | Contractor | M/D | Converged Run | - | - | 2% | 4% | 45.17%
356312 | 1139701 | 6OCT-MENA-CTY | C1_3252UP_PH13 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | A-1-9 | Power System | Power Meter & Main Breaker | Door lock/handle that affects door from open easily or close firmly | Minor | faulty lock | Aging | Contractor | M/D | Converged Run | - | - | 2% | 4% | 45.17%
356312 | 1139697 | 6OCT-MENA-CTY | C1_3252UP_PH13 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-35 | Civil | Shelter Body / Main Enclosure | Trays/Roxtec/Plate not earthed | Minor | stolen earth | Stealth | Contractor | M/D | Converged Run | - | - | 2.25% | 9% | 45.17%
356312 | 1139685 | 6OCT-MENA-CTY | C1_3252UP_PH13 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-62 | Civil | Shelter Body / Main Enclosure | Lights operation | Minor | not operate | Contractor | Contractor | M/D | Converged Run | - | - | 2.25% | 9% | 45.17%
356312 | 1139709 | 6OCT-MENA-CTY | C1_3252UP_PH13 | Bronze | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-21 | Civil | Antenna Support | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange | Converged Run | Contractor | M/D | Converged Run | - | - | 2% | 2% | 45.17%
356311 | 1139577 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | A-5-2 | Power System | DC Boxes | Label unit/components | Minor | label missing | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 3% | 22%
356311 | 1139579 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | A-5-8 | Power System | DC Boxes | Door/frame fixation that affects door from open easily or close firmly | Minor | fix | Converged Run | Contractor | M/D | Converged Run | - | - | 2% | 3% | 22%
356311 | 1139574 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | A-6-2 | Power System | Rectifiers | Label unit/components | Minor | label missing | Contractor | Contractor | M/D | Converged Run | - | - | 4% | 8% | 22%
356311 | 1139590 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | B-54 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Refrigerant line isolation | Minor | replace | Aging | Contractor | M/D | Converged Run | - | - | 2% | 12% | 22%
356311 | 1139567 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | D-21 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange | Converged Run | Contractor | M/D | Converged Run | - | - | 2.333% | 7% | 22%
356311 | 1139566 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-62 | Civil | Shelter Body / Main Enclosure | Lights operation | Minor | faulty | Contractor | Contractor | M/D | Converged Run | - | - | 1.8% | 9% | 22%
356311 | 1139568 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | E-1-67 | Civil | Shelter Body / Main Enclosure | Non-flammable junk/trash inside/outside (e.g. metals, woods, etc… ) | Minor | remove | Contractor | Contractor | M/D | Converged Run | - | - | 1.8% | 9% | 22%
356311 | 1139599 | 6OCT-RSD-2 | C1_0693UP_PH09 | Silver | LTE | Ahmed Sabry | Mohamed Hassan | Orange | 2019-09-17 | HGLI | Huawei | Cairo West | October | V10R00 | E-2-21 | Civil | Antenna Support | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | arrange | Converged Run | Contractor | M/D | Converged Run | - | - | 2.333% | 7% | 22%
356309 | 1139335 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-3-32 | Power System | GEDP | Ducts/conduits covers missing/unfixed | Minor | Missing covers of ducts | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 11% | 29.17%
356309 | 1139338 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-6-2 | Power System | Rectifiers | Label unit/components | Minor | Missing labels of CBs | Contractor | Contractor | M/D | Converged Run | - | - | 1.333% | 8% | 29.17%
356309 | 1139340 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-6-21 | Power System | Rectifiers | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | Bad arrangement of cables | Contractor | Contractor | M/D | Converged Run | - | - | 1.333% | 8% | 29.17%
356309 | 1139342 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-6-35 | Power System | Rectifiers | Trays/Roxtec/Plate not earthed | Minor | Stolen earth connections of basket trays | Stealth | Contractor | M/D | Converged Run | - | - | 1.333% | 8% | 29.17%
356309 | 1139337 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-6-8 | Power System | Rectifiers | Door/frame fixation that affects door from open easily or close firmly | Minor | A cover of the rectifier isn't fixed | Contractor | Contractor | M/D | Converged Run | - | - | 1.333% | 8% | 29.17%
356309 | 1139343 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | A-7-1 | Power System | Batteries | Clean (not normal dust) | Minor | Batteries need cleaning | Aging | Contractor | M/D | Converged Run | - | - | 2% | 2% | 29.17%
356309 | 1139348 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | B-13 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Earth plates cleaned, waxed, covered with foil | Minor | Earth plates need cleaning and grease | Aging | Contractor | M/D | Converged Run | - | - | 1% | 6.833% | 29.17%
356309 | 1139350 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | D-21 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | Bad arrangement of cables | Contractor | Contractor | M/D | Converged Run | - | - | 1.4% | 7% | 29.17%
356309 | 1139355 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | D-32 | Equipment and DDF | Equipment and DDF | Ducts/conduits covers missing/unfixed | Minor | Missing covers of ducts | Contractor | Contractor | M/D | Converged Run | - | - | 1.4% | 7% | 29.17%
356309 | 1139353 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | D-35 | Equipment and DDF | Equipment and DDF | Trays/Roxtec/Plate not earthed | Minor | Stolen earth connections of basket trays | Stealth | Contractor | M/D | Converged Run | - | - | 1.4% | 7% | 29.17%
356309 | 1139366 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | E-2-13 | Civil | Antenna Support | Earth plates cleaned, waxed, covered with foil | Minor | Earth plates need cleaning and grease | Aging | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 29.17%
356309 | 1139384 | 01_W_GIZA-LUXOR-6_0137UP | C1_0137UP_PH3 | Golden | Nodal/VIP | Atef Zidan | Ramy Kheer | Sectra | 2019-09-16 | NGLI | Huawei | North Upper | Beni Suef | V10R00 | F-2 | Generator | ATS / Engine | Label unit/components | Minor | Missing labels of CBs | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 10% | 29.17%
356285 | 1138194 | Khattara 1 & 2 BSC | C1_8050UP_PH9_1 | Golden | Whitelist | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | A-1-1 | Power System | Power Meter & Main Breaker | Clean (not normal dust) | Minor | 100 A enclosure need cleaning | Aging | Contractor | M/D | Converged Run | - | - | 2.5% | 5% | 64%
356285 | 1138175 | Khattara 1 & 2 BSC | C1_8050UP_PH9_1 | Golden | Whitelist | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | A-6-1 | Power System | Rectifiers | Clean (not normal dust) | Minor | Rectifier cabinet is not clean | Aging | Contractor | M/D | Converged Run | - | - | 1% | 1% | 64%
356285 | 1138191 | Khattara 1 & 2 BSC | C1_8050UP_PH9_1 | Golden | Whitelist | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | B-13 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Earth plates cleaned, waxed, covered with foil | Minor | Earth bar need cleaning and new grease | Aging | Contractor | M/D | Converged Run | - | - | 1% | 6% | 64%
356285 | 1138187 | Khattara 1 & 2 BSC | C1_8050UP_PH9_1 | Golden | Whitelist | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | E-1-13 | Civil | Shelter Body / Main Enclosure | Earth plates cleaned, waxed, covered with foil | Minor | Earth bar need cleaning and new grease | Aging | Contractor | M/D | Converged Run | - | - | 3% | 9% | 64%
356284 | 1138141 | 01_W_QN-KHATARA_0273UP | C1_0273UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | A-6-2 | Power System | Rectifiers | Label unit/components | Minor | Missing labels at Rectifier C.Bs | Contractor | Contractor | M/D | Converged Run | - | - | 2.667% | 8% | 58%
356284 | 1138158 | 01_W_QN-KHATARA_0273UP | C1_0273UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | B-54 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Refrigerant line isolation | Minor | A/c refrigerant line need new isolation | Aging | Contractor | M/D | Converged Run | - | - | 3% | 12% | 58%
356284 | 1138126 | 01_W_QN-KHATARA_0273UP | C1_0273UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | D-2 | Equipment and DDF | Equipment and DDF | Label unit/components | Minor | Missing label at ddf rack | Contractor | Contractor | M/D | Converged Run | - | - | 2.333% | 7% | 58%
356284 | 1138145 | 01_W_QN-KHATARA_0273UP | C1_0273UP_PH8 | Golden | Nodal/VIP | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | D-32 | Equipment and DDF | Equipment and DDF | Ducts/conduits covers missing/unfixed | Minor | Duct inside shelter not covered | Contractor | Contractor | M/D | Converged Run | - | - | 2.333% | 7% | 58%
356283 | 1138095 | 01_H_QN-MAHROUSA_0274UP | C1_0274UP_PH8 | Golden | BSC | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | A-6-2 | Power System | Rectifiers | Label unit/components | Minor | Missing labels at Rectifier C.Bs | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 1% | 70%
356283 | 1138089 | 01_H_QN-MAHROUSA_0274UP | C1_0274UP_PH8 | Golden | BSC | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | D-2 | Equipment and DDF | Equipment and DDF | Label unit/components | Minor | Missing label at ddf rack | Contractor | Contractor | M/D | Converged Run | - | - | 2.333% | 7% | 70%
356283 | 1138093 | 01_H_QN-MAHROUSA_0274UP | C1_0274UP_PH8 | Golden | BSC | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | D-21 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | cables need arangement | Contractor | Contractor | M/D | Converged Run | - | - | 2.333% | 7% | 70%
356283 | 1138110 | 01_H_QN-MAHROUSA_0274UP | C1_0274UP_PH8 | Golden | BSC | Atef Zidan | Ali Ashour Moustafa | Sectra | 2019-09-11 | NGLI | Huawei | South Upper | Qena | V10R00 | F-13 | Generator | ATS / Engine | Earth plates cleaned, waxed, covered with foil | Minor | Earth bar need cleaning and new grease | Aging | Contractor | M/D | Converged Run | - | - | 2% | 7% | 70%
356282 | 1138356 | BH-SHOBRA-RIS | C1_4360DE_PH13 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | E-1-39 | Civil | Shelter Body / Main Enclosure | Unit rust (else trays) | Minor | Treat rust and paint | Aging | Contractor | M/D | Converged Run | - | - | 0.6667% | 0.6667% | 67.67%
356282 | 1138365 | BH-SHOBRA-RIS | C1_4360DE_PH13 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | E-2-39 | Civil | Antenna Support | Unit rust (else trays) | Minor | Safety wire has rust | Aging | Converged Run | M/D | Converged Run | - | - | 0.6667% | 5.667% | 67.67%
356282 | 1138355 | BH-SHOBRA-RIS | C1_4360DE_PH13 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | E-3-39 | Civil | Fence / Roof | Unit rust (else trays) | Minor | Treat rust and paint | Aging | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 67.67%
356282 | 1138351 | BH-SHOBRA-RIS | C1_4360DE_PH13 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | E-3-67 | Civil | Fence / Roof | Non-flammable junk/trash inside/outside (e.g. metals, woods, etc… ) | Minor | Plants around site | Guard | Converged Run | M/D | Converged Run | - | - | 1.75% | 7% | 67.67%
356282 | 1138371 | BH-SHOBRA-RIS | C1_4360DE_PH13 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | F-1 | Generator | ATS / Engine | Clean (not normal dust) | Minor | Need cleaning | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 9% | 67.67%
356282 | 1138370 | BH-SHOBRA-RIS | C1_4360DE_PH13 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | F-32 | Generator | ATS / Engine | Ducts/conduits covers missing/unfixed | Minor | Fuel pipes without tray | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 9% | 67.67%
356280 | 1138301 | BH-KFR-QASHASH | C4_0545DE_PH8 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | A-1-21 | Power System | Power Meter & Main Breaker | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | Power cable need proper installation | Electricity Company | Converged Run | M/D | Converged Run | - | - | 2% | 4% | 46%
356280 | 1138299 | BH-KFR-QASHASH | C4_0545DE_PH8 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | A-1-8 | Power System | Power Meter & Main Breaker | Door/frame fixation that affects door from open easily or close firmly | Minor | Protective cover requried | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 4% | 46%
356280 | 1138282 | BH-KFR-QASHASH | C4_0545DE_PH8 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | A-4-32 | Power System | Surge Arrestor | Ducts/conduits covers missing/unfixed | Minor | Missing bolt | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 1% | 46%
356280 | 1138277 | BH-KFR-QASHASH | C4_0545DE_PH8 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | A-6-49 | Power System | Rectifiers | Module faulty | Minor | Faulty module | Aging | Contractor | M/D | Converged Run | - | - | 2% | 7% | 46%
356280 | 1138287 | BH-KFR-QASHASH | C4_0545DE_PH8 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | B-32 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Ducts/conduits covers missing/unfixed | Minor | Cover uninstalled | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 12% | 46%
356280 | 1138286 | BH-KFR-QASHASH | C4_0545DE_PH8 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | B-39 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Unit rust (else trays) | Minor | Treat rust and paint | Aging | Contractor | M/D | Converged Run | - | - | 1% | 12% | 46%
356280 | 1138290 | BH-KFR-QASHASH | C4_0545DE_PH8 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | E-1-35 | Civil | Shelter Body / Main Enclosure | Trays/Roxtec/Plate not earthed | Minor | Need proper sealing | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 7% | 46%
356280 | 1138292 | BH-KFR-QASHASH | C4_0545DE_PH8 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Damanhour | V10R00 | E-2-39 | Civil | Antenna Support | Unit rust (else trays) | Minor | Rusty bolts | Aging | Converged Run | M/D | Converged Run | - | - | 1% | 6% | 46%
356278 | 1138071 | BH-DAHRIA | C2_3508DE_PH13 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Tanta | V10R00 | C-21 | Fire System | Fire Alarm and Fighting System | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | Rosite need proper fixation | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 7% | 73%
356278 | 1138069 | BH-DAHRIA | C2_3508DE_PH13 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta North | Tanta | V10R00 | E-1-62 | Civil | Shelter Body / Main Enclosure | Lights operation | Minor | Faulty light // Protective cover requried | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 7% | 73%
356274 | 1137935 | MF-BANI-SALAMA | C1-3232DE-PH12 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-09 | AGLI | AGLI-Contractor | Delta South | Sadat | V10R00 | A-6-32 | Power System | Rectifiers | Ducts/conduits covers missing/unfixed | Minor | Cover need proper fixation | Contractor | Contractor | M/D | Converged Run | - | - | 2% | 7% | 71%
356274 | 1137928 | MF-BANI-SALAMA | C1-3232DE-PH12 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-09 | AGLI | AGLI-Contractor | Delta South | Sadat | V10R00 | D-21 | Equipment and DDF | Equipment and DDF | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | Need arrangement | Contractor | Contractor | M/D | Converged Run | - | - | 1% | 2.667% | 71%
356274 | 1137927 | MF-BANI-SALAMA | C1-3232DE-PH12 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-09 | AGLI | AGLI-Contractor | Delta South | Sadat | V10R00 | E-1-39 | Civil | Shelter Body / Main Enclosure | Unit rust (else trays) | Minor | Treat rust and paint | Aging | Contractor | M/D | Converged Run | - | - | 2% | 2% | 71%
356274 | 1137923 | MF-BANI-SALAMA | C1-3232DE-PH12 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-09 | AGLI | AGLI-Contractor | Delta South | Sadat | V10R00 | E-2-21 | Civil | Antenna Support | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | Need arrangement | Contractor | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 71%
356274 | 1137917 | MF-BANI-SALAMA | C1-3232DE-PH12 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Eslam Ahmed | Sectra | 2019-09-09 | AGLI | AGLI-Contractor | Delta South | Sadat | V10R00 | E-3-67 | Civil | Fence / Roof | Non-flammable junk/trash inside/outside (e.g. metals, woods, etc… ) | Minor | Area need cleaning | Aging | Contractor | M/D | Converged Run | - | - | 2.333% | 7% | 71%
356266 | 1137524 | AT-QUSIYA5 | C1_3920UP_PH15 | Bronze | New Sites (After 2015) | Atef Zidan | Mohamed Abd Assalam Abass | Sectra | 2019-09-08 | NGLI | Huawei | North Upper | Asyout | V10R00 | A-6-2 | Power System | Rectifiers | Label unit/components | Minor | Missing labels at Rectifier C.Bs | New Sites | Converged Run | M/D | Converged Run | - | - | 2% | 7% | 81%
356264 | 1138310 | SK-QUDAH | C1-3402DE-PH13 | Golden | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | E-3-39 | Civil | Fence / Roof | Unit rust (else trays) | Minor | Fence gate has some rust. | Aging | Contractor | M/D | Converged Run | - | - | 1.75% | 7% | 44%
356263 | 1138248 | SK-SHARQAYA | C1-3793DE-PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | A-5-1 | Power System | DC Boxes | Clean (not normal dust) | Minor | DC box needs cleaning. | Aging | Contractor | M/D | Converged Run | - | - | 0.6667% | 0.6667% | 37.67%
356263 | 1138249 | SK-SHARQAYA | C1-3793DE-PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | A-6-8 | Power System | Rectifiers | Door/frame fixation that affects door from open easily or close firmly | Minor | - | Aging | Contractor | M/D | Converged Run | - | - | 2% | 2% | 37.67%
356263 | 1138261 | SK-SHARQAYA | C1-3793DE-PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | D-1 | Equipment and DDF | Equipment and DDF | Clean (not normal dust) | Minor | Generator and its area need cleaning. | Aging | Contractor | M/D | Converged Run | - | - | 0.6667% | 5.667% | 37.67%
356263 | 1138246 | SK-SHARQAYA | C1-3793DE-PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | E-1-13 | Civil | Shelter Body / Main Enclosure | Earth plates cleaned, waxed, covered with foil | Minor | Outside earth plates need cleaning and wax. | Aging | Contractor | M/D | Converged Run | - | - | 3% | 9% | 37.67%
356263 | 1138264 | SK-SHARQAYA | C1-3793DE-PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | E-2-21 | Civil | Antenna Support | Cables/Jumpers/Coaxial/FO/PCM organization | Minor | Cables need arrangement and fixation. | Aging | Contractor | M/D | Converged Run | - | - | 2% | 4% | 37.67%
356263 | 1138265 | SK-SHARQAYA | C1-3793DE-PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | E-2-39 | Civil | Antenna Support | Unit rust (else trays) | Minor | - | Aging | Converged Run | M/D | Converged Run | - | - | 2% | 4% | 37.67%
356263 | 1138253 | SK-SHARQAYA | C1-3793DE-PH14 | Bronze | Old Sites (Before 2015) | Mohamed Hassan | Mohamed Farid | Sectra | 2019-09-11 | AGLI | AGLI-Contractor | Delta South | Faqous | V10R00 | F-1 | Generator | ATS / Engine | Clean (not normal dust) | Minor | - | Aging | Contractor | M/D | Converged Run | - | - | 2.5% | 10% | 37.67%
356254 | 1137191 | SZ-MENA-OASIS | C1_0032RE_PH1 | Golden | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | A-4-9 | Power System | Surge Arrestor | Door lock/handle that affects door from open easily or close firmly | Minor | Surge panel door open | Aging | Contractor | M/D | Converged Run | - | - | 2% | 9.5% | 31.17%
356254 | 1137200 | SZ-MENA-OASIS | C1_0032RE_PH1 | Golden | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | A-5-2 | Power System | DC Boxes | Label unit/components | Minor | Missing label on C.B | Aging | Contractor | M/D | Converged Run | - | - | 1% | 3% | 31.17%
356254 | 1137194 | SZ-MENA-OASIS | C1_0032RE_PH1 | Golden | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | A-5-8 | Power System | DC Boxes | Door/frame fixation that affects door from open easily or close firmly | Minor | DC Box cover not isolated | Aging | Contractor | M/D | Converged Run | - | - | 2% | 3% | 31.17%
356254 | 1137209 | SZ-MENA-OASIS | C1_0032RE_PH1 | Golden | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | A-7-1 | Power System | Batteries | Clean (not normal dust) | Minor | Battery surface unclean | Aging | Contractor | M/D | Converged Run | - | - | 1.667% | 5% | 31.17%
356254 | 1137210 | SZ-MENA-OASIS | C1_0032RE_PH1 | Golden | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | A-7-2 | Power System | Batteries | Label unit/components | Minor | Missing label on Battery | Aging | Contractor | M/D | Converged Run | - | - | 1.667% | 5% | 31.17%
356254 | 1137231 | SZ-MENA-OASIS | C1_0032RE_PH1 | Golden | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | D-1 | Equipment and DDF | Equipment and DDF | Clean (not normal dust) | Minor | Shelter floor unclean | Aging | Contractor | M/D | Converged Run | - | - | 1.667% | 3.667% | 31.17%
356254 | 1137249 | SZ-MENA-OASIS | C1_0032RE_PH1 | Golden | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | D-32 | Equipment and DDF | Equipment and DDF | Ducts/conduits covers missing/unfixed | Minor | Duct cover not fixed | Aging | Contractor | M/D | Converged Run | - | - | 2% | 3.667% | 31.17%
356254 | 1137254 | SZ-MENA-OASIS | C1_0032RE_PH1 | Golden | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | E-1-62 | Civil | Shelter Body / Main Enclosure | Lights operation | Minor | One lamp only working | Aging | Contractor | M/D | Converged Run | - | - | 3% | 9% | 31.17%
356251 | 1136948 | SUKHNA-RD6 | C2_0014RE_PH1 | Golden | Whitelist | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | A-5-2 | Power System | DC Boxes | Label unit/components | Minor | Missing label on C.B | Aging | Contractor | M/D | Converged Run | - | - | 2% | 4% | 31.5%
356251 | 1136945 | SUKHNA-RD6 | C2_0014RE_PH1 | Golden | Whitelist | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | A-5-8 | Power System | DC Boxes | Door/frame fixation that affects door from open easily or close firmly | Minor | DC Box cover not fixed | Aging | Contractor | M/D | Converged Run | - | - | 2% | 4% | 31.5%
356251 | 1136950 | SUKHNA-RD6 | C2_0014RE_PH1 | Golden | Whitelist | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | A-6-1 | Power System | Rectifiers | Clean (not normal dust) | Minor | Rectifier unclean | Aging | Contractor | M/D | Converged Run | - | - | 4% | 8% | 31.5%
356251 | 1136953 | SUKHNA-RD6 | C2_0014RE_PH1 | Golden | Whitelist | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | A-7-1 | Power System | Batteries | Clean (not normal dust) | Minor | Battery surface unclean | Aging | Contractor | M/D | Converged Run | - | - | 2.5% | 5% | 31.5%
356251 | 1136966 | SUKHNA-RD6 | C2_0014RE_PH1 | Golden | Whitelist | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | D-1 | Equipment and DDF | Equipment and DDF | Clean (not normal dust) | Minor | Cabinet unclean | Aging | Contractor | M/D | Converged Run | - | - | 1.25% | 3.25% | 31.5%
356251 | 1136974 | SUKHNA-RD6 | C2_0014RE_PH1 | Golden | Whitelist | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-09 | NGLI | Huawei | Red Sea | Suez | V10R00 | D-32 | Equipment and DDF | Equipment and DDF | Ducts/conduits covers missing/unfixed | Minor | Missing duct cover | Aging | Contractor | M/D | Converged Run | - | - | 2% | 3.25% | 31.5%
356332 | 1140907 | 10TH-RSD1 | C5_0241CA_PH2 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-3-2 | Power System | GEDP | Label unit/components | Minor | Power cable missing label number | Aging | Contractor | M/D | Converged Run | - | - | 2% | 12% | 51%
356332 | 1140911 | 10TH-RSD1 | C5_0241CA_PH2 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | A-5-8 | Power System | DC Boxes | Door/frame fixation that affects door from open easily or close firmly | Minor | DC box cover not isolated | Aging | Contractor | M/D | Converged Run | - | - | 2% | 4% | 51%
356332 | 1140931 | 10TH-RSD1 | C5_0241CA_PH2 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | D-1 | Equipment and DDF | Equipment and DDF | Clean (not normal dust) | Minor | Shelter floor unclean | Aging | Contractor | M/D | Converged Run | - | - | 2% | 4% | 51%
356332 | 1140934 | 10TH-RSD1 | C5_0241CA_PH2 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | D-32 | Equipment and DDF | Equipment and DDF | Ducts/conduits covers missing/unfixed | Minor | Duct cover not exist | Aging | Contractor | M/D | Converged Run | - | - | 2% | 4% | 51%
356332 | 1140938 | 10TH-RSD1 | C5_0241CA_PH2 | Silver | Nodal/VIP | Ahmed Sabry | Mohammed Alaa | Sectra | 2019-09-18 | NGLI | Huawei | Sinai | Ismailia | V10R00 | E-1-62 | Civil | Shelter Body / Main Enclosure | Lights operation | Minor | Light not work | Aging | Contractor | M/D | Converged Run | - | - | 2% | 4.5% | 51%

## Assigned Team Breakdown-CPI
ReportID | Site Name | Total Score | Converged Run | Contractor Site Score
356414 | I-CTYSTR-COM_BBU1 | 61.5% | 0% | 61.5%
356413 | GOLDEN-PYRAMDS | 62% | 0% | 62%
356412 | M-ANDREA | 76% | 0% | 76%
356411 | I-MARIOT-MRAGE_BBU1 | 71% | 0% | 71%
356391 | 01_S_QALAHA_0985UP | 20% | 12.5% | 32.5%
356365 | KORDY | 20.33% | 12.75% | 33.08%
356364 | 6OCT-IND-ZONE2 | 13.64% | 8.056% | 21.7%
356357 | 10TH-RES4 | 35% | 0% | 35%
356349 | 6OCT-RSD | 53.83% | 9.333% | 63.17%
356346 | 01_N_BS-TAZMANT-EST_0283UP | 28.5% | 5% | 33.5%
356345 | TAWENEAT-ZAYED | 18.42% | 17.42% | 35.83%
356344 | 6OCT-DIPLOMAT | 36% | 5% | 41%
356343 | 6OCT-ZAYED-1ST | 31.33% | 27.83% | 59.17%
356342 | 6OCT-DREAM-5 | 44.17% | 6.417% | 50.58%
356341 | DREAM-LAND-3 | 43% | 5.292% | 48.29%
356340 | 6OCT-IND-NTH2 | 22.83% | 16.17% | 39%
356339 | 6OCT-IND-WST | 27% | 6% | 33%
356338 | DAR-FOUAD | 5.5% | 10.19% | 15.69%
356337 | 10th of Ramadan BSC 2 | 19.5% | 5.667% | 25.17%
356330 | 6OCT-DREAM-4 | 34.5% | 3.5% | 38%
356328 | DREAM-PARK | 53% | 1.167% | 54.17%
356326 | DK-TILBANA | 67% | 4% | 71%
356324 | DK-BELGAY-VLG | 77% | 5% | 82%
356323 | DK-MIT-KHAYRON | 45% | 12.83% | 57.83%
356321 | 23_S_ ZAHREYA-TOWN_ 0583AL_S000 | 75.5% | 12.8% | 88.3%
356318 | QL-DEER-2 | 43.17% | 10% | 53.17%
356317 | QL-DEER | 44% | 4% | 48%
356315 | QL-MUSHTAHER | 42% | 8.5% | 50.5%
356313 | 6th October 5 | 46% | 3% | 49%
356312 | 6OCT-MENA-CTY | 45.17% | 11.5% | 56.67%
356311 | 6OCT-RSD-2 | 22% | 13.33% | 35.33%
356309 | 01_W_GIZA-LUXOR-6_0137UP | 29.17% | 0% | 29.17%
356285 | Khattara 1 & 2 BSC | 64% | 13% | 77%
356284 | 01_W_QN-KHATARA_0273UP | 58% | 7.5% | 65.5%
356283 | 01_H_QN-MAHROUSA_0274UP | 70% | 2.333% | 72.33%
356282 | BH-SHOBRA-RIS | 67.67% | 2.417% | 70.08%
356280 | BH-KFR-QASHASH | 46% | 3% | 49%
356278 | BH-DAHRIA | 73% | 4% | 77%
356274 | MF-BANI-SALAMA | 71% | 3.5% | 74.5%
356266 | AT-QUSIYA5 | 81% | 7% | 88%
356264 | SK-QUDAH | 44% | 9% | 53%
356263 | SK-SHARQAYA | 37.67% | 9% | 46.67%
356254 | SZ-MENA-OASIS | 31.17% | 0% | 31.17%
356251 | SUKHNA-RD6 | 31.5% | 3.75% | 35.25%
356332 | 10TH-RSD1 | 51% | 0% | 51%