## Reserve Description
ReserveID | ReportID | Audit Date | SiteID | Site Name | Site Code | Office | Auditor | Requester | Requester Team | Requester Company | Maintenance Office | Contractor | Contractor Area | On Air Date | Version | Class | Sub-Class | Criteria | Reference | Severity | Offender | Assigned Team | Responsible | Logging | Before Comment | After Comment | After Response Received | Before Pic Inc | After Pic Inc | Fake Photo | Marked | Marked Grade | Marker Comment | Equipment | Vendor | Before Date | Deadline | After Date | Marking Date | Reassigned Trials
1134651 | 356173 | 2019-09-01 | 23199 | MM-CARLOS | C1_0756AL_PH15 | Matrouh | Ahmed Abdullatief | Ahmed Abdullatief | Audit | Orange | AGLI | Orascom | North Coast | 2012-05-29 | V10R00 | Fire System | Fire Alarm and Fighting System | Fire extinguisher missing/empty/expired/(safety seal) | C-60 | Critical | Stealth | Contractor | Converged Run | Contractor | Stolen fire extinguisher |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-01 | 2019-09-15 |  |  | 0
1145331 | 356374 | 2019-09-23 | 20137 | 01_W_SS-MR66-TANKA_0039SI | C1_0039SI_PH2 | Abo Redees | Ahmed Sabry | Ahmed Alaraby | Sinai | Sectra | NGLI | Huawei | Sinai | 2010-08-27 | V10R00 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Some parts are (missing / stolen) | B-41 | Critical | Stealth | Contractor | Converged Run | Contractor | Stolen A/C unit |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-29 | 2019-10-13 |  |  | 0
1145332 | 356374 | 2019-09-23 | 20137 | 01_W_SS-MR66-TANKA_0039SI | C1_0039SI_PH2 | Abo Redees | Ahmed Sabry | Ahmed Alaraby | Sinai | Sectra | NGLI | Huawei | Sinai | 2010-08-27 | V10R00 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Some parts are (missing / stolen) | B-41 | Critical | Stealth | Contractor | Converged Run | Contractor | Stolen A/C unit |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-29 | 2019-10-13 |  |  | 0
1145491 | 356395 | 2019-09-25 | 27186 | Abu Zenima BSC 2 | C1_8045SI_PH2 | Abo Redees | Ahmed Sabry | Ahmed Alaraby | Sinai | Sectra | NGLI | Huawei | Sinai | 2008-12-11 | V10R00 | Generator | ATS / Engine | Unit earth | F-12 | Critical | Stealth | Contractor | Converged Run | Contractor | Genset earth bar not connected to the main earth rod |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-30 | 2019-10-14 |  |  | 0
1145500 | 356395 | 2019-09-25 | 27186 | Abu Zenima BSC 2 | C1_8045SI_PH2 | Abo Redees | Ahmed Sabry | Ahmed Alaraby | Sinai | Sectra | NGLI | Huawei | Sinai | 2008-12-11 | V10R00 | Generator | ATS / Engine | Unit earth | F-12 | Critical | Stealth | Contractor | Converged Run | Contractor | Fuel tank not earthed |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-30 | 2019-10-14 |  |  | 0
1146447 | 356399 | 2019-09-25 | 20113 | 01_G_SS-MR66-TARAQIN_0035SI | C2_0035SI_PH2 | Abo Redees | Ahmed Sabry | Ahmed Alaraby | Sinai | Sectra | NGLI | Huawei | Sinai | 2006-03-30 | V10R00 | Generator | ATS / Engine | Wrong connection | F-17 | Critical | Stealth | Contractor | Converged Run | Contractor | Fuel tank indoor light stolen & power cable not isolated |  | FALSE | TRUE | [5 empty] | - | - | 2019-10-02 | 2019-10-16 |  |  | 0
1146448 | 356399 | 2019-09-25 | 20113 | 01_G_SS-MR66-TARAQIN_0035SI | C2_0035SI_PH2 | Abo Redees | Ahmed Sabry | Ahmed Alaraby | Sinai | Sectra | NGLI | Huawei | Sinai | 2006-03-30 | V10R00 | Generator | ATS / Engine | Wrong connection | F-17 | Critical | Stealth | Contractor | Converged Run | Contractor | Fuel tank indoor light stolen & power cable not isolated |  | FALSE | TRUE | [5 empty] | - | - | 2019-10-02 | 2019-10-16 |  |  | 0
1144024 | 356372 | 2019-09-23 | 20148 | 01_H_SS-RAS-ABU-RDS_0041SI | C3_0041SI_PH2 | Abo Redees | Ahmed Sabry | Ahmed Alaraby | Sinai | Sectra | NGLI | Huawei | Sinai | 2006-03-30 | V10R00 | Cooling System | A/Cs Cooling / Free Cooling / Ventilation | Wrong connection | B-17 | Critical | Sabotage | Contractor | Converged Run | Contractor | Loop on the Minor alarm on the DDF |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-27 | 2019-10-11 |  |  | 0
1144052 | 356372 | 2019-09-23 | 20148 | 01_H_SS-RAS-ABU-RDS_0041SI | C3_0041SI_PH2 | Abo Redees | Ahmed Sabry | Ahmed Alaraby | Sinai | Sectra | NGLI | Huawei | Sinai | 2006-03-30 | V10R00 | Civil | Shelter Body / Main Enclosure | Emergency light operation & battery condition | E-1-63 | Recommendation | Stealth | Contractor | Converged Run | Contractor | Emergency light stolen |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-27 | 2019-10-11 |  |  | 0
1144283 | 356373 | 2019-09-23 | 20466 | 01_G_SS-MR66-MATULA_0099SI | C2_0099SI_PH2 | Abo Redees | Ahmed Sabry | Ahmed Alaraby | Sinai | Sectra | NGLI | Huawei | Sinai | 2010-08-26 | V10R00 | Generator | ATS / Engine | Unit earth | F-12 | Critical | Stealth | Contractor | Converged Run | Contractor | Loose & stolen earth cables |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-27 | 2019-10-11 |  |  | 0
1144284 | 356373 | 2019-09-23 | 20466 | 01_G_SS-MR66-MATULA_0099SI | C2_0099SI_PH2 | Abo Redees | Ahmed Sabry | Ahmed Alaraby | Sinai | Sectra | NGLI | Huawei | Sinai | 2010-08-26 | V10R00 | Generator | ATS / Engine | Unit earth | F-12 | Critical | Stealth | Contractor | Converged Run | Contractor | Loose & stolen earth cables |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-27 | 2019-10-11 |  |  | 0
1144305 | 356373 | 2019-09-23 | 20466 | 01_G_SS-MR66-MATULA_0099SI | C2_0099SI_PH2 | Abo Redees | Ahmed Sabry | Ahmed Alaraby | Sinai | Sectra | NGLI | Huawei | Sinai | 2010-08-26 | V10R00 | Generator | ATS / Engine | Wrong connection | F-17 | Critical | Stealth | Contractor | Converged Run | Contractor | Stolen fuel tank indoor light & non isolated power cable |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-27 | 2019-10-11 |  |  | 0
1144312 | 356373 | 2019-09-23 | 20466 | 01_G_SS-MR66-MATULA_0099SI | C2_0099SI_PH2 | Abo Redees | Ahmed Sabry | Ahmed Alaraby | Sinai | Sectra | NGLI | Huawei | Sinai | 2010-08-26 | V10R00 | Generator | ATS / Engine | Wrong connection | F-17 | Critical | Stealth | Contractor | Converged Run | Contractor | Stolen fuel tank indoor light & non isolated power cable |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-27 | 2019-10-11 |  |  | 0
1144348 | 356400 | 2019-09-25 | 21315 | 01_S_CORAL-GARDN_0273RE | C1_0273RE_PH9 | Hurghada | Atef Zidan | Ali Ashour Moustafa | Upper | Sectra | NGLI | Huawei | Red Sea | 2008-01-29 | V10R00 | Fire System | Fire Alarm and Fighting System | Fire extinguisher missing/empty/expired/(safety seal) | C-60 | Critical | Stealth | Contractor | Converged Run | Contractor | Fire extinguisher is not exist in the site |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-29 | 2019-10-13 |  |  | 0
1144397 | 356402 | 2019-09-25 | 20792 | 01_S_RS-QUSEIR-ENT_0164RE | C1_0164RE_PH9 | Hurghada | Atef Zidan | Ali Ashour Moustafa | Upper | Sectra | NGLI | Huawei | Red Sea | 2006-03-01 | V10R00 | Civil | Shelter Body / Main Enclosure | Door lock/handle that affects door from open easily or close firmly | E-1-9 | Recommendation | Stealth | Contractor | Converged Run | Contractor | Shelte door was open and door alarm appear on omc |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-29 | 2019-10-13 |  |  | 0
1144399 | 356402 | 2019-09-25 | 20792 | 01_S_RS-QUSEIR-ENT_0164RE | C1_0164RE_PH9 | Hurghada | Atef Zidan | Ali Ashour Moustafa | Upper | Sectra | NGLI | Huawei | Red Sea | 2006-03-01 | V10R00 | Civil | Shelter Body / Main Enclosure | Door lock/handle that affects door from open easily or close firmly | E-1-9 | Recommendation | Stealth | Contractor | Converged Run | Contractor | Shelte door was open and door alarm appear on omc |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-29 | 2019-10-13 |  |  | 0
1134955 | 356189 | 2019-09-03 | 26025 | 01_S_AS-GAFAR-SADK_3499UP | C1_3499UP_PH14 | Idfu | Atef Zidan | Ali Ashour Moustafa | Upper | Sectra | NGLI | Huawei | South Upper | 2011-09-05 | V10R00 | Power System | Batteries | Some parts are (missing / stolen) | A-7-41 | Critical | Stealth | Converged Run | Converged Run | Converged Run | Site Batteries were stolen |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-08 | 2019-09-22 |  |  | 0
1134956 | 356189 | 2019-09-03 | 26025 | 01_S_AS-GAFAR-SADK_3499UP | C1_3499UP_PH14 | Idfu | Atef Zidan | Ali Ashour Moustafa | Upper | Sectra | NGLI | Huawei | South Upper | 2011-09-05 | V10R00 | Power System | Batteries | Some parts are (missing / stolen) | A-7-41 | Critical | Stealth | Converged Run | Converged Run | Converged Run | Site Batteries were stolen |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-08 | 2019-09-22 |  |  | 0
1134960 | 356189 | 2019-09-03 | 26025 | 01_S_AS-GAFAR-SADK_3499UP | C1_3499UP_PH14 | Idfu | Atef Zidan | Ali Ashour Moustafa | Upper | Sectra | NGLI | Huawei | South Upper | 2011-09-05 | V10R00 | Civil | Shelter Body / Main Enclosure | Alarms reporting to the OMC | E-1-19 | Critical | Stealth | Contractor | Converged Run | Contractor | Door open alarm not appeared on the Omc ( looped at sensor door ) | Solved and checked | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE |  | - | - | 2019-09-08 | 2019-09-22 | 2019-09-19 | 2019-09-24 | 0
1136172 | 356238 | 2019-09-04 | 20149 | 01_A_AS-MR02-DARAW_0041UP | C3_0041UP_PH2 | Aswan | Atef Zidan | Ali Ashour Moustafa | Upper | Sectra | NGLI | Huawei | South Upper | 2000-11-01 | V10R00 | Civil | Shelter Body / Main Enclosure | Unit earth | E-1-12 | Major | Stealth | Contractor | Converged Run | Contractor | earth bar and earth belts were stolen |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-12 | 2019-09-26 |  |  | 0
1136173 | 356238 | 2019-09-04 | 20149 | 01_A_AS-MR02-DARAW_0041UP | C3_0041UP_PH2 | Aswan | Atef Zidan | Ali Ashour Moustafa | Upper | Sectra | NGLI | Huawei | South Upper | 2000-11-01 | V10R00 | Civil | Shelter Body / Main Enclosure | Unit earth | E-1-12 | Major | Stealth | Contractor | Converged Run | Contractor | earth bar and earth belts were stolen |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-12 | 2019-09-26 |  |  | 0
1136174 | 356238 | 2019-09-04 | 20149 | 01_A_AS-MR02-DARAW_0041UP | C3_0041UP_PH2 | Aswan | Atef Zidan | Ali Ashour Moustafa | Upper | Sectra | NGLI | Huawei | South Upper | 2000-11-01 | V10R00 | Civil | Shelter Body / Main Enclosure | Unit earth | E-1-12 | Major | Stealth | Contractor | Converged Run | Contractor | earth bar and earth belts were stolen |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-12 | 2019-09-26 |  |  | 0
1136176 | 356238 | 2019-09-04 | 20149 | 01_A_AS-MR02-DARAW_0041UP | C3_0041UP_PH2 | Aswan | Atef Zidan | Ali Ashour Moustafa | Upper | Sectra | NGLI | Huawei | South Upper | 2000-11-01 | V10R00 | Civil | Shelter Body / Main Enclosure | Unit earth | E-1-12 | Major | Stealth | Contractor | Converged Run | Contractor | earth bar and earth belts were stolen |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-12 | 2019-09-26 |  |  | 0
1136187 | 356238 | 2019-09-04 | 20149 | 01_A_AS-MR02-DARAW_0041UP | C3_0041UP_PH2 | Aswan | Atef Zidan | Ali Ashour Moustafa | Upper | Sectra | NGLI | Huawei | South Upper | 2000-11-01 | V10R00 | Equipment and DDF | Equipment and DDF | Unit earth | D-12 | Major | Stealth | Contractor | Converged Run | Contractor | ddf earth cable is missing |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-12 | 2019-09-26 |  |  | 0
1136188 | 356238 | 2019-09-04 | 20149 | 01_A_AS-MR02-DARAW_0041UP | C3_0041UP_PH2 | Aswan | Atef Zidan | Ali Ashour Moustafa | Upper | Sectra | NGLI | Huawei | South Upper | 2000-11-01 | V10R00 | Equipment and DDF | Equipment and DDF | Unit earth | D-12 | Major | Stealth | Contractor | Converged Run | Contractor | ddf earth cable is missing |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-12 | 2019-09-26 |  |  | 0
1136263 | 356239 | 2019-09-04 | 20161 | 01_N_AS-NAJQARMILAH_0043UP | C1_0043UP_PH2 | Aswan | Atef Zidan | Ali Ashour Moustafa | Upper | Sectra | NGLI | Huawei | South Upper | 2001-08-11 | V10R00 | Civil | Shelter Body / Main Enclosure | Door lock/handle that affects door from open easily or close firmly | E-1-9 | Critical | Stealth | Contractor | Converged Run | Contractor | Shelter door is open and door alarm appeared on omc |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-11 | 2019-09-25 |  |  | 0
1136264 | 356239 | 2019-09-04 | 20161 | 01_N_AS-NAJQARMILAH_0043UP | C1_0043UP_PH2 | Aswan | Atef Zidan | Ali Ashour Moustafa | Upper | Sectra | NGLI | Huawei | South Upper | 2001-08-11 | V10R00 | Civil | Shelter Body / Main Enclosure | Door lock/handle that affects door from open easily or close firmly | E-1-9 | Critical | Stealth | Contractor | Converged Run | Contractor | Shelter door is open and door alarm appeared on omc |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-11 | 2019-09-25 |  |  | 0
1136307 | 356239 | 2019-09-04 | 20161 | 01_N_AS-NAJQARMILAH_0043UP | C1_0043UP_PH2 | Aswan | Atef Zidan | Ali Ashour Moustafa | Upper | Sectra | NGLI | Huawei | South Upper | 2001-08-11 | V10R00 | Equipment and DDF | Equipment and DDF | Unit earth | D-12 | Major | Stealth | Contractor | Converged Run | Contractor | ddf earth cable is missing |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-11 | 2019-09-25 |  |  | 0
1136308 | 356239 | 2019-09-04 | 20161 | 01_N_AS-NAJQARMILAH_0043UP | C1_0043UP_PH2 | Aswan | Atef Zidan | Ali Ashour Moustafa | Upper | Sectra | NGLI | Huawei | South Upper | 2001-08-11 | V10R00 | Equipment and DDF | Equipment and DDF | Unit earth | D-12 | Major | Stealth | Contractor | Converged Run | Contractor | ddf earth cable is missing |  | FALSE | TRUE | [5 empty] | - | - | 2019-09-11 | 2019-09-25 |  |  | 0
1136361 | 356240 | 2019-09-05 | 25167 | 01_S_AS-ATWANY_3081UP | C1_3081UP_PH13 | Idfu | Atef Zidan | Ali Ashour Moustafa | Upper | Sectra | NGLI | Huawei | South Upper | 2010-07-29 | V10R00 | Equipment and DDF | Equipment and DDF | Unit earth | D-12 | Major | Stealth | Contractor | Converged Run | Contractor | ddf earth cable is missing | Earthed | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE |  | - | - | 2019-09-11 | 2019-09-25 | 2019-09-19 | 2019-09-24 | 0